M-068 | Lighting - Induction Fixture (Outdoor) | SCE | COM | Electric | COMLighting - Induction Fixture (Outdoor) | Exterior Induction Fixtures; 4 cases- 100W HID to 70W Induction; 101-175W HID to 100W Induction; 176-200W Induction to 120W Induction; 201-399W HID to 180W Induction; 400W HID to 250W Induction | Standard metal halide or high-pressure sodium | Standard metal halide or high-pressure sodium | Lighting | OutGen | Ltg_Wired | Induc_fixt | Outdoor | 1 | 0 | 0 | 0.9 | 61 | NA | 1 | NA | Fixtures | WRF | WAREHOUSE - REFRIGERATED | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.078051 | 0.010915 | 0.088966 | Fixtures/1000 sf | 192.72 | 416.1 | 416.1 | 0.044 | 0.095 | 0.095 | 0 | 0 | 0 | 192.72 | 416.1 | 416.1 | 0.044 | 0.095 | 0.095 | 0 | 0 | 0 |  | 15 | 15 | 15 | 5 | 0.5 | 372.2067 | 182.0985 | 182.0985 | 0 | 61.3465 | 61.3465 | 0 | 0 | 0 | 1 | 1 | 0.082868 | 0.0060986 | [7 empty] | Low (2008) | Low (2008) | Low (2008) | None
M-068 | Lighting - Induction Fixture (Outdoor) | SCE | COM | Electric | COMLighting - Induction Fixture (Outdoor) | Exterior Induction Fixtures; 4 cases- 100W HID to 70W Induction; 101-175W HID to 100W Induction; 176-200W Induction to 120W Induction; 201-399W HID to 180W Induction; 400W HID to 250W Induction | Standard metal halide or high-pressure sodium | Standard metal halide or high-pressure sodium | Lighting | OutGen | Ltg_Wired | Induc_fixt | Outdoor | 1 | 0 | 0 | 0.9 | 61 | NA | 1 | NA | Fixtures | WRF | WAREHOUSE - REFRIGERATED | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.078051 | 0.010915 | 0.088966 | Fixtures/1000 sf | 192.72 | 416.1 | 416.1 | 0.044 | 0.095 | 0.095 | 0 | 0 | 0 | 192.72 | 416.1 | 416.1 | 0.044 | 0.095 | 0.095 | 0 | 0 | 0 |  | 15 | 15 | 15 | 5 | 0.5 | 372.2067 | 182.0985 | 182.0985 | 0 | 61.3465 | 61.3465 | 0 | 0 | 0 | 1 | 1 | 0.082868 | 0.0060986 | [7 empty] | Low (2008) | Low (2008) | Low (2008) | None
M-068 | Lighting - Induction Fixture (Outdoor) | SCE | COM | Electric | COMLighting - Induction Fixture (Outdoor) | Exterior Induction Fixtures; 4 cases- 100W HID to 70W Induction; 101-175W HID to 100W Induction; 176-200W Induction to 120W Induction; 201-399W HID to 180W Induction; 400W HID to 250W Induction | Standard metal halide or high-pressure sodium | Standard metal halide or high-pressure sodium | Lighting | OutGen | Ltg_Wired | Induc_fixt | Outdoor | 1 | 0 | 0 | 0.9 | 61 | NA | 1 | NA | Fixtures | WRF | WAREHOUSE - REFRIGERATED | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.078051 | 0.010915 | 0.088966 | Fixtures/1000 sf | 192.72 | 416.1 | 416.1 | 0.044 | 0.095 | 0.095 | 0 | 0 | 0 | 192.72 | 416.1 | 416.1 | 0.044 | 0.095 | 0.095 | 0 | 0 | 0 |  | 15 | 15 | 15 | 5 | 0.5 | 372.2067 | 182.0985 | 182.0985 | 0 | 61.3465 | 61.3465 | 0 | 0 | 0 | 1 | 1 | 0.082868 | 0.0060986 | [7 empty] | Low (2008) | Low (2008) | Low (2008) | None
M-068 | Lighting - Induction Fixture (Outdoor) | SDGE | COM | Electric | COMLighting - Induction Fixture (Outdoor) | Exterior Induction Fixtures; 4 cases- 100W HID to 70W Induction; 101-175W HID to 100W Induction; 176-200W Induction to 120W Induction; 201-399W HID to 180W Induction; 400W HID to 250W Induction | Standard metal halide or high-pressure sodium | Standard metal halide or high-pressure sodium | Lighting | OutGen | Ltg_Wired | Induc_fixt | Outdoor | 1 | 0 | 0 | 0.9 | 61 | NA | 1 | NA | Fixtures | WRF | WAREHOUSE - REFRIGERATED | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.10227 | 0.012474 | 0.11474 | Fixtures/1000 sf | 192.72 | 416.1 | 416.1 | 0.044 | 0.095 | 0.095 | 0 | 0 | 0 | 192.72 | 416.1 | 416.1 | 0.044 | 0.095 | 0.095 | 0 | 0 | 0 |  | 15 | 15 | 15 | 5 | 0.5 | 372.2067 | 182.0985 | 182.0985 | 0 | 61.3465 | 61.3465 | 0 | 0 | 0 | 1 | 1 | 0.10833 | 0.0064159 | [7 empty] | Low (2008) | Low (2008) | Low (2008) | None
M-068 | Lighting - Induction Fixture (Outdoor) | SDGE | COM | Electric | COMLighting - Induction Fixture (Outdoor) | Exterior Induction Fixtures; 4 cases- 100W HID to 70W Induction; 101-175W HID to 100W Induction; 176-200W Induction to 120W Induction; 201-399W HID to 180W Induction; 400W HID to 250W Induction | Standard metal halide or high-pressure sodium | Standard metal halide or high-pressure sodium | Lighting | OutGen | Ltg_Wired | Induc_fixt | Outdoor | 1 | 0 | 0 | 0.9 | 61 | NA | 1 | NA | Fixtures | WRF | WAREHOUSE - REFRIGERATED | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.10227 | 0.012474 | 0.11474 | Fixtures/1000 sf | 192.72 | 416.1 | 416.1 | 0.044 | 0.095 | 0.095 | 0 | 0 | 0 | 192.72 | 416.1 | 416.1 | 0.044 | 0.095 | 0.095 | 0 | 0 | 0 |  | 15 | 15 | 15 | 5 | 0.5 | 372.2067 | 182.0985 | 182.0985 | 0 | 61.3465 | 61.3465 | 0 | 0 | 0 | 1 | 1 | 0.10833 | 0.0064159 | [7 empty] | Low (2008) | Low (2008) | Low (2008) | None
M-068 | Lighting - Induction Fixture (Outdoor) | SDGE | COM | Electric | COMLighting - Induction Fixture (Outdoor) | Exterior Induction Fixtures; 4 cases- 100W HID to 70W Induction; 101-175W HID to 100W Induction; 176-200W Induction to 120W Induction; 201-399W HID to 180W Induction; 400W HID to 250W Induction | Standard metal halide or high-pressure sodium | Standard metal halide or high-pressure sodium | Lighting | OutGen | Ltg_Wired | Induc_fixt | Outdoor | 1 | 0 | 0 | 0.9 | 61 | NA | 1 | NA | Fixtures | WRF | WAREHOUSE - REFRIGERATED | Existing | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.10227 | 0.012474 | 0.11474 | Fixtures/1000 sf | 192.72 | 416.1 | 416.1 | 0.044 | 0.095 | 0.095 | 0 | 0 | 0 | 192.72 | 416.1 | 416.1 | 0.044 | 0.095 | 0.095 | 0 | 0 | 0 |  | 15 | 15 | 15 | 5 | 0.5 | 372.2067 | 182.0985 | 182.0985 | 0 | 61.3465 | 61.3465 | 0 | 0 | 0 | 1 | 1 | 0.10833 | 0.0064159 | [7 empty] | Low (2008) | Low (2008) | Low (2008) | None
M-068 | Lighting - Induction Fixture (Outdoor) | SDGE | COM | Electric | COMLighting - Induction Fixture (Outdoor) | Exterior Induction Fixtures; 4 cases- 100W HID to 70W Induction; 101-175W HID to 100W Induction; 176-200W Induction to 120W Induction; 201-399W HID to 180W Induction; 400W HID to 250W Induction | Standard metal halide or high-pressure sodium | Standard metal halide or high-pressure sodium | Lighting | OutGen | Ltg_Wired | Induc_fixt | Outdoor | 1 | 0 | 0 | 0.9 | 61 | NA | 1 | NA | Fixtures | WRF | WAREHOUSE - REFRIGERATED | New | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.10227 | 0.012474 | 0.11474 | Fixtures/1000 sf | 192.72 | 416.1 | 416.1 | 0.044 | 0.095 | 0.095 | 0 | 0 | 0 | 192.72 | 416.1 | 416.1 | 0.044 | 0.095 | 0.095 | 0 | 0 | 0 |  | 15 | 15 | 15 | 5 | 0.5 | 372.2067 | 182.0985 | 182.0985 | 0 | 61.3465 | 61.3465 | 0 | 0 | 0 | 1 | 1 | 0.10833 | 0.0064159 | [7 empty] | Low (2008) | Low (2008) | Low (2008) | None
M-068 | Lighting - Induction Fixture (Outdoor) | SDGE | COM | Electric | COMLighting - Induction Fixture (Outdoor) | Exterior Induction Fixtures; 4 cases- 100W HID to 70W Induction; 101-175W HID to 100W Induction; 176-200W Induction to 120W Induction; 201-399W HID to 180W Induction; 400W HID to 250W Induction | Standard metal halide or high-pressure sodium | Standard metal halide or high-pressure sodium | Lighting | OutGen | Ltg_Wired | Induc_fixt | Outdoor | 1 | 0 | 0 | 0.9 | 61 | NA | 1 | NA | Fixtures | WRF | WAREHOUSE - REFRIGERATED | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.10227 | 0.012474 | 0.11474 | Fixtures/1000 sf | 192.72 | 416.1 | 416.1 | 0.044 | 0.095 | 0.095 | 0 | 0 | 0 | 192.72 | 416.1 | 416.1 | 0.044 | 0.095 | 0.095 | 0 | 0 | 0 |  | 15 | 15 | 15 | 5 | 0.5 | 372.2067 | 182.0985 | 182.0985 | 0 | 61.3465 | 61.3465 | 0 | 0 | 0 | 1 | 1 | 0.10833 | 0.0064159 | [7 empty] | Low (2008) | Low (2008) | Low (2008) | None
M-068 | Lighting - Induction Fixture (Outdoor) | SDGE | COM | Electric | COMLighting - Induction Fixture (Outdoor) | Exterior Induction Fixtures; 4 cases- 100W HID to 70W Induction; 101-175W HID to 100W Induction; 176-200W Induction to 120W Induction; 201-399W HID to 180W Induction; 400W HID to 250W Induction | Standard metal halide or high-pressure sodium | Standard metal halide or high-pressure sodium | Lighting | OutGen | Ltg_Wired | Induc_fixt | Outdoor | 1 | 0 | 0 | 0.9 | 61 | NA | 1 | NA | Fixtures | WRF | WAREHOUSE - REFRIGERATED | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.10227 | 0.012474 | 0.11474 | Fixtures/1000 sf | 192.72 | 416.1 | 416.1 | 0.044 | 0.095 | 0.095 | 0 | 0 | 0 | 192.72 | 416.1 | 416.1 | 0.044 | 0.095 | 0.095 | 0 | 0 | 0 |  | 15 | 15 | 15 | 5 | 0.5 | 372.2067 | 182.0985 | 182.0985 | 0 | 61.3465 | 61.3465 | 0 | 0 | 0 | 1 | 1 | 0.10833 | 0.0064159 | [7 empty] | Low (2008) | Low (2008) | Low (2008) | None
M-068 | Lighting - Induction Fixture (Outdoor) | SDGE | COM | Electric | COMLighting - Induction Fixture (Outdoor) | Exterior Induction Fixtures; 4 cases- 100W HID to 70W Induction; 101-175W HID to 100W Induction; 176-200W Induction to 120W Induction; 201-399W HID to 180W Induction; 400W HID to 250W Induction | Standard metal halide or high-pressure sodium | Standard metal halide or high-pressure sodium | Lighting | OutGen | Ltg_Wired | Induc_fixt | Outdoor | 1 | 0 | 0 | 0.9 | 61 | NA | 1 | NA | Fixtures | WRF | WAREHOUSE - REFRIGERATED | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.10227 | 0.012474 | 0.11474 | Fixtures/1000 sf | 192.72 | 416.1 | 416.1 | 0.044 | 0.095 | 0.095 | 0 | 0 | 0 | 192.72 | 416.1 | 416.1 | 0.044 | 0.095 | 0.095 | 0 | 0 | 0 |  | 15 | 15 | 15 | 5 | 0.5 | 372.2067 | 182.0985 | 182.0985 | 0 | 61.3465 | 61.3465 | 0 | 0 | 0 | 1 | 1 | 0.10833 | 0.0064159 | [7 empty] | Low (2008) | Low (2008) | Low (2008) | None
M-068 | Lighting - Induction Fixture (Outdoor) | SDGE | COM | Electric | COMLighting - Induction Fixture (Outdoor) | Exterior Induction Fixtures; 4 cases- 100W HID to 70W Induction; 101-175W HID to 100W Induction; 176-200W Induction to 120W Induction; 201-399W HID to 180W Induction; 400W HID to 250W Induction | Standard metal halide or high-pressure sodium | Standard metal halide or high-pressure sodium | Lighting | OutGen | Ltg_Wired | Induc_fixt | Outdoor | 1 | 0 | 0 | 0.9 | 61 | NA | 1 | NA | Fixtures | WRF | WAREHOUSE - REFRIGERATED | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.10227 | 0.012474 | 0.11474 | Fixtures/1000 sf | 192.72 | 416.1 | 416.1 | 0.044 | 0.095 | 0.095 | 0 | 0 | 0 | 192.72 | 416.1 | 416.1 | 0.044 | 0.095 | 0.095 | 0 | 0 | 0 |  | 15 | 15 | 15 | 5 | 0.5 | 372.2067 | 182.0985 | 182.0985 | 0 | 61.3465 | 61.3465 | 0 | 0 | 0 | 1 | 1 | 0.10833 | 0.0064159 | [7 empty] | Low (2008) | Low (2008) | Low (2008) | None
M-068 | Lighting - Induction Fixture (Outdoor) | SDGE | COM | Electric | COMLighting - Induction Fixture (Outdoor) | Exterior Induction Fixtures; 4 cases- 100W HID to 70W Induction; 101-175W HID to 100W Induction; 176-200W Induction to 120W Induction; 201-399W HID to 180W Induction; 400W HID to 250W Induction | Standard metal halide or high-pressure sodium | Standard metal halide or high-pressure sodium | Lighting | OutGen | Ltg_Wired | Induc_fixt | Outdoor | 1 | 0 | 0 | 0.9 | 61 | NA | 1 | NA | Fixtures | WRF | WAREHOUSE - REFRIGERATED | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.10227 | 0.012474 | 0.11474 | Fixtures/1000 sf | 192.72 | 416.1 | 416.1 | 0.044 | 0.095 | 0.095 | 0 | 0 | 0 | 192.72 | 416.1 | 416.1 | 0.044 | 0.095 | 0.095 | 0 | 0 | 0 |  | 15 | 15 | 15 | 5 | 0.5 | 372.2067 | 182.0985 | 182.0985 | 0 | 61.3465 | 61.3465 | 0 | 0 | 0 | 1 | 1 | 0.10833 | 0.0064159 | [7 empty] | Low (2008) | Low (2008) | Low (2008) | None
M-068 | Lighting - Induction Fixture (Outdoor) | SDGE | COM | Electric | COMLighting - Induction Fixture (Outdoor) | Exterior Induction Fixtures; 4 cases- 100W HID to 70W Induction; 101-175W HID to 100W Induction; 176-200W Induction to 120W Induction; 201-399W HID to 180W Induction; 400W HID to 250W Induction | Standard metal halide or high-pressure sodium | Standard metal halide or high-pressure sodium | Lighting | OutGen | Ltg_Wired | Induc_fixt | Outdoor | 1 | 0 | 0 | 0.9 | 61 | NA | 1 | NA | Fixtures | WRF | WAREHOUSE - REFRIGERATED | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.10227 | 0.012474 | 0.11474 | Fixtures/1000 sf | 192.72 | 416.1 | 416.1 | 0.044 | 0.095 | 0.095 | 0 | 0 | 0 | 192.72 | 416.1 | 416.1 | 0.044 | 0.095 | 0.095 | 0 | 0 | 0 |  | 15 | 15 | 15 | 5 | 0.5 | 372.2067 | 182.0985 | 182.0985 | 0 | 61.3465 | 61.3465 | 0 | 0 | 0 | 1 | 1 | 0.10833 | 0.0064159 | [7 empty] | Low (2008) | Low (2008) | Low (2008) | None
M-068 | Lighting - Induction Fixture (Outdoor) | SDGE | COM | Electric | COMLighting - Induction Fixture (Outdoor) | Exterior Induction Fixtures; 4 cases- 100W HID to 70W Induction; 101-175W HID to 100W Induction; 176-200W Induction to 120W Induction; 201-399W HID to 180W Induction; 400W HID to 250W Induction | Standard metal halide or high-pressure sodium | Standard metal halide or high-pressure sodium | Lighting | OutGen | Ltg_Wired | Induc_fixt | Outdoor | 1 | 0 | 0 | 0.9 | 61 | NA | 1 | NA | Fixtures | WRF | WAREHOUSE - REFRIGERATED | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.10227 | 0.012474 | 0.11474 | Fixtures/1000 sf | 192.72 | 416.1 | 416.1 | 0.044 | 0.095 | 0.095 | 0 | 0 | 0 | 192.72 | 416.1 | 416.1 | 0.044 | 0.095 | 0.095 | 0 | 0 | 0 |  | 15 | 15 | 15 | 5 | 0.5 | 372.2067 | 182.0985 | 182.0985 | 0 | 61.3465 | 61.3465 | 0 | 0 | 0 | 1 | 1 | 0.10833 | 0.0064159 | [7 empty] | Low (2008) | Low (2008) | Low (2008) | None
M-068 | Lighting - Induction Fixture (Outdoor) | SDGE | COM | Electric | COMLighting - Induction Fixture (Outdoor) | Exterior Induction Fixtures; 4 cases- 100W HID to 70W Induction; 101-175W HID to 100W Induction; 176-200W Induction to 120W Induction; 201-399W HID to 180W Induction; 400W HID to 250W Induction | Standard metal halide or high-pressure sodium | Standard metal halide or high-pressure sodium | Lighting | OutGen | Ltg_Wired | Induc_fixt | Outdoor | 1 | 0 | 0 | 0.9 | 61 | NA | 1 | NA | Fixtures | SUN | STORAGE - UNCONDITIONED | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.10227 | 0.012474 | 0.11474 | Fixtures/1000 sf | 192.72 | 416.1 | 416.1 | 0.044 | 0.095 | 0.095 | 0 | 0 | 0 | 192.72 | 416.1 | 416.1 | 0.044 | 0.095 | 0.095 | 0 | 0 | 0 |  | 15 | 15 | 15 | 5 | 0.5 | 372.2067 | 182.0985 | 182.0985 | 0 | 61.3465 | 61.3465 | 0 | 0 | 0 | 1 | 1 | 0.10833 | 0.0064159 | [7 empty] | Low (2008) | Low (2008) | Low (2008) | None
M-068 | Lighting - Induction Fixture (Outdoor) | SDGE | COM | Electric | COMLighting - Induction Fixture (Outdoor) | Exterior Induction Fixtures; 4 cases- 100W HID to 70W Induction; 101-175W HID to 100W Induction; 176-200W Induction to 120W Induction; 201-399W HID to 180W Induction; 400W HID to 250W Induction | Standard metal halide or high-pressure sodium | Standard metal halide or high-pressure sodium | Lighting | OutGen | Ltg_Wired | Induc_fixt | Outdoor | 1 | 0 | 0 | 0.9 | 61 | NA | 1 | NA | Fixtures | SUN | STORAGE - UNCONDITIONED | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.10227 | 0.012474 | 0.11474 | Fixtures/1000 sf | 192.72 | 416.1 | 416.1 | 0.044 | 0.095 | 0.095 | 0 | 0 | 0 | 192.72 | 416.1 | 416.1 | 0.044 | 0.095 | 0.095 | 0 | 0 | 0 |  | 15 | 15 | 15 | 5 | 0.5 | 372.2067 | 182.0985 | 182.0985 | 0 | 61.3465 | 61.3465 | 0 | 0 | 0 | 1 | 1 | 0.10833 | 0.0064159 | [7 empty] | Low (2008) | Low (2008) | Low (2008) | None
M-068 | Lighting - Induction Fixture (Outdoor) | SDGE | COM | Electric | COMLighting - Induction Fixture (Outdoor) | Exterior Induction Fixtures; 4 cases- 100W HID to 70W Induction; 101-175W HID to 100W Induction; 176-200W Induction to 120W Induction; 201-399W HID to 180W Induction; 400W HID to 250W Induction | Standard metal halide or high-pressure sodium | Standard metal halide or high-pressure sodium | Lighting | OutGen | Ltg_Wired | Induc_fixt | Outdoor | 1 | 0 | 0 | 0.9 | 61 | NA | 1 | NA | Fixtures | SUN | STORAGE - UNCONDITIONED | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.10227 | 0.012474 | 0.11474 | Fixtures/1000 sf | 192.72 | 416.1 | 416.1 | 0.044 | 0.095 | 0.095 | 0 | 0 | 0 | 192.72 | 416.1 | 416.1 | 0.044 | 0.095 | 0.095 | 0 | 0 | 0 |  | 15 | 15 | 15 | 5 | 0.5 | 372.2067 | 182.0985 | 182.0985 | 0 | 61.3465 | 61.3465 | 0 | 0 | 0 | 1 | 1 | 0.10833 | 0.0064159 | [7 empty] | Low (2008) | Low (2008) | Low (2008) | None
M-068 | Lighting - Induction Fixture (Outdoor) | SDGE | COM | Electric | COMLighting - Induction Fixture (Outdoor) | Exterior Induction Fixtures; 4 cases- 100W HID to 70W Induction; 101-175W HID to 100W Induction; 176-200W Induction to 120W Induction; 201-399W HID to 180W Induction; 400W HID to 250W Induction | Standard metal halide or high-pressure sodium | Standard metal halide or high-pressure sodium | Lighting | OutGen | Ltg_Wired | Induc_fixt | Outdoor | 1 | 0 | 0 | 0.9 | 61 | NA | 1 | NA | Fixtures | SUN | STORAGE - UNCONDITIONED | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.10227 | 0.012474 | 0.11474 | Fixtures/1000 sf | 192.72 | 416.1 | 416.1 | 0.044 | 0.095 | 0.095 | 0 | 0 | 0 | 192.72 | 416.1 | 416.1 | 0.044 | 0.095 | 0.095 | 0 | 0 | 0 |  | 15 | 15 | 15 | 5 | 0.5 | 372.2067 | 182.0985 | 182.0985 | 0 | 61.3465 | 61.3465 | 0 | 0 | 0 | 1 | 1 | 0.10833 | 0.0064159 | [7 empty] | Low (2008) | Low (2008) | Low (2008) | None
M-068 | Lighting - Induction Fixture (Outdoor) | SDGE | COM | Electric | COMLighting - Induction Fixture (Outdoor) | Exterior Induction Fixtures; 4 cases- 100W HID to 70W Induction; 101-175W HID to 100W Induction; 176-200W Induction to 120W Induction; 201-399W HID to 180W Induction; 400W HID to 250W Induction | Standard metal halide or high-pressure sodium | Standard metal halide or high-pressure sodium | Lighting | OutGen | Ltg_Wired | Induc_fixt | Outdoor | 1 | 0 | 0 | 0.9 | 61 | NA | 1 | NA | Fixtures | SUN | STORAGE - UNCONDITIONED | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.10227 | 0.012474 | 0.11474 | Fixtures/1000 sf | 192.72 | 416.1 | 416.1 | 0.044 | 0.095 | 0.095 | 0 | 0 | 0 | 192.72 | 416.1 | 416.1 | 0.044 | 0.095 | 0.095 | 0 | 0 | 0 |  | 15 | 15 | 15 | 5 | 0.5 | 372.2067 | 182.0985 | 182.0985 | 0 | 61.3465 | 61.3465 | 0 | 0 | 0 | 1 | 1 | 0.10833 | 0.0064159 | [7 empty] | Low (2008) | Low (2008) | Low (2008) | None
M-068 | Lighting - Induction Fixture (Outdoor) | SDGE | COM | Electric | COMLighting - Induction Fixture (Outdoor) | Exterior Induction Fixtures; 4 cases- 100W HID to 70W Induction; 101-175W HID to 100W Induction; 176-200W Induction to 120W Induction; 201-399W HID to 180W Induction; 400W HID to 250W Induction | Standard metal halide or high-pressure sodium | Standard metal halide or high-pressure sodium | Lighting | OutGen | Ltg_Wired | Induc_fixt | Outdoor | 1 | 0 | 0 | 0.9 | 61 | NA | 1 | NA | Fixtures | SUN | STORAGE - UNCONDITIONED | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.10227 | 0.012474 | 0.11474 | Fixtures/1000 sf | 192.72 | 416.1 | 416.1 | 0.044 | 0.095 | 0.095 | 0 | 0 | 0 | 192.72 | 416.1 | 416.1 | 0.044 | 0.095 | 0.095 | 0 | 0 | 0 |  | 15 | 15 | 15 | 5 | 0.5 | 372.2067 | 182.0985 | 182.0985 | 0 | 61.3465 | 61.3465 | 0 | 0 | 0 | 1 | 1 | 0.10833 | 0.0064159 | [7 empty] | Low (2008) | Low (2008) | Low (2008) | None
M-068 | Lighting - Induction Fixture (Outdoor) | PGE | COM | Electric | COMLighting - Induction Fixture (Outdoor) | Exterior Induction Fixtures; 4 cases- 100W HID to 70W Induction; 101-175W HID to 100W Induction; 176-200W Induction to 120W Induction; 201-399W HID to 180W Induction; 400W HID to 250W Induction | Standard metal halide or high-pressure sodium | Standard metal halide or high-pressure sodium | Lighting | OutGen | Ltg_Wired | Induc_fixt | Outdoor | 1 | 0 | 0 | 0.9 | 61 | NA | 1 | NA | Fixtures | WRF | WAREHOUSE - REFRIGERATED | Existing | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.077363 | 0.011603 | 0.088966 | Fixtures/1000 sf | 590.4 | 902 | 902 | 0.2606 | 0.2606 | 0.2606 | 0 | 0 | 0 | 590.4 | 902 | 902 | 0.2606 | 0.2606 | 0.2606 | 0 | 0 | 0 |  | 14.6 | 14.6 | 14.6 | 4.8667 | 0.5 | 372.2067 | 182.0985 | 182.0985 | 70.2 | 61.3465 | 61.3465 | 0 | 0 | 0 | 1 | 1 | 0.082274 | 0.0066919 | [7 empty] | Low (2008) | Low (2008) | Low (2008) | None
M-068 | Lighting - Induction Fixture (Outdoor) | PGE | COM | Electric | COMLighting - Induction Fixture (Outdoor) | Exterior Induction Fixtures; 4 cases- 100W HID to 70W Induction; 101-175W HID to 100W Induction; 176-200W Induction to 120W Induction; 201-399W HID to 180W Induction; 400W HID to 250W Induction | Standard metal halide or high-pressure sodium | Standard metal halide or high-pressure sodium | Lighting | OutGen | Ltg_Wired | Induc_fixt | Outdoor | 1 | 0 | 0 | 0.9 | 61 | NA | 1 | NA | Fixtures | WRF | WAREHOUSE - REFRIGERATED | New | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.077363 | 0.011603 | 0.088966 | Fixtures/1000 sf | 590.4 | 902 | 902 | 0.2606 | 0.2606 | 0.2606 | 0 | 0 | 0 | 590.4 | 902 | 902 | 0.2606 | 0.2606 | 0.2606 | 0 | 0 | 0 |  | 14.6 | 14.6 | 14.6 | 4.8667 | 0.5 | 372.2067 | 182.0985 | 182.0985 | 70.2 | 61.3465 | 61.3465 | 0 | 0 | 0 | 1 | 1 | 0.082274 | 0.0066919 | [7 empty] | Low (2008) | Low (2008) | Low (2008) | None
M-068 | Lighting - Induction Fixture (Outdoor) | PGE | COM | Electric | COMLighting - Induction Fixture (Outdoor) | Exterior Induction Fixtures; 4 cases- 100W HID to 70W Induction; 101-175W HID to 100W Induction; 176-200W Induction to 120W Induction; 201-399W HID to 180W Induction; 400W HID to 250W Induction | Standard metal halide or high-pressure sodium | Standard metal halide or high-pressure sodium | Lighting | OutGen | Ltg_Wired | Induc_fixt | Outdoor | 1 | 0 | 0 | 0.9 | 61 | NA | 1 | NA | Fixtures | WRF | WAREHOUSE - REFRIGERATED | New | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.077363 | 0.011603 | 0.088966 | Fixtures/1000 sf | 590.4 | 902 | 902 | 0.2606 | 0.2606 | 0.2606 | 0 | 0 | 0 | 590.4 | 902 | 902 | 0.2606 | 0.2606 | 0.2606 | 0 | 0 | 0 |  | 14.6 | 14.6 | 14.6 | 4.8667 | 0.5 | 372.2067 | 182.0985 | 182.0985 | 70.2 | 61.3465 | 61.3465 | 0 | 0 | 0 | 1 | 1 | 0.082274 | 0.0066919 | [7 empty] | Low (2008) | Low (2008) | Low (2008) | None
M-068 | Lighting - Induction Fixture (Outdoor) | PGE | COM | Electric | COMLighting - Induction Fixture (Outdoor) | Exterior Induction Fixtures; 4 cases- 100W HID to 70W Induction; 101-175W HID to 100W Induction; 176-200W Induction to 120W Induction; 201-399W HID to 180W Induction; 400W HID to 250W Induction | Standard metal halide or high-pressure sodium | Standard metal halide or high-pressure sodium | Lighting | OutGen | Ltg_Wired | Induc_fixt | Outdoor | 1 | 0 | 0 | 0.9 | 61 | NA | 1 | NA | Fixtures | WRF | WAREHOUSE - REFRIGERATED | Existing | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.077363 | 0.011603 | 0.088966 | Fixtures/1000 sf | 590.4 | 902 | 902 | 0.2606 | 0.2606 | 0.2606 | 0 | 0 | 0 | 590.4 | 902 | 902 | 0.2606 | 0.2606 | 0.2606 | 0 | 0 | 0 |  | 14.6 | 14.6 | 14.6 | 4.8667 | 0.5 | 372.2067 | 182.0985 | 182.0985 | 70.2 | 61.3465 | 61.3465 | 0 | 0 | 0 | 1 | 1 | 0.082274 | 0.0066919 | [7 empty] | Low (2008) | Low (2008) | Low (2008) | None
M-068 | Lighting - Induction Fixture (Outdoor) | PGE | COM | Electric | COMLighting - Induction Fixture (Outdoor) | Exterior Induction Fixtures; 4 cases- 100W HID to 70W Induction; 101-175W HID to 100W Induction; 176-200W Induction to 120W Induction; 201-399W HID to 180W Induction; 400W HID to 250W Induction | Standard metal halide or high-pressure sodium | Standard metal halide or high-pressure sodium | Lighting | OutGen | Ltg_Wired | Induc_fixt | Outdoor | 1 | 0 | 0 | 0.9 | 61 | NA | 1 | NA | Fixtures | WRF | WAREHOUSE - REFRIGERATED | Existing | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.077363 | 0.011603 | 0.088966 | Fixtures/1000 sf | 590.4 | 902 | 902 | 0.2606 | 0.2606 | 0.2606 | 0 | 0 | 0 | 590.4 | 902 | 902 | 0.2606 | 0.2606 | 0.2606 | 0 | 0 | 0 |  | 14.6 | 14.6 | 14.6 | 4.8667 | 0.5 | 372.2067 | 182.0985 | 182.0985 | 70.2 | 61.3465 | 61.3465 | 0 | 0 | 0 | 1 | 1 | 0.082274 | 0.0066919 | [7 empty] | Low (2008) | Low (2008) | Low (2008) | None
M-068 | Lighting - Induction Fixture (Outdoor) | PGE | COM | Electric | COMLighting - Induction Fixture (Outdoor) | Exterior Induction Fixtures; 4 cases- 100W HID to 70W Induction; 101-175W HID to 100W Induction; 176-200W Induction to 120W Induction; 201-399W HID to 180W Induction; 400W HID to 250W Induction | Standard metal halide or high-pressure sodium | Standard metal halide or high-pressure sodium | Lighting | OutGen | Ltg_Wired | Induc_fixt | Outdoor | 1 | 0 | 0 | 0.9 | 61 | NA | 1 | NA | Fixtures | WRF | WAREHOUSE - REFRIGERATED | New | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.077363 | 0.011603 | 0.088966 | Fixtures/1000 sf | 590.4 | 902 | 902 | 0.2606 | 0.2606 | 0.2606 | 0 | 0 | 0 | 590.4 | 902 | 902 | 0.2606 | 0.2606 | 0.2606 | 0 | 0 | 0 |  | 14.6 | 14.6 | 14.6 | 4.8667 | 0.5 | 372.2067 | 182.0985 | 182.0985 | 70.2 | 61.3465 | 61.3465 | 0 | 0 | 0 | 1 | 1 | 0.082274 | 0.0066919 | [7 empty] | Low (2008) | Low (2008) | Low (2008) | None
M-068 | Lighting - Induction Fixture (Outdoor) | PGE | COM | Electric | COMLighting - Induction Fixture (Outdoor) | Exterior Induction Fixtures; 4 cases- 100W HID to 70W Induction; 101-175W HID to 100W Induction; 176-200W Induction to 120W Induction; 201-399W HID to 180W Induction; 400W HID to 250W Induction | Standard metal halide or high-pressure sodium | Standard metal halide or high-pressure sodium | Lighting | OutGen | Ltg_Wired | Induc_fixt | Outdoor | 1 | 0 | 0 | 0.9 | 61 | NA | 1 | NA | Fixtures | WRF | WAREHOUSE - REFRIGERATED | Existing | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.077363 | 0.011603 | 0.088966 | Fixtures/1000 sf | 590.4 | 902 | 902 | 0.2606 | 0.2606 | 0.2606 | 0 | 0 | 0 | 590.4 | 902 | 902 | 0.2606 | 0.2606 | 0.2606 | 0 | 0 | 0 |  | 14.6 | 14.6 | 14.6 | 4.8667 | 0.5 | 372.2067 | 182.0985 | 182.0985 | 70.2 | 61.3465 | 61.3465 | 0 | 0 | 0 | 1 | 1 | 0.082274 | 0.0066919 | [7 empty] | Low (2008) | Low (2008) | Low (2008) | None
M-068 | Lighting - Induction Fixture (Outdoor) | PGE | COM | Electric | COMLighting - Induction Fixture (Outdoor) | Exterior Induction Fixtures; 4 cases- 100W HID to 70W Induction; 101-175W HID to 100W Induction; 176-200W Induction to 120W Induction; 201-399W HID to 180W Induction; 400W HID to 250W Induction | Standard metal halide or high-pressure sodium | Standard metal halide or high-pressure sodium | Lighting | OutGen | Ltg_Wired | Induc_fixt | Outdoor | 1 | 0 | 0 | 0.9 | 61 | NA | 1 | NA | Fixtures | WRF | WAREHOUSE - REFRIGERATED | New | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.077363 | 0.011603 | 0.088966 | Fixtures/1000 sf | 590.4 | 902 | 902 | 0.2606 | 0.2606 | 0.2606 | 0 | 0 | 0 | 590.4 | 902 | 902 | 0.2606 | 0.2606 | 0.2606 | 0 | 0 | 0 |  | 14.6 | 14.6 | 14.6 | 4.8667 | 0.5 | 372.2067 | 182.0985 | 182.0985 | 70.2 | 61.3465 | 61.3465 | 0 | 0 | 0 | 1 | 1 | 0.082274 | 0.0066919 | [7 empty] | Low (2008) | Low (2008) | Low (2008) | None
M-068 | Lighting - Induction Fixture (Outdoor) | PGE | COM | Electric | COMLighting - Induction Fixture (Outdoor) | Exterior Induction Fixtures; 4 cases- 100W HID to 70W Induction; 101-175W HID to 100W Induction; 176-200W Induction to 120W Induction; 201-399W HID to 180W Induction; 400W HID to 250W Induction | Standard metal halide or high-pressure sodium | Standard metal halide or high-pressure sodium | Lighting | OutGen | Ltg_Wired | Induc_fixt | Outdoor | 1 | 0 | 0 | 0.9 | 61 | NA | 1 | NA | Fixtures | WRF | WAREHOUSE - REFRIGERATED | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.077363 | 0.011603 | 0.088966 | Fixtures/1000 sf | 590.4 | 902 | 902 | 0.2606 | 0.2606 | 0.2606 | 0 | 0 | 0 | 590.4 | 902 | 902 | 0.2606 | 0.2606 | 0.2606 | 0 | 0 | 0 |  | 14.6 | 14.6 | 14.6 | 4.8667 | 0.5 | 372.2067 | 182.0985 | 182.0985 | 70.2 | 61.3465 | 61.3465 | 0 | 0 | 0 | 1 | 1 | 0.082274 | 0.0066919 | [7 empty] | Low (2008) | Low (2008) | Low (2008) | None
M-068 | Lighting - Induction Fixture (Outdoor) | PGE | COM | Electric | COMLighting - Induction Fixture (Outdoor) | Exterior Induction Fixtures; 4 cases- 100W HID to 70W Induction; 101-175W HID to 100W Induction; 176-200W Induction to 120W Induction; 201-399W HID to 180W Induction; 400W HID to 250W Induction | Standard metal halide or high-pressure sodium | Standard metal halide or high-pressure sodium | Lighting | OutGen | Ltg_Wired | Induc_fixt | Outdoor | 1 | 0 | 0 | 0.9 | 61 | NA | 1 | NA | Fixtures | WRF | WAREHOUSE - REFRIGERATED | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.077363 | 0.011603 | 0.088966 | Fixtures/1000 sf | 590.4 | 902 | 902 | 0.2606 | 0.2606 | 0.2606 | 0 | 0 | 0 | 590.4 | 902 | 902 | 0.2606 | 0.2606 | 0.2606 | 0 | 0 | 0 |  | 14.6 | 14.6 | 14.6 | 4.8667 | 0.5 | 372.2067 | 182.0985 | 182.0985 | 70.2 | 61.3465 | 61.3465 | 0 | 0 | 0 | 1 | 1 | 0.082274 | 0.0066919 | [7 empty] | Low (2008) | Low (2008) | Low (2008) | None
M-068 | Lighting - Induction Fixture (Outdoor) | PGE | COM | Electric | COMLighting - Induction Fixture (Outdoor) | Exterior Induction Fixtures; 4 cases- 100W HID to 70W Induction; 101-175W HID to 100W Induction; 176-200W Induction to 120W Induction; 201-399W HID to 180W Induction; 400W HID to 250W Induction | Standard metal halide or high-pressure sodium | Standard metal halide or high-pressure sodium | Lighting | OutGen | Ltg_Wired | Induc_fixt | Outdoor | 1 | 0 | 0 | 0.9 | 61 | NA | 1 | NA | Fixtures | WRF | WAREHOUSE - REFRIGERATED | Existing | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.077363 | 0.011603 | 0.088966 | Fixtures/1000 sf | 590.4 | 902 | 902 | 0.2606 | 0.2606 | 0.2606 | 0 | 0 | 0 | 590.4 | 902 | 902 | 0.2606 | 0.2606 | 0.2606 | 0 | 0 | 0 |  | 14.6 | 14.6 | 14.6 | 4.8667 | 0.5 | 372.2067 | 182.0985 | 182.0985 | 70.2 | 61.3465 | 61.3465 | 0 | 0 | 0 | 1 | 1 | 0.082274 | 0.0066919 | [7 empty] | Low (2008) | Low (2008) | Low (2008) | None
M-068 | Lighting - Induction Fixture (Outdoor) | PGE | COM | Electric | COMLighting - Induction Fixture (Outdoor) | Exterior Induction Fixtures; 4 cases- 100W HID to 70W Induction; 101-175W HID to 100W Induction; 176-200W Induction to 120W Induction; 201-399W HID to 180W Induction; 400W HID to 250W Induction | Standard metal halide or high-pressure sodium | Standard metal halide or high-pressure sodium | Lighting | OutGen | Ltg_Wired | Induc_fixt | Outdoor | 1 | 0 | 0 | 0.9 | 61 | NA | 1 | NA | Fixtures | WRF | WAREHOUSE - REFRIGERATED | New | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.077363 | 0.011603 | 0.088966 | Fixtures/1000 sf | 590.4 | 902 | 902 | 0.2606 | 0.2606 | 0.2606 | 0 | 0 | 0 | 590.4 | 902 | 902 | 0.2606 | 0.2606 | 0.2606 | 0 | 0 | 0 |  | 14.6 | 14.6 | 14.6 | 4.8667 | 0.5 | 372.2067 | 182.0985 | 182.0985 | 70.2 | 61.3465 | 61.3465 | 0 | 0 | 0 | 1 | 1 | 0.082274 | 0.0066919 | [7 empty] | Low (2008) | Low (2008) | Low (2008) | None
M-068 | Lighting - Induction Fixture (Outdoor) | PGE | COM | Electric | COMLighting - Induction Fixture (Outdoor) | Exterior Induction Fixtures; 4 cases- 100W HID to 70W Induction; 101-175W HID to 100W Induction; 176-200W Induction to 120W Induction; 201-399W HID to 180W Induction; 400W HID to 250W Induction | Standard metal halide or high-pressure sodium | Standard metal halide or high-pressure sodium | Lighting | OutGen | Ltg_Wired | Induc_fixt | Outdoor | 1 | 0 | 0 | 0.9 | 61 | NA | 1 | NA | Fixtures | WRF | WAREHOUSE - REFRIGERATED | New | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.077363 | 0.011603 | 0.088966 | Fixtures/1000 sf | 590.4 | 902 | 902 | 0.2606 | 0.2606 | 0.2606 | 0 | 0 | 0 | 590.4 | 902 | 902 | 0.2606 | 0.2606 | 0.2606 | 0 | 0 | 0 |  | 14.6 | 14.6 | 14.6 | 4.8667 | 0.5 | 372.2067 | 182.0985 | 182.0985 | 70.2 | 61.3465 | 61.3465 | 0 | 0 | 0 | 1 | 1 | 0.082274 | 0.0066919 | [7 empty] | Low (2008) | Low (2008) | Low (2008) | None
M-068 | Lighting - Induction Fixture (Outdoor) | PGE | COM | Electric | COMLighting - Induction Fixture (Outdoor) | Exterior Induction Fixtures; 4 cases- 100W HID to 70W Induction; 101-175W HID to 100W Induction; 176-200W Induction to 120W Induction; 201-399W HID to 180W Induction; 400W HID to 250W Induction | Standard metal halide or high-pressure sodium | Standard metal halide or high-pressure sodium | Lighting | OutGen | Ltg_Wired | Induc_fixt | Outdoor | 1 | 0 | 0 | 0.9 | 61 | NA | 1 | NA | Fixtures | WRF | WAREHOUSE - REFRIGERATED | Existing | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.077363 | 0.011603 | 0.088966 | Fixtures/1000 sf | 590.4 | 902 | 902 | 0.2606 | 0.2606 | 0.2606 | 0 | 0 | 0 | 590.4 | 902 | 902 | 0.2606 | 0.2606 | 0.2606 | 0 | 0 | 0 |  | 14.6 | 14.6 | 14.6 | 4.8667 | 0.5 | 372.2067 | 182.0985 | 182.0985 | 70.2 | 61.3465 | 61.3465 | 0 | 0 | 0 | 1 | 1 | 0.082274 | 0.0066919 | [7 empty] | Low (2008) | Low (2008) | Low (2008) | None
M-068 | Lighting - Induction Fixture (Outdoor) | PGE | COM | Electric | COMLighting - Induction Fixture (Outdoor) | Exterior Induction Fixtures; 4 cases- 100W HID to 70W Induction; 101-175W HID to 100W Induction; 176-200W Induction to 120W Induction; 201-399W HID to 180W Induction; 400W HID to 250W Induction | Standard metal halide or high-pressure sodium | Standard metal halide or high-pressure sodium | Lighting | OutGen | Ltg_Wired | Induc_fixt | Outdoor | 1 | 0 | 0 | 0.9 | 61 | NA | 1 | NA | Fixtures | WRF | WAREHOUSE - REFRIGERATED | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.077363 | 0.011603 | 0.088966 | Fixtures/1000 sf | 590.4 | 902 | 902 | 0.2606 | 0.2606 | 0.2606 | 0 | 0 | 0 | 590.4 | 902 | 902 | 0.2606 | 0.2606 | 0.2606 | 0 | 0 | 0 |  | 14.6 | 14.6 | 14.6 | 4.8667 | 0.5 | 372.2067 | 182.0985 | 182.0985 | 70.2 | 61.3465 | 61.3465 | 0 | 0 | 0 | 1 | 1 | 0.082274 | 0.0066919 | [7 empty] | Low (2008) | Low (2008) | Low (2008) | None
M-068 | Lighting - Induction Fixture (Outdoor) | PGE | COM | Electric | COMLighting - Induction Fixture (Outdoor) | Exterior Induction Fixtures; 4 cases- 100W HID to 70W Induction; 101-175W HID to 100W Induction; 176-200W Induction to 120W Induction; 201-399W HID to 180W Induction; 400W HID to 250W Induction | Standard metal halide or high-pressure sodium | Standard metal halide or high-pressure sodium | Lighting | OutGen | Ltg_Wired | Induc_fixt | Outdoor | 1 | 0 | 0 | 0.9 | 61 | NA | 1 | NA | Fixtures | WRF | WAREHOUSE - REFRIGERATED | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.077363 | 0.011603 | 0.088966 | Fixtures/1000 sf | 590.4 | 902 | 902 | 0.2606 | 0.2606 | 0.2606 | 0 | 0 | 0 | 590.4 | 902 | 902 | 0.2606 | 0.2606 | 0.2606 | 0 | 0 | 0 |  | 14.6 | 14.6 | 14.6 | 4.8667 | 0.5 | 372.2067 | 182.0985 | 182.0985 | 70.2 | 61.3465 | 61.3465 | 0 | 0 | 0 | 1 | 1 | 0.082274 | 0.0066919 | [7 empty] | Low (2008) | Low (2008) | Low (2008) | None
M-068 | Lighting - Induction Fixture (Outdoor) | PGE | COM | Electric | COMLighting - Induction Fixture (Outdoor) | Exterior Induction Fixtures; 4 cases- 100W HID to 70W Induction; 101-175W HID to 100W Induction; 176-200W Induction to 120W Induction; 201-399W HID to 180W Induction; 400W HID to 250W Induction | Standard metal halide or high-pressure sodium | Standard metal halide or high-pressure sodium | Lighting | OutGen | Ltg_Wired | Induc_fixt | Outdoor | 1 | 0 | 0 | 0.9 | 61 | NA | 1 | NA | Fixtures | WRF | WAREHOUSE - REFRIGERATED | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.077363 | 0.011603 | 0.088966 | Fixtures/1000 sf | 590.4 | 902 | 902 | 0.2606 | 0.2606 | 0.2606 | 0 | 0 | 0 | 590.4 | 902 | 902 | 0.2606 | 0.2606 | 0.2606 | 0 | 0 | 0 |  | 14.6 | 14.6 | 14.6 | 4.8667 | 0.5 | 372.2067 | 182.0985 | 182.0985 | 70.2 | 61.3465 | 61.3465 | 0 | 0 | 0 | 1 | 1 | 0.082274 | 0.0066919 | [7 empty] | Low (2008) | Low (2008) | Low (2008) | None
M-068 | Lighting - Induction Fixture (Outdoor) | PGE | COM | Electric | COMLighting - Induction Fixture (Outdoor) | Exterior Induction Fixtures; 4 cases- 100W HID to 70W Induction; 101-175W HID to 100W Induction; 176-200W Induction to 120W Induction; 201-399W HID to 180W Induction; 400W HID to 250W Induction | Standard metal halide or high-pressure sodium | Standard metal halide or high-pressure sodium | Lighting | OutGen | Ltg_Wired | Induc_fixt | Outdoor | 1 | 0 | 0 | 0.9 | 61 | NA | 1 | NA | Fixtures | WRF | WAREHOUSE - REFRIGERATED | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.077363 | 0.011603 | 0.088966 | Fixtures/1000 sf | 590.4 | 902 | 902 | 0.2606 | 0.2606 | 0.2606 | 0 | 0 | 0 | 590.4 | 902 | 902 | 0.2606 | 0.2606 | 0.2606 | 0 | 0 | 0 |  | 14.6 | 14.6 | 14.6 | 4.8667 | 0.5 | 372.2067 | 182.0985 | 182.0985 | 70.2 | 61.3465 | 61.3465 | 0 | 0 | 0 | 1 | 1 | 0.082274 | 0.0066919 | [7 empty] | Low (2008) | Low (2008) | Low (2008) | None
M-068 | Lighting - Induction Fixture (Outdoor) | SCE | COM | Electric | COMLighting - Induction Fixture (Outdoor) | Exterior Induction Fixtures; 4 cases- 100W HID to 70W Induction; 101-175W HID to 100W Induction; 176-200W Induction to 120W Induction; 201-399W HID to 180W Induction; 400W HID to 250W Induction | Standard metal halide or high-pressure sodium | Standard metal halide or high-pressure sodium | Lighting | OutGen | Ltg_Wired | Induc_fixt | Outdoor | 1 | 0 | 0 | 0.9 | 61 | NA | 1 | NA | Fixtures | WRF | WAREHOUSE - REFRIGERATED | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.078051 | 0.010915 | 0.088966 | Fixtures/1000 sf | 192.72 | 416.1 | 416.1 | 0.044 | 0.095 | 0.095 | 0 | 0 | 0 | 192.72 | 416.1 | 416.1 | 0.044 | 0.095 | 0.095 | 0 | 0 | 0 |  | 15 | 15 | 15 | 5 | 0.5 | 372.2067 | 182.0985 | 182.0985 | 0 | 61.3465 | 61.3465 | 0 | 0 | 0 | 1 | 1 | 0.082868 | 0.0060986 | [7 empty] | Low (2008) | Low (2008) | Low (2008) | None
M-068 | Lighting - Induction Fixture (Outdoor) | SCE | COM | Electric | COMLighting - Induction Fixture (Outdoor) | Exterior Induction Fixtures; 4 cases- 100W HID to 70W Induction; 101-175W HID to 100W Induction; 176-200W Induction to 120W Induction; 201-399W HID to 180W Induction; 400W HID to 250W Induction | Standard metal halide or high-pressure sodium | Standard metal halide or high-pressure sodium | Lighting | OutGen | Ltg_Wired | Induc_fixt | Outdoor | 1 | 0 | 0 | 0.9 | 61 | NA | 1 | NA | Fixtures | WRF | WAREHOUSE - REFRIGERATED | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.078051 | 0.010915 | 0.088966 | Fixtures/1000 sf | 192.72 | 416.1 | 416.1 | 0.044 | 0.095 | 0.095 | 0 | 0 | 0 | 192.72 | 416.1 | 416.1 | 0.044 | 0.095 | 0.095 | 0 | 0 | 0 |  | 15 | 15 | 15 | 5 | 0.5 | 372.2067 | 182.0985 | 182.0985 | 0 | 61.3465 | 61.3465 | 0 | 0 | 0 | 1 | 1 | 0.082868 | 0.0060986 | [7 empty] | Low (2008) | Low (2008) | Low (2008) | None
M-068 | Lighting - Induction Fixture (Outdoor) | SCE | COM | Electric | COMLighting - Induction Fixture (Outdoor) | Exterior Induction Fixtures; 4 cases- 100W HID to 70W Induction; 101-175W HID to 100W Induction; 176-200W Induction to 120W Induction; 201-399W HID to 180W Induction; 400W HID to 250W Induction | Standard metal halide or high-pressure sodium | Standard metal halide or high-pressure sodium | Lighting | OutGen | Ltg_Wired | Induc_fixt | Outdoor | 1 | 0 | 0 | 0.9 | 61 | NA | 1 | NA | Fixtures | WRF | WAREHOUSE - REFRIGERATED | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.078051 | 0.010915 | 0.088966 | Fixtures/1000 sf | 192.72 | 416.1 | 416.1 | 0.044 | 0.095 | 0.095 | 0 | 0 | 0 | 192.72 | 416.1 | 416.1 | 0.044 | 0.095 | 0.095 | 0 | 0 | 0 |  | 15 | 15 | 15 | 5 | 0.5 | 372.2067 | 182.0985 | 182.0985 | 0 | 61.3465 | 61.3465 | 0 | 0 | 0 | 1 | 1 | 0.082868 | 0.0060986 | [7 empty] | Low (2008) | Low (2008) | Low (2008) | None
M-068 | Lighting - Induction Fixture (Outdoor) | SCE | COM | Electric | COMLighting - Induction Fixture (Outdoor) | Exterior Induction Fixtures; 4 cases- 100W HID to 70W Induction; 101-175W HID to 100W Induction; 176-200W Induction to 120W Induction; 201-399W HID to 180W Induction; 400W HID to 250W Induction | Standard metal halide or high-pressure sodium | Standard metal halide or high-pressure sodium | Lighting | OutGen | Ltg_Wired | Induc_fixt | Outdoor | 1 | 0 | 0 | 0.9 | 61 | NA | 1 | NA | Fixtures | WRF | WAREHOUSE - REFRIGERATED | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.078051 | 0.010915 | 0.088966 | Fixtures/1000 sf | 192.72 | 416.1 | 416.1 | 0.044 | 0.095 | 0.095 | 0 | 0 | 0 | 192.72 | 416.1 | 416.1 | 0.044 | 0.095 | 0.095 | 0 | 0 | 0 |  | 15 | 15 | 15 | 5 | 0.5 | 372.2067 | 182.0985 | 182.0985 | 0 | 61.3465 | 61.3465 | 0 | 0 | 0 | 1 | 1 | 0.082868 | 0.0060986 | [7 empty] | Low (2008) | Low (2008) | Low (2008) | None
M-068 | Lighting - Induction Fixture (Outdoor) | SCE | COM | Electric | COMLighting - Induction Fixture (Outdoor) | Exterior Induction Fixtures; 4 cases- 100W HID to 70W Induction; 101-175W HID to 100W Induction; 176-200W Induction to 120W Induction; 201-399W HID to 180W Induction; 400W HID to 250W Induction | Standard metal halide or high-pressure sodium | Standard metal halide or high-pressure sodium | Lighting | OutGen | Ltg_Wired | Induc_fixt | Outdoor | 1 | 0 | 0 | 0.9 | 61 | NA | 1 | NA | Fixtures | WRF | WAREHOUSE - REFRIGERATED | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.078051 | 0.010915 | 0.088966 | Fixtures/1000 sf | 192.72 | 416.1 | 416.1 | 0.044 | 0.095 | 0.095 | 0 | 0 | 0 | 192.72 | 416.1 | 416.1 | 0.044 | 0.095 | 0.095 | 0 | 0 | 0 |  | 15 | 15 | 15 | 5 | 0.5 | 372.2067 | 182.0985 | 182.0985 | 0 | 61.3465 | 61.3465 | 0 | 0 | 0 | 1 | 1 | 0.082868 | 0.0060986 | [7 empty] | Low (2008) | Low (2008) | Low (2008) | None
M-068 | Lighting - Induction Fixture (Outdoor) | SCE | COM | Electric | COMLighting - Induction Fixture (Outdoor) | Exterior Induction Fixtures; 4 cases- 100W HID to 70W Induction; 101-175W HID to 100W Induction; 176-200W Induction to 120W Induction; 201-399W HID to 180W Induction; 400W HID to 250W Induction | Standard metal halide or high-pressure sodium | Standard metal halide or high-pressure sodium | Lighting | OutGen | Ltg_Wired | Induc_fixt | Outdoor | 1 | 0 | 0 | 0.9 | 61 | NA | 1 | NA | Fixtures | WRF | WAREHOUSE - REFRIGERATED | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.078051 | 0.010915 | 0.088966 | Fixtures/1000 sf | 192.72 | 416.1 | 416.1 | 0.044 | 0.095 | 0.095 | 0 | 0 | 0 | 192.72 | 416.1 | 416.1 | 0.044 | 0.095 | 0.095 | 0 | 0 | 0 |  | 15 | 15 | 15 | 5 | 0.5 | 372.2067 | 182.0985 | 182.0985 | 0 | 61.3465 | 61.3465 | 0 | 0 | 0 | 1 | 1 | 0.082868 | 0.0060986 | [7 empty] | Low (2008) | Low (2008) | Low (2008) | None
M-068 | Lighting - Induction Fixture (Outdoor) | SCE | COM | Electric | COMLighting - Induction Fixture (Outdoor) | Exterior Induction Fixtures; 4 cases- 100W HID to 70W Induction; 101-175W HID to 100W Induction; 176-200W Induction to 120W Induction; 201-399W HID to 180W Induction; 400W HID to 250W Induction | Standard metal halide or high-pressure sodium | Standard metal halide or high-pressure sodium | Lighting | OutGen | Ltg_Wired | Induc_fixt | Outdoor | 1 | 0 | 0 | 0.9 | 61 | NA | 1 | NA | Fixtures | WRF | WAREHOUSE - REFRIGERATED | Existing | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 0.078051 | 0.010915 | 0.088966 | Fixtures/1000 sf | 192.72 | 416.1 | 416.1 | 0.044 | 0.095 | 0.095 | 0 | 0 | 0 | 192.72 | 416.1 | 416.1 | 0.044 | 0.095 | 0.095 | 0 | 0 | 0 |  | 15 | 15 | 15 | 5 | 0.5 | 372.2067 | 182.0985 | 182.0985 | 0 | 61.3465 | 61.3465 | 0 | 0 | 0 | 1 | 1 | 0.082868 | 0.0060986 | [7 empty] | Low (2008) | Low (2008) | Low (2008) | None
M-068 | Lighting - Induction Fixture (Outdoor) | SDGE | COM | Electric | COMLighting - Induction Fixture (Outdoor) | Exterior Induction Fixtures; 4 cases- 100W HID to 70W Induction; 101-175W HID to 100W Induction; 176-200W Induction to 120W Induction; 201-399W HID to 180W Induction; 400W HID to 250W Induction | Standard metal halide or high-pressure sodium | Standard metal halide or high-pressure sodium | Lighting | OutGen | Ltg_Wired | Induc_fixt | Outdoor | 1 | 0 | 0 | 0.9 | 61 | NA | 1 | NA | Fixtures | WRF | WAREHOUSE - REFRIGERATED | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.10227 | 0.012474 | 0.11474 | Fixtures/1000 sf | 192.72 | 416.1 | 416.1 | 0.044 | 0.095 | 0.095 | 0 | 0 | 0 | 192.72 | 416.1 | 416.1 | 0.044 | 0.095 | 0.095 | 0 | 0 | 0 |  | 15 | 15 | 15 | 5 | 0.5 | 372.2067 | 182.0985 | 182.0985 | 0 | 61.3465 | 61.3465 | 0 | 0 | 0 | 1 | 1 | 0.10833 | 0.0064159 | [7 empty] | Low (2008) | Low (2008) | Low (2008) | None
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ASM | ASSEMBLY | New | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 4.099 | 0.025938 | 5.1876 | Fixture/1000 sf | 77.2944 | 242.8294 | 242.8294 | 0.015755 | 0.049496 | 0.049496 | 0 | 0 | 0 | 84.104 | 264.2226 | 264.2226 | 0.019664 | 0.061776 | 0.061776 | -0.45902 | -1.4421 | -1.4421 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ASM | ASSEMBLY | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 4.099 | 0.025938 | 5.1876 | Fixture/1000 sf | 77.2944 | 242.8294 | 242.8294 | 0.015755 | 0.049495 | 0.049495 | 0 | 0 | 0 | 84.104 | 264.2226 | 264.2226 | 0.018835 | 0.059171 | 0.059171 | -0.44421 | -1.3955 | -1.3955 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ASM | ASSEMBLY | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 4.099 | 0.025938 | 5.1876 | Fixture/1000 sf | 77.2944 | 242.8294 | 242.8294 | 0.015755 | 0.049495 | 0.049495 | 0 | 0 | 0 | 84.104 | 264.2226 | 264.2226 | 0.019397 | 0.060939 | 0.060939 | -0.46494 | -1.4607 | -1.4607 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ASM | ASSEMBLY | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 4.099 | 0.025938 | 5.1876 | Fixture/1000 sf | 77.2926 | 242.8236 | 242.8236 | 0.015755 | 0.049496 | 0.049496 | 0 | 0 | 0 | 76.7005 | 240.9636 | 240.9636 | 0.018775 | 0.058985 | 0.058985 | -1.0987 | -3.4516 | -3.4516 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ASM | ASSEMBLY | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 3.5299 | 0.018679 | 3.7358 | Fixture/1000 sf | 75.5205 | 243.7554 | 243.7554 | 0.015393 | 0.049684 | 0.049684 | 0 | 0 | 0 | 83.0423 | 268.0334 | 268.0334 | 0.018981 | 0.061265 | 0.061265 | -0.42245 | -1.3635 | -1.3635 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ASM | ASSEMBLY | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 3.5299 | 0.018679 | 3.7358 | Fixture/1000 sf | 75.5209 | 243.7567 | 243.7567 | 0.015393 | 0.049683 | 0.049683 | 0 | 0 | 0 | 82.1743 | 265.2317 | 265.2317 | 0.018865 | 0.060891 | 0.060891 | -0.51504 | -1.6624 | -1.6624 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ASM | ASSEMBLY | New | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 3.5299 | 0.018679 | 3.7358 | Fixture/1000 sf | 75.5183 | 243.7484 | 243.7484 | 0.015393 | 0.049683 | 0.049683 | 0 | 0 | 0 | 82.753 | 267.0995 | 267.0995 | 0.018865 | 0.060891 | 0.060891 | -0.47163 | -1.5223 | -1.5223 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ASM | ASSEMBLY | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 3.5299 | 0.018679 | 3.7358 | Fixture/1000 sf | 75.5201 | 243.7541 | 243.7541 | 0.015393 | 0.049683 | 0.049683 | 0 | 0 | 0 | 83.9104 | 270.8352 | 270.8352 | 0.018431 | 0.05949 | 0.05949 | -0.3559 | -1.1487 | -1.1487 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | EPR | EDUCATION - PRIMARY SCHOOL | Existing | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 4.6186 | 0.028286 | 5.6572 | Fixture/1000 sf | 66.7156 | 183.6582 | 183.6582 | 0.00062352 | 0.0017165 | 0.0017165 | 0 | 0 | 0 | 70.4583 | 193.9614 | 193.9614 | 0.00062352 | 0.0017165 | 0.0017165 | -0.7077 | -1.9482 | -1.9482 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ERC | EDUCATION - RELOCATABLE CLASSROOM | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 5.093 | 0.036471 | 7.2942 | Fixture/1000 sf | 73.4403 | 230.7212 | 230.7212 | 0.020789 | 0.065311 | 0.065311 | 0 | 0 | 0 | 84.9924 | 267.0137 | 267.0137 | 0.027067 | 0.085035 | 0.085035 | -0.46494 | -1.4607 | -1.4607 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ERC | EDUCATION - RELOCATABLE CLASSROOM | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 5.093 | 0.036471 | 7.2942 | Fixture/1000 sf | 73.4453 | 230.7369 | 230.7369 | 0.020789 | 0.06531 | 0.06531 | 0 | 0 | 0 | 82.031 | 257.7101 | 257.7101 | 0.026682 | 0.083826 | 0.083826 | -0.39979 | -1.256 | -1.256 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ESE | EDUCATION - SECONDARY SCHOOL | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 5.093 | 0.036471 | 7.2942 | Fixture/1000 sf | 67.5201 | 212.1224 | 212.1224 | 0.00059228 | 0.0018607 | 0.0018607 | 0 | 0 | 0 | 67.5201 | 212.1224 | 212.1224 | 0.00059228 | 0.0018607 | 0.0018607 | -0.94765 | -2.9772 | -2.9772 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ESE | EDUCATION - SECONDARY SCHOOL | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 5.1904 | 0.026528 | 5.3056 | Fixture/1000 sf | 65.9713 | 212.9338 | 212.9338 | 0.020515 | 0.066217 | 0.066217 | 0 | 0 | 0 | 74.0726 | 239.0821 | 239.0821 | 0.026186 | 0.084519 | 0.084519 | -0.37326 | -1.2047 | -1.2047 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ESE | EDUCATION - SECONDARY SCHOOL | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 5.1904 | 0.026528 | 5.3056 | Fixture/1000 sf | 65.9687 | 212.9254 | 212.9254 | 0.020514 | 0.066214 | 0.066214 | 0 | 0 | 0 | 72.9152 | 235.3464 | 235.3464 | 0.027112 | 0.087508 | 0.087508 | -0.49189 | -1.5877 | -1.5877 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ESE | EDUCATION - SECONDARY SCHOOL | Existing | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 5.1904 | 0.026528 | 5.3056 | Fixture/1000 sf | 65.9713 | 212.9338 | 212.9338 | 0.020515 | 0.066215 | 0.066215 | 0 | 0 | 0 | 74.0726 | 239.0821 | 239.0821 | 0.025781 | 0.083212 | 0.083212 | -0.32696 | -1.0553 | -1.0553 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ERC | EDUCATION - RELOCATABLE CLASSROOM | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 5.1904 | 0.026528 | 5.3056 | Fixture/1000 sf | 71.7581 | 231.6114 | 231.6114 | 0.020312 | 0.065561 | 0.065561 | 0 | 0 | 0 | 79.8595 | 257.7604 | 257.7604 | 0.02552 | 0.082371 | 0.082371 | -0.43981 | -1.4195 | -1.4195 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ERC | EDUCATION - RELOCATABLE CLASSROOM | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 5.1904 | 0.026528 | 5.3056 | Fixture/1000 sf | 71.7595 | 231.6159 | 231.6159 | 0.020313 | 0.065563 | 0.065563 | 0 | 0 | 0 | 82.753 | 267.0995 | 267.0995 | 0.026273 | 0.084799 | 0.084799 | -0.46006 | -1.4849 | -1.4849 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ERC | EDUCATION - RELOCATABLE CLASSROOM | Existing | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 5.1904 | 0.026528 | 5.3056 | Fixture/1000 sf | 71.7599 | 231.6174 | 231.6174 | 0.020312 | 0.065561 | 0.065561 | 0 | 0 | 0 | 81.0169 | 261.496 | 261.496 | 0.025983 | 0.083866 | 0.083866 | -0.36458 | -1.1767 | -1.1767 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ERC | EDUCATION - RELOCATABLE CLASSROOM | New | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 5.1904 | 0.026528 | 5.3056 | Fixture/1000 sf | 71.7552 | 231.6024 | 231.6024 | 0.020312 | 0.06556 | 0.06556 | 0 | 0 | 0 | 83.0423 | 268.0334 | 268.0334 | 0.026446 | 0.08536 | 0.08536 | -0.36168 | -1.1674 | -1.1674 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ERC | EDUCATION - RELOCATABLE CLASSROOM | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 5.1904 | 0.026528 | 5.3056 | Fixture/1000 sf | 71.7581 | 231.6114 | 231.6114 | 0.020311 | 0.065558 | 0.065558 | 0 | 0 | 0 | 79.8595 | 257.7604 | 257.7604 | 0.02581 | 0.083305 | 0.083305 | -0.38483 | -1.2421 | -1.2421 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ERC | EDUCATION - RELOCATABLE CLASSROOM | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 5.1904 | 0.026528 | 5.3056 | Fixture/1000 sf | 71.759 | 231.6146 | 231.6146 | 0.020312 | 0.065559 | 0.065559 | 0 | 0 | 0 | 84.4891 | 272.703 | 272.703 | 0.02688 | 0.086761 | 0.086761 | -0.38772 | -1.2514 | -1.2514 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | EPR | EDUCATION - PRIMARY SCHOOL | New | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 4.6186 | 0.028286 | 5.6572 | Fixture/1000 sf | 66.7173 | 183.6629 | 183.6629 | 0.00062352 | 0.0017165 | 0.0017165 | 0 | 0 | 0 | 70.1466 | 193.1031 | 193.1031 | 0.00062352 | 0.0017165 | 0.0017165 | -0.85423 | -2.3516 | -2.3516 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | EPR | EDUCATION - PRIMARY SCHOOL | Existing | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 4.6186 | 0.028286 | 5.6572 | Fixture/1000 sf | 66.7185 | 183.6661 | 183.6661 | 0.00062352 | 0.0017165 | 0.0017165 | 0 | 0 | 0 | 71.0818 | 195.6778 | 195.6778 | 0.00062352 | 0.0017165 | 0.0017165 | -0.68588 | -1.8881 | -1.8881 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | EPR | EDUCATION - PRIMARY SCHOOL | New | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 4.6186 | 0.028286 | 5.6572 | Fixture/1000 sf | 66.7144 | 183.6548 | 183.6548 | 0.00062352 | 0.0017165 | 0.0017165 | 0 | 0 | 0 | 69.523 | 191.3867 | 191.3867 | 0.00062352 | 0.0017165 | 0.0017165 | -0.72017 | -1.9825 | -1.9825 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | EPR | EDUCATION - PRIMARY SCHOOL | Existing | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 4.6186 | 0.028286 | 5.6572 | Fixture/1000 sf | 66.7179 | 183.6646 | 183.6646 | 0.019204 | 0.052866 | 0.052866 | 0 | 0 | 0 | 72.3289 | 199.1108 | 199.1108 | 0.023694 | 0.065226 | 0.065226 | -0.53935 | -1.4847 | -1.4847 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | EPR | EDUCATION - PRIMARY SCHOOL | New | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 4.6186 | 0.028286 | 5.6572 | Fixture/1000 sf | 66.7151 | 183.6568 | 183.6568 | 0.019205 | 0.052868 | 0.052868 | 0 | 0 | 0 | 71.7054 | 197.3943 | 197.3943 | 0.025377 | 0.06986 | 0.06986 | -0.64535 | -1.7765 | -1.7765 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | EPR | EDUCATION - PRIMARY SCHOOL | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 4.6186 | 0.028286 | 5.6572 | Fixture/1000 sf | 66.7185 | 183.6661 | 183.6661 | 0.019204 | 0.052867 | 0.052867 | 0 | 0 | 0 | 71.0818 | 195.6778 | 195.6778 | 0.023195 | 0.063853 | 0.063853 | -0.64535 | -1.7765 | -1.7765 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | EPR | EDUCATION - PRIMARY SCHOOL | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 4.6186 | 0.028286 | 5.6572 | Fixture/1000 sf | 66.719 | 183.6676 | 183.6676 | 0.019204 | 0.052866 | 0.052866 | 0 | 0 | 0 | 69.8348 | 192.2449 | 192.2449 | 0.023975 | 0.065998 | 0.065998 | -0.62664 | -1.7251 | -1.7251 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | EPR | EDUCATION - PRIMARY SCHOOL | Existing | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 4.6186 | 0.028286 | 5.6572 | Fixture/1000 sf | 66.7185 | 183.6661 | 183.6661 | 0.00062352 | 0.0017165 | 0.0017165 | 0 | 0 | 0 | 71.0818 | 195.6778 | 195.6778 | 0.00062352 | 0.0017165 | 0.0017165 | -0.65158 | -1.7937 | -1.7937 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ERC | EDUCATION - RELOCATABLE CLASSROOM | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 4.6186 | 0.028286 | 5.6572 | Fixture/1000 sf | 77.3167 | 212.8416 | 212.8416 | 0.00062352 | 0.0017165 | 0.0017165 | 0 | 0 | 0 | 76.6936 | 211.1261 | 211.1261 | 0.00062352 | 0.0017165 | 0.0017165 | -1.2845 | -3.5359 | -3.5359 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ERC | EDUCATION - RELOCATABLE CLASSROOM | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 5.093 | 0.036471 | 7.2942 | Fixture/1000 sf | 73.4434 | 230.731 | 230.731 | 0.020789 | 0.065311 | 0.065311 | 0 | 0 | 0 | 80.8465 | 253.9886 | 253.9886 | 0.02683 | 0.084291 | 0.084291 | -0.72555 | -2.2794 | -2.2794 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ERC | EDUCATION - RELOCATABLE CLASSROOM | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 5.093 | 0.036471 | 7.2942 | Fixture/1000 sf | 73.442 | 230.7268 | 230.7268 | 0.020789 | 0.065313 | 0.065313 | 0 | 0 | 0 | 76.9966 | 241.8939 | 241.8939 | 0.02686 | 0.084384 | 0.084384 | -0.74924 | -2.3538 | -2.3538 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ERC | EDUCATION - RELOCATABLE CLASSROOM | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 5.093 | 0.036471 | 7.2942 | Fixture/1000 sf | 73.4453 | 230.7369 | 230.7369 | 0.020789 | 0.065312 | 0.065312 | 0 | 0 | 0 | 82.031 | 257.7101 | 257.7101 | 0.026357 | 0.082802 | 0.082802 | -0.4531 | -1.4235 | -1.4235 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ASM | ASSEMBLY | Existing | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 3.0079 | 0.015853 | 3.1706 | Fixture/1000 sf | 81.3676 | 223.9929 | 223.9929 | 0.016585 | 0.045656 | 0.045656 | 0 | 0 | 0 | 77.3171 | 212.8426 | 212.8426 | 0.018955 | 0.052181 | 0.052181 | -1.5619 | -4.2998 | -4.2998 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ASM | ASSEMBLY | New | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 3.0079 | 0.015853 | 3.1706 | Fixture/1000 sf | 81.3703 | 224.0003 | 224.0003 | 0.016585 | 0.045657 | 0.045657 | 0 | 0 | 0 | 77.6289 | 213.7008 | 213.7008 | 0.01908 | 0.052524 | 0.052524 | -1.5463 | -4.2569 | -4.2569 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ASM | ASSEMBLY | Existing | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 3.0079 | 0.015853 | 3.1706 | Fixture/1000 sf | 81.3686 | 223.9959 | 223.9959 | 0.016586 | 0.045659 | 0.045659 | 0 | 0 | 0 | 84.1759 | 231.7238 | 231.7238 | 0.019329 | 0.053211 | 0.053211 | -0.87917 | -2.4202 | -2.4202 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ASM | ASSEMBLY | New | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 3.0079 | 0.015853 | 3.1706 | Fixture/1000 sf | 81.3666 | 223.9902 | 223.9902 | 0.016586 | 0.045659 | 0.045659 | 0 | 0 | 0 | 82.9288 | 228.2908 | 228.2908 | 0.019454 | 0.053554 | 0.053554 | -0.96023 | -2.6434 | -2.6434 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ASM | ASSEMBLY | Existing | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 3.0079 | 0.015853 | 3.1706 | Fixture/1000 sf | 81.3691 | 223.9971 | 223.9971 | 0.016586 | 0.045658 | 0.045658 | 0 | 0 | 0 | 83.2406 | 229.1491 | 229.1491 | 0.01936 | 0.053296 | 0.053296 | -0.96958 | -2.6691 | -2.6691 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ASM | ASSEMBLY | New | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 3.0079 | 0.015853 | 3.1706 | Fixture/1000 sf | 81.3695 | 223.9984 | 223.9984 | 0.016586 | 0.04566 | 0.04566 | 0 | 0 | 0 | 82.3053 | 226.5744 | 226.5744 | 0.019142 | 0.052696 | 0.052696 | -1.0163 | -2.7978 | -2.7978 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ASM | ASSEMBLY | Existing | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 3.0079 | 0.015853 | 3.1706 | Fixture/1000 sf | 81.3707 | 224.0014 | 224.0014 | 0.016586 | 0.045659 | 0.045659 | 0 | 0 | 0 | 85.4229 | 235.1567 | 235.1567 | 0.019298 | 0.053125 | 0.053125 | -0.72329 | -1.9911 | -1.9911 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ASM | ASSEMBLY | New | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 3.0079 | 0.015853 | 3.1706 | Fixture/1000 sf | 81.3686 | 223.9959 | 223.9959 | 0.016586 | 0.045659 | 0.045659 | 0 | 0 | 0 | 84.1759 | 231.7238 | 231.7238 | 0.019329 | 0.053211 | 0.053211 | -0.79499 | -2.1885 | -2.1885 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ASM | ASSEMBLY | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 3.0079 | 0.015853 | 3.1706 | Fixture/1000 sf | 81.3662 | 223.9891 | 223.9891 | 0.016586 | 0.045659 | 0.045659 | 0 | 0 | 0 | 83.8641 | 230.8655 | 230.8655 | 0.019018 | 0.052352 | 0.052352 | -0.86982 | -2.3945 | -2.3945 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ASM | ASSEMBLY | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 3.0079 | 0.015853 | 3.1706 | Fixture/1000 sf | 81.3666 | 223.9902 | 223.9902 | 0.016585 | 0.045657 | 0.045657 | 0 | 0 | 0 | 82.9288 | 228.2908 | 228.2908 | 0.018924 | 0.052095 | 0.052095 | -0.88541 | -2.4374 | -2.4374 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ASM | ASSEMBLY | Existing | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 3.0079 | 0.015853 | 3.1706 | Fixture/1000 sf | 81.3707 | 224.0014 | 224.0014 | 0.016586 | 0.045659 | 0.045659 | 0 | 0 | 0 | 85.4229 | 235.1567 | 235.1567 | 0.019298 | 0.053125 | 0.053125 | -0.7607 | -2.0941 | -2.0941 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ASM | ASSEMBLY | New | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 3.0079 | 0.015853 | 3.1706 | Fixture/1000 sf | 81.3736 | 224.0094 | 224.0094 | 0.016586 | 0.045658 | 0.045658 | 0 | 0 | 0 | 84.7994 | 233.4402 | 233.4402 | 0.019672 | 0.054155 | 0.054155 | -0.82305 | -2.2657 | -2.2657 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ASM | ASSEMBLY | Existing | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 3.0079 | 0.015853 | 3.1706 | Fixture/1000 sf | 81.3736 | 224.0094 | 224.0094 | 0.016586 | 0.045659 | 0.045659 | 0 | 0 | 0 | 84.7994 | 233.4402 | 233.4402 | 0.019454 | 0.053554 | 0.053554 | -0.80435 | -2.2142 | -2.2142 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ASM | ASSEMBLY | New | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 3.0079 | 0.015853 | 3.1706 | Fixture/1000 sf | 81.3711 | 224.0027 | 224.0027 | 0.016586 | 0.045659 | 0.045659 | 0 | 0 | 0 | 84.4876 | 232.582 | 232.582 | 0.019641 | 0.054069 | 0.054069 | -0.87917 | -2.4202 | -2.4202 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ASM | ASSEMBLY | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 3.0079 | 0.015853 | 3.1706 | Fixture/1000 sf | 81.3707 | 224.0014 | 224.0014 | 0.016585 | 0.045656 | 0.045656 | 0 | 0 | 0 | 85.4229 | 235.1567 | 235.1567 | 0.019267 | 0.053039 | 0.053039 | -0.73888 | -2.034 | -2.034 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ASM | ASSEMBLY | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 3.0079 | 0.015853 | 3.1706 | Fixture/1000 sf | 81.3682 | 223.9947 | 223.9947 | 0.016586 | 0.045659 | 0.045659 | 0 | 0 | 0 | 85.1112 | 234.2985 | 234.2985 | 0.019641 | 0.054069 | 0.054069 | -0.79811 | -2.1971 | -2.1971 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ASM | ASSEMBLY | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 3.0079 | 0.015853 | 3.1706 | Fixture/1000 sf | 81.3685 | 223.9954 | 223.9954 | 0.016586 | 0.045659 | 0.045659 | 0 | 0 | 0 | 79.4994 | 218.8502 | 218.8502 | 0.019018 | 0.052352 | 0.052352 | -1.1629 | -3.2012 | -3.2012 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ASM | ASSEMBLY | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 3.0079 | 0.015853 | 3.1706 | Fixture/1000 sf | 81.3702 | 224.0003 | 224.0003 | 0.016586 | 0.045658 | 0.045658 | 0 | 0 | 0 | 79.8112 | 219.7085 | 219.7085 | 0.019049 | 0.052438 | 0.052438 | -1.1722 | -3.227 | -3.227 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ASM | ASSEMBLY | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 4.099 | 0.025938 | 5.1876 | Fixture/1000 sf | 77.2957 | 242.8335 | 242.8335 | 0.015755 | 0.049495 | 0.049495 | 0 | 0 | 0 | 81.4388 | 255.8494 | 255.8494 | 0.018835 | 0.059171 | 0.059171 | -0.79662 | -2.5027 | -2.5027 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ASM | ASSEMBLY | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 4.099 | 0.025938 | 5.1876 | Fixture/1000 sf | 77.2938 | 242.8276 | 242.8276 | 0.015754 | 0.049493 | 0.049493 | 0 | 0 | 0 | 80.2542 | 252.1279 | 252.1279 | 0.018598 | 0.058427 | 0.058427 | -0.82031 | -2.5771 | -2.5771 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ASM | ASSEMBLY | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 4.099 | 0.025938 | 5.1876 | Fixture/1000 sf | 77.3069 | 242.8687 | 242.8687 | 0.015755 | 0.049496 | 0.049496 | 0 | 0 | 0 | 86.7693 | 272.5959 | 272.5959 | 0.019516 | 0.061311 | 0.061311 | -0.38498 | -1.2095 | -1.2095 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ASM | ASSEMBLY | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 4.099 | 0.025938 | 5.1876 | Fixture/1000 sf | 77.2922 | 242.8223 | 242.8223 | 0.015755 | 0.049496 | 0.049496 | 0 | 0 | 0 | 83.8079 | 263.2923 | 263.2923 | 0.01922 | 0.06038 | 0.06038 | -0.49159 | -1.5444 | -1.5444 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ASM | ASSEMBLY | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 4.099 | 0.025938 | 5.1876 | Fixture/1000 sf | 77.3111 | 242.8819 | 242.8819 | 0.015754 | 0.049494 | 0.049494 | 0 | 0 | 0 | 87.3616 | 274.4566 | 274.4566 | 0.019012 | 0.059729 | 0.059729 | -0.33168 | -1.042 | -1.042 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ASM | ASSEMBLY | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 4.099 | 0.025938 | 5.1876 | Fixture/1000 sf | 77.2918 | 242.8211 | 242.8211 | 0.015755 | 0.049496 | 0.049496 | 0 | 0 | 0 | 84.6963 | 266.0833 | 266.0833 | 0.018923 | 0.05945 | 0.05945 | -0.40275 | -1.2653 | -1.2653 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ASM | ASSEMBLY | Existing | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 4.099 | 0.025938 | 5.1876 | Fixture/1000 sf | 77.3069 | 242.8687 | 242.8687 | 0.015755 | 0.049496 | 0.049496 | 0 | 0 | 0 | 86.7693 | 272.5959 | 272.5959 | 0.019516 | 0.061311 | 0.061311 | -0.40275 | -1.2653 | -1.2653 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ASM | ASSEMBLY | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 4.099 | 0.025938 | 5.1876 | Fixture/1000 sf | 77.2903 | 242.8165 | 242.8165 | 0.015755 | 0.049497 | 0.049497 | 0 | 0 | 0 | 82.6233 | 259.5708 | 259.5708 | 0.019042 | 0.059822 | 0.059822 | -0.69889 | -2.1957 | -2.1957 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ASM | ASSEMBLY | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 4.099 | 0.025938 | 5.1876 | Fixture/1000 sf | 77.2903 | 242.8165 | 242.8165 | 0.015755 | 0.049497 | 0.049497 | 0 | 0 | 0 | 82.6233 | 259.5708 | 259.5708 | 0.019486 | 0.061218 | 0.061218 | -0.74628 | -2.3445 | -2.3445 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ASM | ASSEMBLY | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 4.099 | 0.025938 | 5.1876 | Fixture/1000 sf | 77.2926 | 242.8236 | 242.8236 | 0.015754 | 0.049494 | 0.049494 | 0 | 0 | 0 | 82.9195 | 260.5012 | 260.5012 | 0.017828 | 0.056008 | 0.056008 | -0.69889 | -2.1957 | -2.1957 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ECC | EDUCATION - COMMUNITY COLLEGE | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 5.093 | 0.036471 | 7.2942 | Fixture/1000 sf | 71.6661 | 225.1473 | 225.1473 | 0.014422 | 0.04531 | 0.04531 | 0 | 0 | 0 | 80.8465 | 253.9886 | 253.9886 | 0.018598 | 0.058427 | 0.058427 | -0.61597 | -1.9352 | -1.9352 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ECC | EDUCATION - COMMUNITY COLLEGE | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 5.093 | 0.036471 | 7.2942 | Fixture/1000 sf | 71.6679 | 225.153 | 225.153 | 0.014422 | 0.045308 | 0.045308 | 0 | 0 | 0 | 82.031 | 257.7101 | 257.7101 | 0.01996 | 0.062706 | 0.062706 | -0.5982 | -1.8793 | -1.8793 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ECC | EDUCATION - COMMUNITY COLLEGE | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 5.093 | 0.036471 | 7.2942 | Fixture/1000 sf | 71.664 | 225.1408 | 225.1408 | 0.023869 | 0.074988 | 0.074988 | 0 | 0 | 0 | 80.5503 | 253.0583 | 253.0583 | 0.030503 | 0.095827 | 0.095827 | -0.64559 | -2.0282 | -2.0282 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ECC | EDUCATION - COMMUNITY COLLEGE | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 5.093 | 0.036471 | 7.2942 | Fixture/1000 sf | 71.6658 | 225.1466 | 225.1466 | 0.023869 | 0.074988 | 0.074988 | 0 | 0 | 0 | 81.7349 | 256.7797 | 256.7797 | 0.030799 | 0.096758 | 0.096758 | -0.63078 | -1.9817 | -1.9817 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ECC | EDUCATION - COMMUNITY COLLEGE | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 5.093 | 0.036471 | 7.2942 | Fixture/1000 sf | 71.6683 | 225.1542 | 225.1542 | 0.023869 | 0.074988 | 0.074988 | 0 | 0 | 0 | 88.5461 | 278.178 | 278.178 | 0.030503 | 0.095827 | 0.095827 | -0.17798 | -0.55915 | -0.55915 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ECC | EDUCATION - COMMUNITY COLLEGE | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 5.093 | 0.036471 | 7.2942 | Fixture/1000 sf | 71.6674 | 225.1516 | 225.1516 | 0.023869 | 0.074987 | 0.074987 | 0 | 0 | 0 | 92.0998 | 289.3424 | 289.3424 | 0.034056 | 0.10699 | 0.10699 | -0.13356 | -0.41959 | -0.41959 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ESE | EDUCATION - SECONDARY SCHOOL | New | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 5.093 | 0.036471 | 7.2942 | Fixture/1000 sf | 67.5197 | 212.1211 | 212.1211 | 0.020997 | 0.065964 | 0.065964 | 0 | 0 | 0 | 76.1082 | 239.1029 | 239.1029 | 0.029584 | 0.092943 | 0.092943 | -0.45013 | -1.4141 | -1.4141 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ESE | EDUCATION - SECONDARY SCHOOL | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 5.093 | 0.036471 | 7.2942 | Fixture/1000 sf | 67.5214 | 212.1264 | 212.1264 | 0.020997 | 0.065964 | 0.065964 | 0 | 0 | 0 | 75.5159 | 237.2421 | 237.2421 | 0.026742 | 0.084012 | 0.084012 | -0.4294 | -1.349 | -1.349 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ESE | EDUCATION - SECONDARY SCHOOL | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 5.093 | 0.036471 | 7.2942 | Fixture/1000 sf | 67.518 | 212.1158 | 212.1158 | 0.020997 | 0.065965 | 0.065965 | 0 | 0 | 0 | 76.7005 | 240.9636 | 240.9636 | 0.02991 | 0.093966 | 0.093966 | -0.48863 | -1.5351 | -1.5351 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | HSP | HEALTH/MEDICAL - HOSPITAL | Existing | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 4.3484 | 0.024242 | 4.8484 | Fixture/1000 sf | 163.9824 | 451.4194 | 451.4194 | 0.025782 | 0.070974 | 0.070974 | 0 | 0 | 0 | 182.6928 | 502.9264 | 502.9264 | 0.032112 | 0.088398 | 0.088398 | -1.0257 | -2.8236 | -2.8236 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | HSP | HEALTH/MEDICAL - HOSPITAL | New | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 4.3484 | 0.024242 | 4.8484 | Fixture/1000 sf | 163.9797 | 451.412 | 451.412 | 0.025782 | 0.070974 | 0.070974 | 0 | 0 | 0 | 178.0164 | 490.0529 | 490.0529 | 0.031114 | 0.085652 | 0.085652 | -1.0413 | -2.8665 | -2.8665 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | HSP | HEALTH/MEDICAL - HOSPITAL | Existing | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 4.3484 | 0.024242 | 4.8484 | Fixture/1000 sf | 163.9821 | 451.4185 | 451.4185 | 0.025782 | 0.070974 | 0.070974 | 0 | 0 | 0 | 182.0693 | 501.2099 | 501.2099 | 0.032112 | 0.088398 | 0.088398 | -0.99764 | -2.7464 | -2.7464 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | OFL | OFFICE - LARGE | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 3.1486 | 0.018018 | 3.6035 | Fixture/1000 sf | 82.3058 | 226.5756 | 226.5756 | 0.022135 | 0.060935 | 0.060935 | 0 | 0 | 0 | 87.2935 | 240.3061 | 240.3061 | 0.028027 | 0.077155 | 0.077155 | -0.92282 | -2.5404 | -2.5404 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | OFL | OFFICE - LARGE | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 3.1486 | 0.018018 | 3.6035 | Fixture/1000 sf | 82.3078 | 226.5813 | 226.5813 | 0.022135 | 0.060934 | 0.060934 | 0 | 0 | 0 | 89.1641 | 245.4555 | 245.4555 | 0.027279 | 0.075096 | 0.075096 | -0.57053 | -1.5706 | -1.5706 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | OFL | OFFICE - LARGE | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 4.2972 | 0.025741 | 5.1481 | Fixture/1000 sf | 78.1821 | 245.618 | 245.618 | 0.021025 | 0.066054 | 0.066054 | 0 | 0 | 0 | 87.6577 | 275.387 | 275.387 | 0.02686 | 0.084384 | 0.084384 | -0.53898 | -1.6933 | -1.6933 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RSD | RESTAURANT - SIT-DOWN | Existing | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 3.5448 | 0.020224 | 4.0448 | Fixture/1000 sf | 150.5819 | 414.5298 | 414.5298 | 0.024941 | 0.068659 | 0.068659 | 0 | 0 | 0 | 137.799 | 379.3404 | 379.3404 | 0.028744 | 0.079129 | 0.079129 | -2.5752 | -7.089 | -7.089 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RSD | RESTAURANT - SIT-DOWN | Existing | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 3.5448 | 0.020224 | 4.0448 | Fixture/1000 sf | 150.5802 | 414.5251 | 414.5251 | 0.02494 | 0.068656 | 0.068656 | 0 | 0 | 0 | 152.7636 | 420.5357 | 420.5357 | 0.029274 | 0.080588 | 0.080588 | -1.459 | -4.0165 | -4.0165 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RSD | RESTAURANT - SIT-DOWN | New | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 3.5448 | 0.020224 | 4.0448 | Fixture/1000 sf | 150.5785 | 414.5205 | 414.5205 | 0.024941 | 0.068659 | 0.068659 | 0 | 0 | 0 | 151.8283 | 417.961 | 417.961 | 0.030802 | 0.084794 | 0.084794 | -1.6555 | -4.5572 | -4.5572 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | SCN | STORAGE - CONDITIONED | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 1.4764 | 0.0081354 | 1.6271 | Fixture/1000 sf | 101.277 | 318.1735 | 318.1735 | 0.02073 | 0.065125 | 0.065125 | 0 | 0 | 0 | 103.3532 | 324.6961 | 324.6961 | 0.02683 | 0.084291 | 0.084291 | -0.7907 | -2.4841 | -2.4841 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | SCN | STORAGE - CONDITIONED | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 1.4764 | 0.0081354 | 1.6271 | Fixture/1000 sf | 101.2798 | 318.1823 | 318.1823 | 0.02073 | 0.065125 | 0.065125 | 0 | 0 | 0 | 100.9841 | 317.2532 | 317.2532 | 0.025379 | 0.079732 | 0.079732 | -0.79662 | -2.5027 | -2.5027 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | SCN | STORAGE - CONDITIONED | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 1.4764 | 0.0081354 | 1.6271 | Fixture/1000 sf | 101.2822 | 318.1898 | 318.1898 | 0.020729 | 0.065123 | 0.065123 | 0 | 0 | 0 | 102.7609 | 322.8354 | 322.8354 | 0.026801 | 0.084198 | 0.084198 | -0.87065 | -2.7353 | -2.7353 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ASM | ASSEMBLY | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 4.099 | 0.025938 | 5.1876 | Fixture/1000 sf | 77.2953 | 242.8321 | 242.8321 | 0.015755 | 0.049496 | 0.049496 | 0 | 0 | 0 | 82.3272 | 258.6404 | 258.6404 | 0.018923 | 0.05945 | 0.05945 | -0.74331 | -2.3352 | -2.3352 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ASM | ASSEMBLY | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 4.099 | 0.025938 | 5.1876 | Fixture/1000 sf | 77.3039 | 242.8591 | 242.8591 | 0.015755 | 0.049495 | 0.049495 | 0 | 0 | 0 | 92.0998 | 289.3424 | 289.3424 | 0.018686 | 0.058706 | 0.058706 | -0.19812 | -0.62241 | -0.62241 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ASM | ASSEMBLY | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 4.099 | 0.025938 | 5.1876 | Fixture/1000 sf | 77.2895 | 242.8141 | 242.8141 | 0.015754 | 0.049494 | 0.049494 | 0 | 0 | 0 | 90.0268 | 282.8298 | 282.8298 | 0.019308 | 0.06066 | 0.06066 | -0.21411 | -0.67265 | -0.67265 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ASM | ASSEMBLY | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 4.099 | 0.025938 | 5.1876 | Fixture/1000 sf | 77.2923 | 242.8229 | 242.8229 | 0.015755 | 0.049495 | 0.049495 | 0 | 0 | 0 | 76.1082 | 239.1029 | 239.1029 | 0.018686 | 0.058706 | 0.058706 | -1.0898 | -3.4237 | -3.4237 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ASM | ASSEMBLY | Existing | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 3.5299 | 0.018679 | 3.7358 | Fixture/1000 sf | 75.5226 | 243.7623 | 243.7623 | 0.015393 | 0.049684 | 0.049684 | 0 | 0 | 0 | 83.3317 | 268.9673 | 268.9673 | 0.018952 | 0.061171 | 0.061171 | -0.39062 | -1.2608 | -1.2608 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | EPR | EDUCATION - PRIMARY SCHOOL | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 5.093 | 0.036471 | 7.2942 | Fixture/1000 sf | 63.3726 | 199.0926 | 199.0926 | 0.018242 | 0.057309 | 0.057309 | 0 | 0 | 0 | 66.9279 | 210.2617 | 210.2617 | 0.02378 | 0.074708 | 0.074708 | -0.5449 | -1.7119 | -1.7119 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | EPR | EDUCATION - PRIMARY SCHOOL | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 5.093 | 0.036471 | 7.2942 | Fixture/1000 sf | 63.3717 | 199.0897 | 199.0897 | 0.018242 | 0.057308 | 0.057308 | 0 | 0 | 0 | 69.297 | 217.7046 | 217.7046 | 0.023247 | 0.073033 | 0.073033 | -0.55971 | -1.7584 | -1.7584 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | EPR | EDUCATION - PRIMARY SCHOOL | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 5.093 | 0.036471 | 7.2942 | Fixture/1000 sf | 63.3755 | 199.1015 | 199.1015 | 0.018242 | 0.05731 | 0.05731 | 0 | 0 | 0 | 74.0352 | 232.5903 | 232.5903 | 0.023691 | 0.074429 | 0.074429 | -0.27245 | -0.85593 | -0.85593 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | EPR | EDUCATION - PRIMARY SCHOOL | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 5.093 | 0.036471 | 7.2942 | Fixture/1000 sf | 63.3731 | 199.0941 | 199.0941 | 0.018242 | 0.05731 | 0.05731 | 0 | 0 | 0 | 65.7433 | 206.5402 | 206.5402 | 0.017324 | 0.054426 | 0.054426 | -0.2991 | -0.93966 | -0.93966 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | EPR | EDUCATION - PRIMARY SCHOOL | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 5.093 | 0.036471 | 7.2942 | Fixture/1000 sf | 63.3726 | 199.0923 | 199.0923 | 0.018242 | 0.057308 | 0.057308 | 0 | 0 | 0 | 74.6275 | 234.4511 | 234.4511 | 0.024017 | 0.075452 | 0.075452 | -0.22359 | -0.70242 | -0.70242 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | EPR | EDUCATION - PRIMARY SCHOOL | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 5.093 | 0.036471 | 7.2942 | Fixture/1000 sf | 63.3724 | 199.0917 | 199.0917 | 0.018242 | 0.057311 | 0.057311 | 0 | 0 | 0 | 71.37 | 224.2171 | 224.2171 | 0.02535 | 0.079639 | 0.079639 | -0.30206 | -0.94897 | -0.94897 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | EPR | EDUCATION - PRIMARY SCHOOL | Existing | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 5.093 | 0.036471 | 7.2942 | Fixture/1000 sf | 63.373 | 199.0936 | 199.0936 | 0.018242 | 0.057308 | 0.057308 | 0 | 0 | 0 | 73.443 | 230.7296 | 230.7296 | 0.024017 | 0.075452 | 0.075452 | -0.28015 | -0.88012 | -0.88012 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | EPR | EDUCATION - PRIMARY SCHOOL | New | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 5.093 | 0.036471 | 7.2942 | Fixture/1000 sf | 63.3724 | 199.0917 | 199.0917 | 0.018242 | 0.057309 | 0.057309 | 0 | 0 | 0 | 71.37 | 224.2171 | 224.2171 | 0.026297 | 0.082616 | 0.082616 | -0.34648 | -1.0885 | -1.0885 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | EPR | EDUCATION - PRIMARY SCHOOL | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 5.093 | 0.036471 | 7.2942 | Fixture/1000 sf | 63.3724 | 199.0917 | 199.0917 | 0.018243 | 0.057312 | 0.057312 | 0 | 0 | 0 | 71.37 | 224.2171 | 224.2171 | 0.023484 | 0.073778 | 0.073778 | -0.30503 | -0.95827 | -0.95827 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | EPR | EDUCATION - PRIMARY SCHOOL | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 5.093 | 0.036471 | 7.2942 | Fixture/1000 sf | 63.3765 | 199.1046 | 199.1046 | 0.018242 | 0.05731 | 0.05731 | 0 | 0 | 0 | 71.6661 | 225.1474 | 225.1474 | 0.026712 | 0.083919 | 0.083919 | -0.37314 | -1.1723 | -1.1723 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | EPR | EDUCATION - PRIMARY SCHOOL | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 5.093 | 0.036471 | 7.2942 | Fixture/1000 sf | 63.3759 | 199.1029 | 199.1029 | 0.00059228 | 0.0018607 | 0.0018607 | 0 | 0 | 0 | 69.5931 | 218.6349 | 218.6349 | 0.00059228 | 0.0018607 | 0.0018607 | -0.51529 | -1.6188 | -1.6188 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | EPR | EDUCATION - PRIMARY SCHOOL | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 5.093 | 0.036471 | 7.2942 | Fixture/1000 sf | 63.377 | 199.1062 | 199.1062 | 0.00059228 | 0.0018607 | 0.0018607 | 0 | 0 | 0 | 70.4815 | 221.426 | 221.426 | 0.00059228 | 0.0018607 | 0.0018607 | -0.60709 | -1.9072 | -1.9072 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | EPR | EDUCATION - PRIMARY SCHOOL | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 5.093 | 0.036471 | 7.2942 | Fixture/1000 sf | 63.3717 | 199.0897 | 199.0897 | 0.018242 | 0.057311 | 0.057311 | 0 | 0 | 0 | 69.297 | 217.7046 | 217.7046 | 0.023573 | 0.074057 | 0.074057 | -0.50936 | -1.6002 | -1.6002 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | EPR | EDUCATION - PRIMARY SCHOOL | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 5.093 | 0.036471 | 7.2942 | Fixture/1000 sf | 63.377 | 199.1062 | 199.1062 | 0.018242 | 0.05731 | 0.05731 | 0 | 0 | 0 | 70.4815 | 221.426 | 221.426 | 0.026208 | 0.082337 | 0.082337 | -0.61005 | -1.9165 | -1.9165 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | EPR | EDUCATION - PRIMARY SCHOOL | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 5.093 | 0.036471 | 7.2942 | Fixture/1000 sf | 63.3731 | 199.0941 | 199.0941 | 0.018243 | 0.057312 | 0.057312 | 0 | 0 | 0 | 76.7005 | 240.9636 | 240.9636 | 0.023484 | 0.073778 | 0.073778 | -0.12497 | -0.39261 | -0.39261 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ESE | EDUCATION - SECONDARY SCHOOL | New | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 5.1904 | 0.026528 | 5.3056 | Fixture/1000 sf | 65.9712 | 212.9335 | 212.9335 | 0.020514 | 0.066213 | 0.066213 | 0 | 0 | 0 | 72.0472 | 232.5447 | 232.5447 | 0.026533 | 0.08564 | 0.08564 | -0.38483 | -1.2421 | -1.2421 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ESE | EDUCATION - SECONDARY SCHOOL | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 5.1904 | 0.026528 | 5.3056 | Fixture/1000 sf | 65.9689 | 212.9259 | 212.9259 | 0.020515 | 0.066214 | 0.066214 | 0 | 0 | 0 | 74.9407 | 241.8838 | 241.8838 | 0.026041 | 0.084052 | 0.084052 | -0.31828 | -1.0273 | -1.0273 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ASM | ASSEMBLY | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 3.5299 | 0.018679 | 3.7358 | Fixture/1000 sf | 75.5205 | 243.7554 | 243.7554 | 0.015394 | 0.049686 | 0.049686 | 0 | 0 | 0 | 83.0423 | 268.0334 | 268.0334 | 0.018605 | 0.060051 | 0.060051 | -0.42245 | -1.3635 | -1.3635 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ASM | ASSEMBLY | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 3.5299 | 0.018679 | 3.7358 | Fixture/1000 sf | 75.5205 | 243.7554 | 243.7554 | 0.015394 | 0.049685 | 0.049685 | 0 | 0 | 0 | 83.0423 | 268.0334 | 268.0334 | 0.018634 | 0.060144 | 0.060144 | -0.45427 | -1.4662 | -1.4662 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ASM | ASSEMBLY | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 3.5299 | 0.018679 | 3.7358 | Fixture/1000 sf | 75.5162 | 243.7414 | 243.7414 | 0.015393 | 0.049685 | 0.049685 | 0 | 0 | 0 | 82.4637 | 266.1656 | 266.1656 | 0.019068 | 0.061545 | 0.061545 | -0.48899 | -1.5783 | -1.5783 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ASM | ASSEMBLY | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 3.5299 | 0.018679 | 3.7358 | Fixture/1000 sf | 75.5169 | 243.7438 | 243.7438 | 0.015393 | 0.049682 | 0.049682 | 0 | 0 | 0 | 80.7276 | 260.5621 | 260.5621 | 0.017448 | 0.056315 | 0.056315 | -0.72915 | -2.3535 | -2.3535 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ASM | ASSEMBLY | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 3.5299 | 0.018679 | 3.7358 | Fixture/1000 sf | 75.5218 | 243.7594 | 243.7594 | 0.015394 | 0.049686 | 0.049686 | 0 | 0 | 0 | 80.4382 | 259.6282 | 259.6282 | 0.018605 | 0.060051 | 0.060051 | -0.77834 | -2.5122 | -2.5122 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ASM | ASSEMBLY | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 3.5299 | 0.018679 | 3.7358 | Fixture/1000 sf | 75.5211 | 243.7573 | 243.7573 | 0.015393 | 0.049683 | 0.049683 | 0 | 0 | 0 | 91.4334 | 295.1169 | 295.1169 | 0.018431 | 0.05949 | 0.05949 | -0.20167 | -0.65094 | -0.65094 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ASM | ASSEMBLY | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 3.5299 | 0.018679 | 3.7358 | Fixture/1000 sf | 75.5182 | 243.748 | 243.748 | 0.015393 | 0.049684 | 0.049684 | 0 | 0 | 0 | 88.2506 | 284.8439 | 284.8439 | 0.018981 | 0.061265 | 0.061265 | -0.22569 | -0.72845 | -0.72845 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ECC | EDUCATION - COMMUNITY COLLEGE | Existing | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 4.6186 | 0.028286 | 5.6572 | Fixture/1000 sf | 75.4484 | 207.6983 | 207.6983 | 0.025127 | 0.069171 | 0.069171 | 0 | 0 | 0 | 77.6289 | 213.7008 | 213.7008 | 0.030303 | 0.083421 | 0.083421 | -1.5183 | -4.1796 | -4.1796 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ECC | EDUCATION - COMMUNITY COLLEGE | New | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 4.6186 | 0.028286 | 5.6572 | Fixture/1000 sf | 75.4434 | 207.6847 | 207.6847 | 0.025127 | 0.069171 | 0.069171 | 0 | 0 | 0 | 77.9406 | 214.559 | 214.559 | 0.029462 | 0.081103 | 0.081103 | -1.459 | -4.0165 | -4.0165 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ECC | EDUCATION - COMMUNITY COLLEGE | Existing | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 4.6186 | 0.028286 | 5.6572 | Fixture/1000 sf | 75.4494 | 207.701 | 207.701 | 0.015183 | 0.041796 | 0.041796 | 0 | 0 | 0 | 82.6171 | 227.4326 | 227.4326 | 0.019797 | 0.054498 | 0.054498 | -0.91346 | -2.5146 | -2.5146 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ECC | EDUCATION - COMMUNITY COLLEGE | New | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 4.6186 | 0.028286 | 5.6572 | Fixture/1000 sf | 75.4494 | 207.701 | 207.701 | 0.015183 | 0.041796 | 0.041796 | 0 | 0 | 0 | 82.6171 | 227.4326 | 227.4326 | 0.020327 | 0.055957 | 0.055957 | -0.84488 | -2.3258 | -2.3258 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ECC | EDUCATION - COMMUNITY COLLEGE | Existing | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 4.6186 | 0.028286 | 5.6572 | Fixture/1000 sf | 75.4496 | 207.7017 | 207.7017 | 0.015183 | 0.041798 | 0.041798 | 0 | 0 | 0 | 81.6818 | 224.8579 | 224.8579 | 0.01883 | 0.051837 | 0.051837 | -0.95088 | -2.6176 | -2.6176 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ECC | EDUCATION - COMMUNITY COLLEGE | New | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 4.6186 | 0.028286 | 5.6572 | Fixture/1000 sf | 75.4451 | 207.6893 | 207.6893 | 0.015183 | 0.041796 | 0.041796 | 0 | 0 | 0 | 81.0582 | 223.1414 | 223.1414 | 0.019672 | 0.054155 | 0.054155 | -0.89164 | -2.4546 | -2.4546 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ECC | EDUCATION - COMMUNITY COLLEGE | Existing | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 4.6186 | 0.028286 | 5.6572 | Fixture/1000 sf | 75.4445 | 207.6876 | 207.6876 | 0.025128 | 0.069175 | 0.069175 | 0 | 0 | 0 | 83.8641 | 230.8655 | 230.8655 | 0.032423 | 0.089257 | 0.089257 | -0.72017 | -1.9825 | -1.9825 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ECC | EDUCATION - COMMUNITY COLLEGE | New | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 4.6186 | 0.028286 | 5.6572 | Fixture/1000 sf | 75.4445 | 207.6876 | 207.6876 | 0.025128 | 0.069174 | 0.069174 | 0 | 0 | 0 | 83.8641 | 230.8655 | 230.8655 | 0.031488 | 0.086682 | 0.086682 | -0.66094 | -1.8195 | -1.8195 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ECC | EDUCATION - COMMUNITY COLLEGE | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 4.6186 | 0.028286 | 5.6572 | Fixture/1000 sf | 75.4496 | 207.7017 | 207.7017 | 0.025128 | 0.069174 | 0.069174 | 0 | 0 | 0 | 81.6818 | 224.8579 | 224.8579 | 0.030646 | 0.084365 | 0.084365 | -0.91346 | -2.5146 | -2.5146 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ECC | EDUCATION - COMMUNITY COLLEGE | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 4.6186 | 0.028286 | 5.6572 | Fixture/1000 sf | 75.4496 | 207.7017 | 207.7017 | 0.025128 | 0.069173 | 0.069173 | 0 | 0 | 0 | 81.6818 | 224.8579 | 224.8579 | 0.030553 | 0.084107 | 0.084107 | -0.86982 | -2.3945 | -2.3945 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ECC | EDUCATION - COMMUNITY COLLEGE | Existing | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 4.6186 | 0.028286 | 5.6572 | Fixture/1000 sf | 75.4443 | 207.687 | 207.687 | 0.015182 | 0.041795 | 0.041795 | 0 | 0 | 0 | 84.7994 | 233.4402 | 233.4402 | 0.018893 | 0.052009 | 0.052009 | -0.82305 | -2.2657 | -2.2657 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ECC | EDUCATION - COMMUNITY COLLEGE | New | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 4.6186 | 0.028286 | 5.6572 | Fixture/1000 sf | 75.4465 | 207.693 | 207.693 | 0.015182 | 0.041795 | 0.041795 | 0 | 0 | 0 | 85.1112 | 234.2985 | 234.2985 | 0.019953 | 0.054927 | 0.054927 | -0.71394 | -1.9654 | -1.9654 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ECC | EDUCATION - COMMUNITY COLLEGE | Existing | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 4.6186 | 0.028286 | 5.6572 | Fixture/1000 sf | 75.4445 | 207.6876 | 207.6876 | 0.015183 | 0.041795 | 0.041795 | 0 | 0 | 0 | 83.8641 | 230.8655 | 230.8655 | 0.019548 | 0.053811 | 0.053811 | -0.81682 | -2.2486 | -2.2486 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ECC | EDUCATION - COMMUNITY COLLEGE | New | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 4.6186 | 0.028286 | 5.6572 | Fixture/1000 sf | 75.4489 | 207.6996 | 207.6996 | 0.015182 | 0.041795 | 0.041795 | 0 | 0 | 0 | 84.4876 | 232.582 | 232.582 | 0.020358 | 0.056043 | 0.056043 | -0.72329 | -1.9911 | -1.9911 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ECC | EDUCATION - COMMUNITY COLLEGE | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 4.6186 | 0.028286 | 5.6572 | Fixture/1000 sf | 75.4486 | 207.6989 | 207.6989 | 0.015183 | 0.041796 | 0.041796 | 0 | 0 | 0 | 85.4229 | 235.1567 | 235.1567 | 0.019735 | 0.054326 | 0.054326 | -0.72329 | -1.9911 | -1.9911 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ECC | EDUCATION - COMMUNITY COLLEGE | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 4.6186 | 0.028286 | 5.6572 | Fixture/1000 sf | 75.4441 | 207.6865 | 207.6865 | 0.015183 | 0.041796 | 0.041796 | 0 | 0 | 0 | 85.7347 | 236.0149 | 236.0149 | 0.02014 | 0.055442 | 0.055442 | -0.62976 | -1.7336 | -1.7336 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ECC | EDUCATION - COMMUNITY COLLEGE | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 4.6186 | 0.028286 | 5.6572 | Fixture/1000 sf | 75.4453 | 207.6899 | 207.6899 | 0.015183 | 0.041798 | 0.041798 | 0 | 0 | 0 | 80.123 | 220.5667 | 220.5667 | 0.019298 | 0.053125 | 0.053125 | -1.2315 | -3.39 | -3.39 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ECC | EDUCATION - COMMUNITY COLLEGE | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 4.6186 | 0.028286 | 5.6572 | Fixture/1000 sf | 75.443 | 207.6836 | 207.6836 | 0.015183 | 0.041797 | 0.041797 | 0 | 0 | 0 | 79.8112 | 219.7085 | 219.7085 | 0.018581 | 0.051151 | 0.051151 | -1.3281 | -3.6561 | -3.6561 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ECC | EDUCATION - COMMUNITY COLLEGE | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 5.093 | 0.036471 | 7.2942 | Fixture/1000 sf | 71.6691 | 225.1567 | 225.1567 | 0.023869 | 0.074987 | 0.074987 | 0 | 0 | 0 | 77.5889 | 243.7547 | 243.7547 | 0.02991 | 0.093966 | 0.093966 | -0.84696 | -2.6608 | -2.6608 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ECC | EDUCATION - COMMUNITY COLLEGE | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 5.093 | 0.036471 | 7.2942 | Fixture/1000 sf | 71.6667 | 225.1493 | 225.1493 | 0.023868 | 0.074984 | 0.074984 | 0 | 0 | 0 | 78.1812 | 245.6154 | 245.6154 | 0.029436 | 0.092478 | 0.092478 | -0.83216 | -2.6143 | -2.6143 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ECC | EDUCATION - COMMUNITY COLLEGE | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 5.093 | 0.036471 | 7.2942 | Fixture/1000 sf | 71.6676 | 225.1523 | 225.1523 | 0.023869 | 0.074988 | 0.074988 | 0 | 0 | 0 | 82.9195 | 260.5012 | 260.5012 | 0.030503 | 0.095827 | 0.095827 | -0.40275 | -1.2653 | -1.2653 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ECC | EDUCATION - COMMUNITY COLLEGE | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 5.093 | 0.036471 | 7.2942 | Fixture/1000 sf | 71.6638 | 225.1402 | 225.1402 | 0.023869 | 0.074988 | 0.074988 | 0 | 0 | 0 | 81.4388 | 255.8494 | 255.8494 | 0.030503 | 0.095827 | 0.095827 | -0.38202 | -1.2002 | -1.2002 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ECC | EDUCATION - COMMUNITY COLLEGE | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 5.093 | 0.036471 | 7.2942 | Fixture/1000 sf | 71.6674 | 225.1516 | 225.1516 | 0.023869 | 0.074988 | 0.074988 | 0 | 0 | 0 | 83.8079 | 263.2923 | 263.2923 | 0.030503 | 0.095827 | 0.095827 | -0.36425 | -1.1443 | -1.1443 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ECC | EDUCATION - COMMUNITY COLLEGE | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 5.093 | 0.036471 | 7.2942 | Fixture/1000 sf | 71.6636 | 225.1397 | 225.1397 | 0.023869 | 0.074988 | 0.074988 | 0 | 0 | 0 | 82.3272 | 258.6404 | 258.6404 | 0.030503 | 0.095827 | 0.095827 | -0.30799 | -0.96758 | -0.96758 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ECC | EDUCATION - COMMUNITY COLLEGE | Existing | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 5.093 | 0.036471 | 7.2942 | Fixture/1000 sf | 71.6635 | 225.1391 | 225.1391 | 0.02387 | 0.074989 | 0.074989 | 0 | 0 | 0 | 83.2156 | 261.4315 | 261.4315 | 0.031095 | 0.097688 | 0.097688 | -0.41756 | -1.3118 | -1.3118 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ECC | EDUCATION - COMMUNITY COLLEGE | New | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 5.093 | 0.036471 | 7.2942 | Fixture/1000 sf | 71.6636 | 225.1397 | 225.1397 | 0.02387 | 0.074989 | 0.074989 | 0 | 0 | 0 | 82.3272 | 258.6404 | 258.6404 | 0.031391 | 0.098618 | 0.098618 | -0.36425 | -1.1443 | -1.1443 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ECC | EDUCATION - COMMUNITY COLLEGE | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 5.093 | 0.036471 | 7.2942 | Fixture/1000 sf | 71.6636 | 225.1397 | 225.1397 | 0.023869 | 0.074988 | 0.074988 | 0 | 0 | 0 | 82.3272 | 258.6404 | 258.6404 | 0.030799 | 0.096758 | 0.096758 | -0.39979 | -1.256 | -1.256 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ECC | EDUCATION - COMMUNITY COLLEGE | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 5.093 | 0.036471 | 7.2942 | Fixture/1000 sf | 71.6676 | 225.1523 | 225.1523 | 0.02387 | 0.07499 | 0.07499 | 0 | 0 | 0 | 82.9195 | 260.5012 | 260.5012 | 0.031687 | 0.099549 | 0.099549 | -0.36721 | -1.1536 | -1.1536 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ECC | EDUCATION - COMMUNITY COLLEGE | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 5.093 | 0.036471 | 7.2942 | Fixture/1000 sf | 71.663 | 225.1377 | 225.1377 | 0.014422 | 0.045307 | 0.045307 | 0 | 0 | 0 | 74.9237 | 235.3814 | 235.3814 | 0.017946 | 0.05638 | 0.05638 | -1.2053 | -3.7866 | -3.7866 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ECC | EDUCATION - COMMUNITY COLLEGE | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 5.093 | 0.036471 | 7.2942 | Fixture/1000 sf | 71.6628 | 225.1371 | 225.1371 | 0.014422 | 0.045308 | 0.045308 | 0 | 0 | 0 | 75.8121 | 238.1725 | 238.1725 | 0.018953 | 0.059543 | 0.059543 | -1.1905 | -3.7401 | -3.7401 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ECC | EDUCATION - COMMUNITY COLLEGE | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 5.1904 | 0.026528 | 5.3056 | Fixture/1000 sf | 70.0237 | 226.0135 | 226.0135 | 0.023321 | 0.075274 | 0.075274 | 0 | 0 | 0 | 79.2808 | 255.8925 | 255.8925 | 0.029513 | 0.095259 | 0.095259 | -0.40508 | -1.3075 | -1.3075 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ECC | EDUCATION - COMMUNITY COLLEGE | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 5.1904 | 0.026528 | 5.3056 | Fixture/1000 sf | 70.0195 | 226 | 226 | 0.023321 | 0.075274 | 0.075274 | 0 | 0 | 0 | 79.5702 | 256.8264 | 256.8264 | 0.029513 | 0.095259 | 0.095259 | -0.38194 | -1.2328 | -1.2328 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ECC | EDUCATION - COMMUNITY COLLEGE | Existing | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 5.1904 | 0.026528 | 5.3056 | Fixture/1000 sf | 70.0215 | 226.0064 | 226.0064 | 0.023321 | 0.075274 | 0.075274 | 0 | 0 | 0 | 79.8595 | 257.7604 | 257.7604 | 0.029513 | 0.095259 | 0.095259 | -0.33853 | -1.0927 | -1.0927 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ECC | EDUCATION - COMMUNITY COLLEGE | New | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 5.1904 | 0.026528 | 5.3056 | Fixture/1000 sf | 70.0237 | 226.0135 | 226.0135 | 0.023321 | 0.075274 | 0.075274 | 0 | 0 | 0 | 79.2808 | 255.8925 | 255.8925 | 0.029513 | 0.095259 | 0.095259 | -0.3096 | -0.99929 | -0.99929 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ECC | EDUCATION - COMMUNITY COLLEGE | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 5.1904 | 0.026528 | 5.3056 | Fixture/1000 sf | 70.0235 | 226.0128 | 226.0128 | 0.023321 | 0.075274 | 0.075274 | 0 | 0 | 0 | 80.1489 | 258.6943 | 258.6943 | 0.029513 | 0.095259 | 0.095259 | -0.36747 | -1.1861 | -1.1861 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ECC | EDUCATION - COMMUNITY COLLEGE | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 5.1904 | 0.026528 | 5.3056 | Fixture/1000 sf | 70.0193 | 225.9995 | 225.9995 | 0.023321 | 0.075274 | 0.075274 | 0 | 0 | 0 | 80.4382 | 259.6282 | 259.6282 | 0.029513 | 0.095259 | 0.095259 | -0.31539 | -1.018 | -1.018 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ECC | EDUCATION - COMMUNITY COLLEGE | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 5.1904 | 0.026528 | 5.3056 | Fixture/1000 sf | 70.0215 | 226.0064 | 226.0064 | 0.023322 | 0.075275 | 0.075275 | 0 | 0 | 0 | 79.8595 | 257.7604 | 257.7604 | 0.030092 | 0.097127 | 0.097127 | -0.43691 | -1.4102 | -1.4102 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ECC | EDUCATION - COMMUNITY COLLEGE | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 5.1904 | 0.026528 | 5.3056 | Fixture/1000 sf | 70.0192 | 225.9989 | 225.9989 | 0.023322 | 0.075276 | 0.075276 | 0 | 0 | 0 | 81.3063 | 262.4299 | 262.4299 | 0.030671 | 0.098995 | 0.098995 | -0.36747 | -1.1861 | -1.1861 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ECC | EDUCATION - COMMUNITY COLLEGE | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 5.1904 | 0.026528 | 5.3056 | Fixture/1000 sf | 70.0219 | 226.0078 | 226.0078 | 0.023322 | 0.075274 | 0.075274 | 0 | 0 | 0 | 78.1235 | 252.1569 | 252.1569 | 0.029803 | 0.096193 | 0.096193 | -0.65682 | -2.12 | -2.12 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ECC | EDUCATION - COMMUNITY COLLEGE | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 5.1904 | 0.026528 | 5.3056 | Fixture/1000 sf | 70.0235 | 226.0128 | 226.0128 | 0.023321 | 0.075274 | 0.075274 | 0 | 0 | 0 | 80.1489 | 258.6943 | 258.6943 | 0.029513 | 0.095259 | 0.095259 | -0.60763 | -1.9612 | -1.9612 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ECC | EDUCATION - COMMUNITY COLLEGE | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 5.1904 | 0.026528 | 5.3056 | Fixture/1000 sf | 70.0277 | 226.0263 | 226.0263 | 0.023213 | 0.074925 | 0.074925 | 0 | 0 | 0 | 79.8595 | 257.7604 | 257.7604 | 0.029513 | 0.095259 | 0.095259 | -0.36458 | -1.1767 | -1.1767 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ECC | EDUCATION - COMMUNITY COLLEGE | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 5.1904 | 0.026528 | 5.3056 | Fixture/1000 sf | 70.0215 | 226.0064 | 226.0064 | 0.023321 | 0.075272 | 0.075272 | 0 | 0 | 0 | 88.8293 | 286.7117 | 286.7117 | 0.032117 | 0.10366 | 0.10366 | -0.13455 | -0.43427 | -0.43427 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | EPR | EDUCATION - PRIMARY SCHOOL | Existing | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 4.6186 | 0.028286 | 5.6572 | Fixture/1000 sf | 66.7174 | 183.6633 | 183.6633 | 0.019205 | 0.052868 | 0.052868 | 0 | 0 | 0 | 66.0936 | 181.9461 | 181.9461 | 0.022946 | 0.063166 | 0.063166 | -1.2065 | -3.3214 | -3.3214 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | EPR | EDUCATION - PRIMARY SCHOOL | New | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 4.6186 | 0.028286 | 5.6572 | Fixture/1000 sf | 66.7174 | 183.6633 | 183.6633 | 0.019204 | 0.052866 | 0.052866 | 0 | 0 | 0 | 66.0936 | 181.9461 | 181.9461 | 0.022353 | 0.061536 | 0.061536 | -1.3156 | -3.6218 | -3.6218 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | EPR | EDUCATION - PRIMARY SCHOOL | New | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 4.6186 | 0.028286 | 5.6572 | Fixture/1000 sf | 66.7162 | 183.66 | 183.66 | 0.00062352 | 0.0017165 | 0.0017165 | 0 | 0 | 0 | 72.6407 | 199.969 | 199.969 | 0.00062352 | 0.0017165 | 0.0017165 | -0.7607 | -2.0941 | -2.0941 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | EPR | EDUCATION - PRIMARY SCHOOL | Existing | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 4.6186 | 0.028286 | 5.6572 | Fixture/1000 sf | 66.7185 | 183.6661 | 183.6661 | 0.00062352 | 0.0017165 | 0.0017165 | 0 | 0 | 0 | 71.0818 | 195.6778 | 195.6778 | 0.00062352 | 0.0017165 | 0.0017165 | -0.67341 | -1.8538 | -1.8538 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | EPR | EDUCATION - PRIMARY SCHOOL | New | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 4.6186 | 0.028286 | 5.6572 | Fixture/1000 sf | 66.7151 | 183.6568 | 183.6568 | 0.00062352 | 0.0017165 | 0.0017165 | 0 | 0 | 0 | 71.7054 | 197.3943 | 197.3943 | 0.00062352 | 0.0017165 | 0.0017165 | -0.77317 | -2.1284 | -2.1284 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | EPR | EDUCATION - PRIMARY SCHOOL | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 4.6186 | 0.028286 | 5.6572 | Fixture/1000 sf | 66.7151 | 183.6568 | 183.6568 | 0.00062352 | 0.0017165 | 0.0017165 | 0 | 0 | 0 | 71.7054 | 197.3943 | 197.3943 | 0.00062352 | 0.0017165 | 0.0017165 | -0.583 | -1.6049 | -1.6049 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | EPR | EDUCATION - PRIMARY SCHOOL | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 4.6186 | 0.028286 | 5.6572 | Fixture/1000 sf | 66.7146 | 183.6555 | 183.6555 | 0.00062352 | 0.0017165 | 0.0017165 | 0 | 0 | 0 | 72.9524 | 200.8273 | 200.8273 | 0.00062352 | 0.0017165 | 0.0017165 | -0.69523 | -1.9139 | -1.9139 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | EPR | EDUCATION - PRIMARY SCHOOL | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 4.6186 | 0.028286 | 5.6572 | Fixture/1000 sf | 66.717 | 183.662 | 183.662 | 0.00062352 | 0.0017165 | 0.0017165 | 0 | 0 | 0 | 66.4054 | 182.8043 | 182.8043 | 0.00062352 | 0.0017165 | 0.0017165 | -1.113 | -3.0639 | -3.0639 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | EPR | EDUCATION - PRIMARY SCHOOL | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 4.6186 | 0.028286 | 5.6572 | Fixture/1000 sf | 66.7173 | 183.663 | 183.663 | 0.00062352 | 0.0017165 | 0.0017165 | 0 | 0 | 0 | 64.8466 | 178.5131 | 178.5131 | 0.00062352 | 0.0017165 | 0.0017165 | -1.1941 | -3.287 | -3.287 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | EPR | EDUCATION - PRIMARY SCHOOL | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 5.093 | 0.036471 | 7.2942 | Fixture/1000 sf | 63.3765 | 199.1046 | 199.1046 | 0.018242 | 0.057311 | 0.057311 | 0 | 0 | 0 | 78.1812 | 245.6154 | 245.6154 | 0.026742 | 0.084012 | 0.084012 | -0.1611 | -0.50612 | -0.50612 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | EPR | EDUCATION - PRIMARY SCHOOL | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 5.093 | 0.036471 | 7.2942 | Fixture/1000 sf | 63.3743 | 199.0979 | 199.0979 | 0.00059228 | 0.0018607 | 0.0018607 | 0 | 0 | 0 | 61.5973 | 193.5152 | 193.5152 | 0.00059228 | 0.0018607 | 0.0018607 | -1.0513 | -3.3028 | -3.3028 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | EPR | EDUCATION - PRIMARY SCHOOL | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 5.093 | 0.036471 | 7.2942 | Fixture/1000 sf | 63.3742 | 199.0976 | 199.0976 | 0.00059228 | 0.0018607 | 0.0018607 | 0 | 0 | 0 | 62.4857 | 196.3062 | 196.3062 | 0.00059228 | 0.0018607 | 0.0018607 | -0.98319 | -3.0888 | -3.0888 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | EPR | EDUCATION - PRIMARY SCHOOL | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 5.1904 | 0.026528 | 5.3056 | Fixture/1000 sf | 61.9194 | 199.8554 | 199.8554 | 0.017823 | 0.057528 | 0.057528 | 0 | 0 | 0 | 70.6005 | 227.8751 | 227.8751 | 0.022858 | 0.073779 | 0.073779 | -0.27488 | -0.88722 | -0.88722 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | EPR | EDUCATION - PRIMARY SCHOOL | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 5.1904 | 0.026528 | 5.3056 | Fixture/1000 sf | 61.9207 | 199.8597 | 199.8597 | 0.017824 | 0.057529 | 0.057529 | 0 | 0 | 0 | 63.9455 | 206.3951 | 206.3951 | 0.016927 | 0.054634 | 0.054634 | -0.29803 | -0.96193 | -0.96193 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | EPR | EDUCATION - PRIMARY SCHOOL | Existing | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 5.1904 | 0.026528 | 5.3056 | Fixture/1000 sf | 61.9208 | 199.8601 | 199.8601 | 0.017823 | 0.057527 | 0.057527 | 0 | 0 | 0 | 70.3111 | 226.9412 | 226.9412 | 0.02309 | 0.074526 | 0.074526 | -0.24594 | -0.79383 | -0.79383 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | EPR | EDUCATION - PRIMARY SCHOOL | New | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 5.1904 | 0.026528 | 5.3056 | Fixture/1000 sf | 61.9177 | 199.85 | 199.85 | 0.017823 | 0.057528 | 0.057528 | 0 | 0 | 0 | 67.707 | 218.536 | 218.536 | 0.023842 | 0.076955 | 0.076955 | -0.31828 | -1.0273 | -1.0273 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | EPR | EDUCATION - PRIMARY SCHOOL | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 5.1904 | 0.026528 | 5.3056 | Fixture/1000 sf | 61.9218 | 199.8634 | 199.8634 | 0.017823 | 0.057527 | 0.057527 | 0 | 0 | 0 | 71.1792 | 229.7429 | 229.7429 | 0.02309 | 0.074526 | 0.074526 | -0.228 | -0.73592 | -0.73592 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | EPR | EDUCATION - PRIMARY SCHOOL | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 5.1904 | 0.026528 | 5.3056 | Fixture/1000 sf | 61.9183 | 199.852 | 199.852 | 0.017824 | 0.057531 | 0.057531 | 0 | 0 | 0 | 69.7324 | 225.0734 | 225.0734 | 0.024565 | 0.079289 | 0.079289 | -0.29803 | -0.96193 | -0.96193 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | EPR | EDUCATION - PRIMARY SCHOOL | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 5.1904 | 0.026528 | 5.3056 | Fixture/1000 sf | 61.9194 | 199.8554 | 199.8554 | 0.017823 | 0.057527 | 0.057527 | 0 | 0 | 0 | 70.6005 | 227.8751 | 227.8751 | 0.022974 | 0.074153 | 0.074153 | -0.29224 | -0.94325 | -0.94325 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | EPR | EDUCATION - PRIMARY SCHOOL | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 5.1904 | 0.026528 | 5.3056 | Fixture/1000 sf | 61.9223 | 199.8649 | 199.8649 | 0.017824 | 0.05753 | 0.05753 | 0 | 0 | 0 | 70.0218 | 226.0073 | 226.0073 | 0.025896 | 0.083585 | 0.083585 | -0.36747 | -1.1861 | -1.1861 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | EPR | EDUCATION - PRIMARY SCHOOL | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 5.1904 | 0.026528 | 5.3056 | Fixture/1000 sf | 61.9177 | 199.85 | 199.85 | 0.017824 | 0.057528 | 0.057528 | 0 | 0 | 0 | 67.707 | 218.536 | 218.536 | 0.023003 | 0.074246 | 0.074246 | -0.49768 | -1.6063 | -1.6063 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | EPR | EDUCATION - PRIMARY SCHOOL | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 5.1904 | 0.026528 | 5.3056 | Fixture/1000 sf | 61.9188 | 199.8534 | 199.8534 | 0.017824 | 0.05753 | 0.05753 | 0 | 0 | 0 | 68.575 | 221.3377 | 221.3377 | 0.025405 | 0.081998 | 0.081998 | -0.60184 | -1.9425 | -1.9425 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | EPR | EDUCATION - PRIMARY SCHOOL | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 5.1904 | 0.026528 | 5.3056 | Fixture/1000 sf | 61.92 | 199.8575 | 199.8575 | 0.017824 | 0.057528 | 0.057528 | 0 | 0 | 0 | 75.8087 | 244.6856 | 244.6856 | 0.023003 | 0.074246 | 0.074246 | -0.1195 | -0.38571 | -0.38571 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | EPR | EDUCATION - PRIMARY SCHOOL | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 5.1904 | 0.026528 | 5.3056 | Fixture/1000 sf | 61.9187 | 199.8531 | 199.8531 | 0.017824 | 0.05753 | 0.05753 | 0 | 0 | 0 | 76.098 | 245.6195 | 245.6195 | 0.025896 | 0.083585 | 0.083585 | -0.15856 | -0.51179 | -0.51179 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ERC | EDUCATION - RELOCATABLE CLASSROOM | Existing | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 4.6186 | 0.028286 | 5.6572 | Fixture/1000 sf | 77.3172 | 212.843 | 212.843 | 0.021886 | 0.060249 | 0.060249 | 0 | 0 | 0 | 74.823 | 205.9767 | 205.9767 | 0.02597 | 0.071491 | 0.071491 | -1.3375 | -3.6818 | -3.6818 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ERC | EDUCATION - RELOCATABLE CLASSROOM | New | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 4.6186 | 0.028286 | 5.6572 | Fixture/1000 sf | 77.3188 | 212.8472 | 212.8472 | 0.021885 | 0.060246 | 0.060246 | 0 | 0 | 0 | 80.4347 | 221.4249 | 221.4249 | 0.026157 | 0.072006 | 0.072006 | -1.4933 | -4.111 | -4.111 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ERC | EDUCATION - RELOCATABLE CLASSROOM | Existing | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 4.6186 | 0.028286 | 5.6572 | Fixture/1000 sf | 77.3142 | 212.8345 | 212.8345 | 0.00062352 | 0.0017165 | 0.0017165 | 0 | 0 | 0 | 78.8759 | 217.1338 | 217.1338 | 0.00062352 | 0.0017165 | 0.0017165 | -0.94464 | -2.6005 | -2.6005 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ERC | EDUCATION - RELOCATABLE CLASSROOM | New | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 4.6186 | 0.028286 | 5.6572 | Fixture/1000 sf | 77.3201 | 212.8507 | 212.8507 | 0.00062352 | 0.0017165 | 0.0017165 | 0 | 0 | 0 | 84.4876 | 232.582 | 232.582 | 0.00062352 | 0.0017165 | 0.0017165 | -0.9727 | -2.6777 | -2.6777 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ERC | EDUCATION - RELOCATABLE CLASSROOM | Existing | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 4.6186 | 0.028286 | 5.6572 | Fixture/1000 sf | 77.3196 | 212.8494 | 212.8494 | 0.00062352 | 0.0017165 | 0.0017165 | 0 | 0 | 0 | 77.6289 | 213.7008 | 213.7008 | 0.00062352 | 0.0017165 | 0.0017165 | -0.87293 | -2.4031 | -2.4031 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ERC | EDUCATION - RELOCATABLE CLASSROOM | New | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 4.6186 | 0.028286 | 5.6572 | Fixture/1000 sf | 77.3201 | 212.8507 | 212.8507 | 0.00062352 | 0.0017165 | 0.0017165 | 0 | 0 | 0 | 84.4876 | 232.582 | 232.582 | 0.00062352 | 0.0017165 | 0.0017165 | -0.87293 | -2.4031 | -2.4031 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ERC | EDUCATION - RELOCATABLE CLASSROOM | Existing | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 4.6186 | 0.028286 | 5.6572 | Fixture/1000 sf | 77.3137 | 212.8334 | 212.8334 | 0.021885 | 0.060246 | 0.060246 | 0 | 0 | 0 | 80.7465 | 222.2832 | 222.2832 | 0.026531 | 0.073036 | 0.073036 | -0.73576 | -2.0254 | -2.0254 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ERC | EDUCATION - RELOCATABLE CLASSROOM | New | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 4.6186 | 0.028286 | 5.6572 | Fixture/1000 sf | 77.3195 | 212.8493 | 212.8493 | 0.021885 | 0.060246 | 0.060246 | 0 | 0 | 0 | 86.3582 | 237.7314 | 237.7314 | 0.027934 | 0.076898 | 0.076898 | -0.75135 | -2.0683 | -2.0683 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ERC | EDUCATION - RELOCATABLE CLASSROOM | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 4.6186 | 0.028286 | 5.6572 | Fixture/1000 sf | 77.3142 | 212.8345 | 212.8345 | 0.021886 | 0.060249 | 0.060249 | 0 | 0 | 0 | 78.8759 | 217.1338 | 217.1338 | 0.026749 | 0.073637 | 0.073637 | -0.85735 | -2.3601 | -2.3601 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ERC | EDUCATION - RELOCATABLE CLASSROOM | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 4.6186 | 0.028286 | 5.6572 | Fixture/1000 sf | 77.3155 | 212.8381 | 212.8381 | 0.021886 | 0.060248 | 0.060248 | 0 | 0 | 0 | 83.8641 | 230.8655 | 230.8655 | 0.027092 | 0.074581 | 0.074581 | -0.82617 | -2.2743 | -2.2743 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ERC | EDUCATION - RELOCATABLE CLASSROOM | Existing | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 4.6186 | 0.028286 | 5.6572 | Fixture/1000 sf | 77.3188 | 212.8472 | 212.8472 | 0.00062352 | 0.0017165 | 0.0017165 | 0 | 0 | 0 | 80.4347 | 221.4249 | 221.4249 | 0.00062352 | 0.0017165 | 0.0017165 | -0.79499 | -2.1885 | -2.1885 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ERC | EDUCATION - RELOCATABLE CLASSROOM | New | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 4.6186 | 0.028286 | 5.6572 | Fixture/1000 sf | 77.3193 | 212.8487 | 212.8487 | 0.00062352 | 0.0017165 | 0.0017165 | 0 | 0 | 0 | 87.2935 | 240.3061 | 240.3061 | 0.00062352 | 0.0017165 | 0.0017165 | -0.87293 | -2.4031 | -2.4031 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ERC | EDUCATION - RELOCATABLE CLASSROOM | Existing | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 4.6186 | 0.028286 | 5.6572 | Fixture/1000 sf | 77.3188 | 212.8472 | 212.8472 | 0.00062352 | 0.0017165 | 0.0017165 | 0 | 0 | 0 | 80.4347 | 221.4249 | 221.4249 | 0.00062352 | 0.0017165 | 0.0017165 | -0.84176 | -2.3172 | -2.3172 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ERC | EDUCATION - RELOCATABLE CLASSROOM | New | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 4.6186 | 0.028286 | 5.6572 | Fixture/1000 sf | 77.3195 | 212.8493 | 212.8493 | 0.00062352 | 0.0017165 | 0.0017165 | 0 | 0 | 0 | 86.3582 | 237.7314 | 237.7314 | 0.00062352 | 0.0017165 | 0.0017165 | -0.89788 | -2.4717 | -2.4717 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ERC | EDUCATION - RELOCATABLE CLASSROOM | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 4.6186 | 0.028286 | 5.6572 | Fixture/1000 sf | 77.3135 | 212.8328 | 212.8328 | 0.00062352 | 0.0017165 | 0.0017165 | 0 | 0 | 0 | 81.6818 | 224.8579 | 224.8579 | 0.00062352 | 0.0017165 | 0.0017165 | -0.75135 | -2.0683 | -2.0683 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ERC | EDUCATION - RELOCATABLE CLASSROOM | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 4.6186 | 0.028286 | 5.6572 | Fixture/1000 sf | 77.3169 | 212.842 | 212.842 | 0.00062352 | 0.0017165 | 0.0017165 | 0 | 0 | 0 | 87.917 | 242.0226 | 242.0226 | 0.00062352 | 0.0017165 | 0.0017165 | -0.79499 | -2.1885 | -2.1885 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ERC | EDUCATION - RELOCATABLE CLASSROOM | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 4.6186 | 0.028286 | 5.6572 | Fixture/1000 sf | 77.3137 | 212.8334 | 212.8334 | 0.00062352 | 0.0017165 | 0.0017165 | 0 | 0 | 0 | 80.7465 | 222.2832 | 222.2832 | 0.00062352 | 0.0017165 | 0.0017165 | -1.406 | -3.8706 | -3.8706 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ESE | EDUCATION - SECONDARY SCHOOL | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 5.1904 | 0.026528 | 5.3056 | Fixture/1000 sf | 65.9709 | 212.9325 | 212.9325 | 0.020514 | 0.066214 | 0.066214 | 0 | 0 | 0 | 82.4637 | 266.1656 | 266.1656 | 0.02879 | 0.092924 | 0.092924 | -0.20688 | -0.66775 | -0.66775 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | EUN | EDUCATION - UNIVERSITY | Existing | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 4.6186 | 0.028286 | 5.6572 | Fixture/1000 sf | 73.2624 | 201.6806 | 201.6806 | 0.022448 | 0.061795 | 0.061795 | 0 | 0 | 0 | 77.6289 | 213.7008 | 213.7008 | 0.027373 | 0.075353 | 0.075353 | -0.77005 | -2.1198 | -2.1198 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | EUN | EDUCATION - UNIVERSITY | New | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 4.6186 | 0.028286 | 5.6572 | Fixture/1000 sf | 73.2655 | 201.6892 | 201.6892 | 0.022446 | 0.061791 | 0.061791 | 0 | 0 | 0 | 77.3171 | 212.8426 | 212.8426 | 0.026469 | 0.072864 | 0.072864 | -0.6017 | -1.6564 | -1.6564 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | EUN | EDUCATION - UNIVERSITY | Existing | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 4.6186 | 0.028286 | 5.6572 | Fixture/1000 sf | 73.2631 | 201.6824 | 201.6824 | 0.013686 | 0.037676 | 0.037676 | 0 | 0 | 0 | 81.0582 | 223.1414 | 223.1414 | 0.016835 | 0.046345 | 0.046345 | -0.56117 | -1.5448 | -1.5448 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | EUN | EDUCATION - UNIVERSITY | New | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 4.6186 | 0.028286 | 5.6572 | Fixture/1000 sf | 73.2674 | 201.6943 | 201.6943 | 0.013686 | 0.037676 | 0.037676 | 0 | 0 | 0 | 81.9935 | 225.7161 | 225.7161 | 0.017958 | 0.049434 | 0.049434 | -0.43335 | -1.1929 | -1.1929 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | EUN | EDUCATION - UNIVERSITY | Existing | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 4.6186 | 0.028286 | 5.6572 | Fixture/1000 sf | 73.266 | 201.6906 | 201.6906 | 0.013686 | 0.037675 | 0.037675 | 0 | 0 | 0 | 80.7465 | 222.2832 | 222.2832 | 0.016274 | 0.0448 | 0.0448 | -0.5487 | -1.5105 | -1.5105 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | EUN | EDUCATION - UNIVERSITY | New | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 4.6186 | 0.028286 | 5.6572 | Fixture/1000 sf | 73.2653 | 201.6886 | 201.6886 | 0.013686 | 0.037676 | 0.037676 | 0 | 0 | 0 | 80.123 | 220.5667 | 220.5667 | 0.017396 | 0.04789 | 0.04789 | -0.41153 | -1.1329 | -1.1329 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | EUN | EDUCATION - UNIVERSITY | Existing | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 4.6186 | 0.028286 | 5.6572 | Fixture/1000 sf | 73.2674 | 201.6943 | 201.6943 | 0.022446 | 0.061791 | 0.061791 | 0 | 0 | 0 | 81.9935 | 225.7161 | 225.7161 | 0.028744 | 0.079129 | 0.079129 | -0.43959 | -1.2101 | -1.2101 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | EUN | EDUCATION - UNIVERSITY | New | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 4.6186 | 0.028286 | 5.6572 | Fixture/1000 sf | 73.2616 | 201.6783 | 201.6783 | 0.022447 | 0.061794 | 0.061794 | 0 | 0 | 0 | 82.6171 | 227.4326 | 227.4326 | 0.028308 | 0.077928 | 0.077928 | -0.34606 | -0.95264 | -0.95264 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ERC | EDUCATION - RELOCATABLE CLASSROOM | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 5.093 | 0.036471 | 7.2942 | Fixture/1000 sf | 73.4399 | 230.7202 | 230.7202 | 0.020789 | 0.065312 | 0.065312 | 0 | 0 | 0 | 86.7693 | 272.5959 | 272.5959 | 0.027689 | 0.086989 | 0.086989 | -0.39091 | -1.2281 | -1.2281 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ERC | EDUCATION - RELOCATABLE CLASSROOM | Existing | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 5.093 | 0.036471 | 7.2942 | Fixture/1000 sf | 73.4453 | 230.7369 | 230.7369 | 0.020789 | 0.06531 | 0.06531 | 0 | 0 | 0 | 82.031 | 257.7101 | 257.7101 | 0.026682 | 0.083826 | 0.083826 | -0.44717 | -1.4048 | -1.4048 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ERC | EDUCATION - RELOCATABLE CLASSROOM | New | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 5.093 | 0.036471 | 7.2942 | Fixture/1000 sf | 73.4442 | 230.7334 | 230.7334 | 0.020789 | 0.06531 | 0.06531 | 0 | 0 | 0 | 86.4732 | 271.6655 | 271.6655 | 0.028489 | 0.089501 | 0.089501 | -0.44421 | -1.3955 | -1.3955 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ERC | EDUCATION - RELOCATABLE CLASSROOM | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 5.093 | 0.036471 | 7.2942 | Fixture/1000 sf | 73.4432 | 230.7303 | 230.7303 | 0.020788 | 0.065309 | 0.065309 | 0 | 0 | 0 | 81.7349 | 256.7797 | 256.7797 | 0.026534 | 0.08336 | 0.08336 | -0.45606 | -1.4328 | -1.4328 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ERC | EDUCATION - RELOCATABLE CLASSROOM | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 5.093 | 0.036471 | 7.2942 | Fixture/1000 sf | 73.442 | 230.7265 | 230.7265 | 0.020789 | 0.065312 | 0.065312 | 0 | 0 | 0 | 87.0654 | 273.5262 | 273.5262 | 0.029022 | 0.091175 | 0.091175 | -0.46494 | -1.4607 | -1.4607 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ERC | EDUCATION - RELOCATABLE CLASSROOM | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 5.093 | 0.036471 | 7.2942 | Fixture/1000 sf | 73.4414 | 230.7248 | 230.7248 | 0.00059228 | 0.0018607 | 0.0018607 | 0 | 0 | 0 | 79.6619 | 250.2672 | 250.2672 | 0.00059228 | 0.0018607 | 0.0018607 | -0.65151 | -2.0468 | -2.0468 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ERC | EDUCATION - RELOCATABLE CLASSROOM | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 5.093 | 0.036471 | 7.2942 | Fixture/1000 sf | 73.4401 | 230.7207 | 230.7207 | 0.00059228 | 0.0018607 | 0.0018607 | 0 | 0 | 0 | 85.8809 | 269.8048 | 269.8048 | 0.00059228 | 0.0018607 | 0.0018607 | -0.69593 | -2.1863 | -2.1863 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ERC | EDUCATION - RELOCATABLE CLASSROOM | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 5.093 | 0.036471 | 7.2942 | Fixture/1000 sf | 73.4458 | 230.7385 | 230.7385 | 0.020789 | 0.065311 | 0.065311 | 0 | 0 | 0 | 80.2542 | 252.1279 | 252.1279 | 0.026712 | 0.083919 | 0.083919 | -0.61005 | -1.9165 | -1.9165 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ERC | EDUCATION - RELOCATABLE CLASSROOM | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 5.093 | 0.036471 | 7.2942 | Fixture/1000 sf | 73.4444 | 230.7341 | 230.7341 | 0.02079 | 0.065313 | 0.065313 | 0 | 0 | 0 | 85.5847 | 268.8744 | 268.8744 | 0.028578 | 0.08978 | 0.08978 | -0.6752 | -2.1212 | -2.1212 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ERC | EDUCATION - RELOCATABLE CLASSROOM | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 5.093 | 0.036471 | 7.2942 | Fixture/1000 sf | 73.4439 | 230.7327 | 230.7327 | 0.020789 | 0.065311 | 0.065311 | 0 | 0 | 0 | 87.3616 | 274.4566 | 274.4566 | 0.027186 | 0.085407 | 0.085407 | -0.21144 | -0.66428 | -0.66428 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ERC | EDUCATION - RELOCATABLE CLASSROOM | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 5.093 | 0.036471 | 7.2942 | Fixture/1000 sf | 73.4424 | 230.7279 | 230.7279 | 0.020789 | 0.06531 | 0.06531 | 0 | 0 | 0 | 94.469 | 296.7853 | 296.7853 | 0.029081 | 0.091361 | 0.091361 | -0.23069 | -0.72475 | -0.72475 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ERC | EDUCATION - RELOCATABLE CLASSROOM | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 5.093 | 0.036471 | 7.2942 | Fixture/1000 sf | 73.443 | 230.7296 | 230.7296 | 0.00059228 | 0.0018607 | 0.0018607 | 0 | 0 | 0 | 73.443 | 230.7296 | 230.7296 | 0.00059228 | 0.0018607 | 0.0018607 | -1.1224 | -3.5261 | -3.5261 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ERC | EDUCATION - RELOCATABLE CLASSROOM | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 5.093 | 0.036471 | 7.2942 | Fixture/1000 sf | 73.442 | 230.7268 | 230.7268 | 0.00059228 | 0.0018607 | 0.0018607 | 0 | 0 | 0 | 76.9966 | 241.8939 | 241.8939 | 0.00059228 | 0.0018607 | 0.0018607 | -1.2349 | -3.8796 | -3.8796 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ERC | EDUCATION - RELOCATABLE CLASSROOM | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 5.1904 | 0.026528 | 5.3056 | Fixture/1000 sf | 71.756 | 231.6047 | 231.6047 | 0.020312 | 0.065561 | 0.065561 | 0 | 0 | 0 | 79.5702 | 256.8264 | 256.8264 | 0.025868 | 0.083492 | 0.083492 | -0.45427 | -1.4662 | -1.4662 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ERC | EDUCATION - RELOCATABLE CLASSROOM | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 5.1904 | 0.026528 | 5.3056 | Fixture/1000 sf | 71.7549 | 231.6013 | 231.6013 | 0.020312 | 0.065562 | 0.065562 | 0 | 0 | 0 | 84.7784 | 273.6369 | 273.6369 | 0.028124 | 0.090776 | 0.090776 | -0.46006 | -1.4849 | -1.4849 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ERC | EDUCATION - RELOCATABLE CLASSROOM | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 5.1904 | 0.026528 | 5.3056 | Fixture/1000 sf | 71.7606 | 231.6196 | 231.6196 | 0.020313 | 0.065562 | 0.065562 | 0 | 0 | 0 | 78.4128 | 253.0908 | 253.0908 | 0.026012 | 0.083959 | 0.083959 | -0.60184 | -1.9425 | -1.9425 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ERC | EDUCATION - RELOCATABLE CLASSROOM | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 5.1904 | 0.026528 | 5.3056 | Fixture/1000 sf | 71.7572 | 231.6088 | 231.6088 | 0.020313 | 0.065563 | 0.065563 | 0 | 0 | 0 | 83.3317 | 268.9673 | 268.9673 | 0.02769 | 0.089376 | 0.089376 | -0.66839 | -2.1573 | -2.1573 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ERC | EDUCATION - RELOCATABLE CLASSROOM | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 5.1904 | 0.026528 | 5.3056 | Fixture/1000 sf | 71.7569 | 231.6076 | 231.6076 | 0.020313 | 0.065563 | 0.065563 | 0 | 0 | 0 | 85.0678 | 274.5708 | 274.5708 | 0.026504 | 0.085547 | 0.085547 | -0.2118 | -0.68363 | -0.68363 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ERC | EDUCATION - RELOCATABLE CLASSROOM | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 5.1904 | 0.026528 | 5.3056 | Fixture/1000 sf | 71.7593 | 231.6154 | 231.6154 | 0.020312 | 0.065559 | 0.065559 | 0 | 0 | 0 | 91.7227 | 296.0508 | 296.0508 | 0.028182 | 0.090963 | 0.090963 | -0.22829 | -0.73686 | -0.73686 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ESE | EDUCATION - SECONDARY SCHOOL | Existing | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 4.6186 | 0.028286 | 5.6572 | Fixture/1000 sf | 71.0821 | 195.6787 | 195.6787 | 0.022104 | 0.060848 | 0.060848 | 0 | 0 | 0 | 69.2113 | 190.5284 | 190.5284 | 0.02625 | 0.072263 | 0.072263 | -1.5027 | -4.1367 | -4.1367 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ESE | EDUCATION - SECONDARY SCHOOL | New | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 4.6186 | 0.028286 | 5.6572 | Fixture/1000 sf | 71.0821 | 195.6786 | 195.6786 | 0.022104 | 0.060848 | 0.060848 | 0 | 0 | 0 | 70.7701 | 194.8196 | 194.8196 | 0.025627 | 0.070547 | 0.070547 | -1.1036 | -3.0382 | -3.0382 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ESE | EDUCATION - SECONDARY SCHOOL | Existing | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 4.6186 | 0.028286 | 5.6572 | Fixture/1000 sf | 71.0791 | 195.6703 | 195.6703 | 0.00062352 | 0.0017165 | 0.0017165 | 0 | 0 | 0 | 74.1995 | 204.2602 | 204.2602 | 0.00062352 | 0.0017165 | 0.0017165 | -0.92593 | -2.549 | -2.549 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ESE | EDUCATION - SECONDARY SCHOOL | New | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 4.6186 | 0.028286 | 5.6572 | Fixture/1000 sf | 71.0821 | 195.6785 | 195.6785 | 0.00062352 | 0.0017165 | 0.0017165 | 0 | 0 | 0 | 75.4465 | 207.6932 | 207.6932 | 0.00062352 | 0.0017165 | 0.0017165 | -1.0382 | -2.8579 | -2.8579 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ESE | EDUCATION - SECONDARY SCHOOL | Existing | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 4.6186 | 0.028286 | 5.6572 | Fixture/1000 sf | 71.0791 | 195.6703 | 195.6703 | 0.00062352 | 0.0017165 | 0.0017165 | 0 | 0 | 0 | 74.1995 | 204.2602 | 204.2602 | 0.00062352 | 0.0017165 | 0.0017165 | -0.95399 | -2.6262 | -2.6262 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ESE | EDUCATION - SECONDARY SCHOOL | New | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 4.6186 | 0.028286 | 5.6572 | Fixture/1000 sf | 71.0849 | 195.6864 | 195.6864 | 0.00062352 | 0.0017165 | 0.0017165 | 0 | 0 | 0 | 74.5112 | 205.1184 | 205.1184 | 0.00062352 | 0.0017165 | 0.0017165 | -0.96958 | -2.6691 | -2.6691 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ESE | EDUCATION - SECONDARY SCHOOL | Existing | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 4.6186 | 0.028286 | 5.6572 | Fixture/1000 sf | 71.0802 | 195.6734 | 195.6734 | 0.022105 | 0.060851 | 0.060851 | 0 | 0 | 0 | 76.07 | 209.4096 | 209.4096 | 0.026999 | 0.074323 | 0.074323 | -0.72641 | -1.9997 | -1.9997 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ESE | EDUCATION - SECONDARY SCHOOL | New | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 4.6186 | 0.028286 | 5.6572 | Fixture/1000 sf | 71.085 | 195.6864 | 195.6864 | 0.022104 | 0.060849 | 0.060849 | 0 | 0 | 0 | 76.6936 | 211.1261 | 211.1261 | 0.028994 | 0.079816 | 0.079816 | -0.81994 | -2.2572 | -2.2572 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ESE | EDUCATION - SECONDARY SCHOOL | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 4.6186 | 0.028286 | 5.6572 | Fixture/1000 sf | 71.0849 | 195.6864 | 195.6864 | 0.022104 | 0.060849 | 0.060849 | 0 | 0 | 0 | 74.5112 | 205.1184 | 205.1184 | 0.026313 | 0.072435 | 0.072435 | -0.87605 | -2.4116 | -2.4116 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ESE | EDUCATION - SECONDARY SCHOOL | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 4.6186 | 0.028286 | 5.6572 | Fixture/1000 sf | 71.0849 | 195.6864 | 195.6864 | 0.022104 | 0.060848 | 0.060848 | 0 | 0 | 0 | 74.5112 | 205.1184 | 205.1184 | 0.027155 | 0.074752 | 0.074752 | -0.78252 | -2.1542 | -2.1542 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ESE | EDUCATION - SECONDARY SCHOOL | Existing | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 4.6186 | 0.028286 | 5.6572 | Fixture/1000 sf | 71.0811 | 195.6759 | 195.6759 | 0.00062352 | 0.0017165 | 0.0017165 | 0 | 0 | 0 | 75.7583 | 208.5514 | 208.5514 | 0.00062352 | 0.0017165 | 0.0017165 | -0.81994 | -2.2572 | -2.2572 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ESE | EDUCATION - SECONDARY SCHOOL | New | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 4.6186 | 0.028286 | 5.6572 | Fixture/1000 sf | 71.0813 | 195.6763 | 195.6763 | 0.00062352 | 0.0017165 | 0.0017165 | 0 | 0 | 0 | 77.9406 | 214.559 | 214.559 | 0.00062352 | 0.0017165 | 0.0017165 | -0.88852 | -2.446 | -2.446 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ESE | EDUCATION - SECONDARY SCHOOL | Existing | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 4.6186 | 0.028286 | 5.6572 | Fixture/1000 sf | 71.0821 | 195.6785 | 195.6785 | 0.00062352 | 0.0017165 | 0.0017165 | 0 | 0 | 0 | 75.4465 | 207.6932 | 207.6932 | 0.00062352 | 0.0017165 | 0.0017165 | -0.84799 | -2.3344 | -2.3344 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ESE | EDUCATION - SECONDARY SCHOOL | New | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 4.6186 | 0.028286 | 5.6572 | Fixture/1000 sf | 71.084 | 195.6839 | 195.6839 | 0.00062352 | 0.0017165 | 0.0017165 | 0 | 0 | 0 | 77.0053 | 211.9843 | 211.9843 | 0.00062352 | 0.0017165 | 0.0017165 | -0.92593 | -2.549 | -2.549 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ESE | EDUCATION - SECONDARY SCHOOL | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 4.6186 | 0.028286 | 5.6572 | Fixture/1000 sf | 71.085 | 195.6864 | 195.6864 | 0.00062352 | 0.0017165 | 0.0017165 | 0 | 0 | 0 | 76.6936 | 211.1261 | 211.1261 | 0.00062352 | 0.0017165 | 0.0017165 | -0.74199 | -2.0426 | -2.0426 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ESE | EDUCATION - SECONDARY SCHOOL | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 4.6186 | 0.028286 | 5.6572 | Fixture/1000 sf | 71.085 | 195.6865 | 195.6865 | 0.00062352 | 0.0017165 | 0.0017165 | 0 | 0 | 0 | 78.8759 | 217.1338 | 217.1338 | 0.00062352 | 0.0017165 | 0.0017165 | -0.81994 | -2.2572 | -2.2572 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ESE | EDUCATION - SECONDARY SCHOOL | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 4.6186 | 0.028286 | 5.6572 | Fixture/1000 sf | 71.0816 | 195.6771 | 195.6771 | 0.00062352 | 0.0017165 | 0.0017165 | 0 | 0 | 0 | 69.8348 | 192.2449 | 192.2449 | 0.00062352 | 0.0017165 | 0.0017165 | -1.2969 | -3.5703 | -3.5703 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ESE | EDUCATION - SECONDARY SCHOOL | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 4.6186 | 0.028286 | 5.6572 | Fixture/1000 sf | 71.0808 | 195.6751 | 195.6751 | 0.00062352 | 0.0017165 | 0.0017165 | 0 | 0 | 0 | 71.3936 | 196.5361 | 196.5361 | 0.00062352 | 0.0017165 | 0.0017165 | -1.0693 | -2.9438 | -2.9438 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ESE | EDUCATION - SECONDARY SCHOOL | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 5.093 | 0.036471 | 7.2942 | Fixture/1000 sf | 67.5222 | 212.1287 | 212.1287 | 0.020997 | 0.065965 | 0.065965 | 0 | 0 | 0 | 71.0738 | 223.2867 | 223.2867 | 0.026801 | 0.084198 | 0.084198 | -0.68409 | -2.1491 | -2.1491 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ESE | EDUCATION - SECONDARY SCHOOL | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 5.093 | 0.036471 | 7.2942 | Fixture/1000 sf | 67.5195 | 212.1203 | 212.1203 | 0.020997 | 0.065963 | 0.065963 | 0 | 0 | 0 | 71.9622 | 226.0778 | 226.0778 | 0.026149 | 0.082151 | 0.082151 | -0.76997 | -2.4189 | -2.4189 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ESE | EDUCATION - SECONDARY SCHOOL | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 5.093 | 0.036471 | 7.2942 | Fixture/1000 sf | 67.5223 | 212.1291 | 212.1291 | 0.020996 | 0.065962 | 0.065962 | 0 | 0 | 0 | 75.2198 | 236.3118 | 236.3118 | 0.028045 | 0.088105 | 0.088105 | -0.50048 | -1.5723 | -1.5723 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ESE | EDUCATION - SECONDARY SCHOOL | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 5.093 | 0.036471 | 7.2942 | Fixture/1000 sf | 67.5215 | 212.1266 | 212.1266 | 0.020996 | 0.065963 | 0.065963 | 0 | 0 | 0 | 77.5889 | 243.7547 | 243.7547 | 0.027245 | 0.085593 | 0.085593 | -0.39683 | -1.2467 | -1.2467 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ESE | EDUCATION - SECONDARY SCHOOL | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 5.093 | 0.036471 | 7.2942 | Fixture/1000 sf | 67.5198 | 212.1214 | 212.1214 | 0.020996 | 0.06596 | 0.06596 | 0 | 0 | 0 | 78.1812 | 245.6154 | 245.6154 | 0.027097 | 0.085128 | 0.085128 | -0.34648 | -1.0885 | -1.0885 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ESE | EDUCATION - SECONDARY SCHOOL | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 5.093 | 0.036471 | 7.2942 | Fixture/1000 sf | 67.5197 | 212.1211 | 212.1211 | 0.020996 | 0.06596 | 0.06596 | 0 | 0 | 0 | 76.1082 | 239.1029 | 239.1029 | 0.028518 | 0.089594 | 0.089594 | -0.38202 | -1.2002 | -1.2002 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ESE | EDUCATION - SECONDARY SCHOOL | Existing | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 5.093 | 0.036471 | 7.2942 | Fixture/1000 sf | 67.5215 | 212.1266 | 212.1266 | 0.020997 | 0.065963 | 0.065963 | 0 | 0 | 0 | 77.5889 | 243.7547 | 243.7547 | 0.027275 | 0.085686 | 0.085686 | -0.39979 | -1.256 | -1.256 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ESE | EDUCATION - SECONDARY SCHOOL | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 5.093 | 0.036471 | 7.2942 | Fixture/1000 sf | 67.5187 | 212.118 | 212.118 | 0.00059228 | 0.0018607 | 0.0018607 | 0 | 0 | 0 | 74.3314 | 233.5207 | 233.5207 | 0.00059228 | 0.0018607 | 0.0018607 | -0.66336 | -2.084 | -2.084 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ESE | EDUCATION - SECONDARY SCHOOL | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 5.093 | 0.036471 | 7.2942 | Fixture/1000 sf | 67.5197 | 212.1211 | 212.1211 | 0.00059228 | 0.0018607 | 0.0018607 | 0 | 0 | 0 | 76.1082 | 239.1029 | 239.1029 | 0.00059228 | 0.0018607 | 0.0018607 | -0.72258 | -2.2701 | -2.2701 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ESE | EDUCATION - SECONDARY SCHOOL | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 5.093 | 0.036471 | 7.2942 | Fixture/1000 sf | 67.5205 | 212.1234 | 212.1234 | 0.020996 | 0.065962 | 0.065962 | 0 | 0 | 0 | 73.7391 | 231.66 | 231.66 | 0.02606 | 0.081872 | 0.081872 | -0.67224 | -2.1119 | -2.1119 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ESE | EDUCATION - SECONDARY SCHOOL | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 5.093 | 0.036471 | 7.2942 | Fixture/1000 sf | 67.5214 | 212.1264 | 212.1264 | 0.020997 | 0.065964 | 0.065964 | 0 | 0 | 0 | 75.5159 | 237.2421 | 237.2421 | 0.029288 | 0.092013 | 0.092013 | -0.73147 | -2.298 | -2.298 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ESE | EDUCATION - SECONDARY SCHOOL | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 5.093 | 0.036471 | 7.2942 | Fixture/1000 sf | 67.5208 | 212.1245 | 212.1245 | 0.020996 | 0.065962 | 0.065962 | 0 | 0 | 0 | 82.031 | 257.7101 | 257.7101 | 0.026653 | 0.083733 | 0.083733 | -0.1922 | -0.6038 | -0.6038 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ESE | EDUCATION - SECONDARY SCHOOL | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 5.093 | 0.036471 | 7.2942 | Fixture/1000 sf | 67.5186 | 212.1177 | 212.1177 | 0.020997 | 0.065965 | 0.065965 | 0 | 0 | 0 | 84.9924 | 267.0137 | 267.0137 | 0.02991 | 0.093966 | 0.093966 | -0.21174 | -0.66521 | -0.66521 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ESE | EDUCATION - SECONDARY SCHOOL | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 5.093 | 0.036471 | 7.2942 | Fixture/1000 sf | 67.5201 | 212.1224 | 212.1224 | 0.00059228 | 0.0018607 | 0.0018607 | 0 | 0 | 0 | 66.0394 | 207.4706 | 207.4706 | 0.00059228 | 0.0018607 | 0.0018607 | -1.1579 | -3.6377 | -3.6377 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ESE | EDUCATION - SECONDARY SCHOOL | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 5.1904 | 0.026528 | 5.3056 | Fixture/1000 sf | 65.9713 | 212.9338 | 212.9338 | 0.020515 | 0.066216 | 0.066216 | 0 | 0 | 0 | 74.0726 | 239.0821 | 239.0821 | 0.027546 | 0.088909 | 0.088909 | -0.37326 | -1.2047 | -1.2047 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ESE | EDUCATION - SECONDARY SCHOOL | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 5.1904 | 0.026528 | 5.3056 | Fixture/1000 sf | 65.9697 | 212.9285 | 212.9285 | 0.020514 | 0.066214 | 0.066214 | 0 | 0 | 0 | 74.6513 | 240.9499 | 240.9499 | 0.026012 | 0.083959 | 0.083959 | -0.3993 | -1.2888 | -1.2888 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ESE | EDUCATION - SECONDARY SCHOOL | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 5.1904 | 0.026528 | 5.3056 | Fixture/1000 sf | 65.9697 | 212.9285 | 212.9285 | 0.020515 | 0.066216 | 0.066216 | 0 | 0 | 0 | 74.6513 | 240.9499 | 240.9499 | 0.028935 | 0.093391 | 0.093391 | -0.48031 | -1.5503 | -1.5503 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ESE | EDUCATION - SECONDARY SCHOOL | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 5.1904 | 0.026528 | 5.3056 | Fixture/1000 sf | 65.9712 | 212.9335 | 212.9335 | 0.020515 | 0.066215 | 0.066215 | 0 | 0 | 0 | 72.0472 | 232.5447 | 232.5447 | 0.02526 | 0.081531 | 0.081531 | -0.64235 | -2.0733 | -2.0733 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ESE | EDUCATION - SECONDARY SCHOOL | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 5.1904 | 0.026528 | 5.3056 | Fixture/1000 sf | 65.973 | 212.9392 | 212.9392 | 0.020515 | 0.066215 | 0.066215 | 0 | 0 | 0 | 73.4939 | 237.2142 | 237.2142 | 0.028298 | 0.091337 | 0.091337 | -0.72047 | -2.3254 | -2.3254 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | ESE | EDUCATION - SECONDARY SCHOOL | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 5.1904 | 0.026528 | 5.3056 | Fixture/1000 sf | 65.9701 | 212.9297 | 212.9297 | 0.020514 | 0.066213 | 0.066213 | 0 | 0 | 0 | 80.7276 | 260.5621 | 260.5621 | 0.025983 | 0.083866 | 0.083866 | -0.17592 | -0.56782 | -0.56782 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | EUN | EDUCATION - UNIVERSITY | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 4.6186 | 0.028286 | 5.6572 | Fixture/1000 sf | 73.2623 | 201.6804 | 201.6804 | 0.022447 | 0.061792 | 0.061792 | 0 | 0 | 0 | 80.4347 | 221.4249 | 221.4249 | 0.027248 | 0.07501 | 0.07501 | -0.52376 | -1.4418 | -1.4418 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | EUN | EDUCATION - UNIVERSITY | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 4.6186 | 0.028286 | 5.6572 | Fixture/1000 sf | 73.2653 | 201.6886 | 201.6886 | 0.022448 | 0.061795 | 0.061795 | 0 | 0 | 0 | 80.123 | 220.5667 | 220.5667 | 0.027123 | 0.074667 | 0.074667 | -0.39906 | -1.0985 | -1.0985 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | EUN | EDUCATION - UNIVERSITY | Existing | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 4.6186 | 0.028286 | 5.6572 | Fixture/1000 sf | 73.2645 | 201.6863 | 201.6863 | 0.013687 | 0.037677 | 0.037677 | 0 | 0 | 0 | 82.3053 | 226.5744 | 226.5744 | 0.017053 | 0.046946 | 0.046946 | -0.50194 | -1.3818 | -1.3818 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | EUN | EDUCATION - UNIVERSITY | New | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 4.6186 | 0.028286 | 5.6572 | Fixture/1000 sf | 73.263 | 201.6821 | 201.6821 | 0.013686 | 0.037675 | 0.037675 | 0 | 0 | 0 | 83.8641 | 230.8655 | 230.8655 | 0.017989 | 0.04952 | 0.04952 | -0.39282 | -1.0814 | -1.0814 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | EUN | EDUCATION - UNIVERSITY | Existing | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 4.6186 | 0.028286 | 5.6572 | Fixture/1000 sf | 73.2674 | 201.6943 | 201.6943 | 0.013686 | 0.037677 | 0.037677 | 0 | 0 | 0 | 81.9935 | 225.7161 | 225.7161 | 0.016929 | 0.046602 | 0.046602 | -0.50506 | -1.3903 | -1.3903 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | EUN | EDUCATION - UNIVERSITY | New | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 4.6186 | 0.028286 | 5.6572 | Fixture/1000 sf | 73.2658 | 201.69 | 201.69 | 0.013686 | 0.037675 | 0.037675 | 0 | 0 | 0 | 83.5523 | 230.0073 | 230.0073 | 0.017989 | 0.04952 | 0.04952 | -0.36476 | -1.0041 | -1.0041 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | EUN | EDUCATION - UNIVERSITY | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 4.6186 | 0.028286 | 5.6572 | Fixture/1000 sf | 73.2651 | 201.6882 | 201.6882 | 0.013687 | 0.037677 | 0.037677 | 0 | 0 | 0 | 82.9288 | 228.2908 | 228.2908 | 0.017334 | 0.047718 | 0.047718 | -0.4427 | -1.2187 | -1.2187 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | EUN | EDUCATION - UNIVERSITY | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 4.6186 | 0.028286 | 5.6572 | Fixture/1000 sf | 73.2636 | 201.684 | 201.684 | 0.013686 | 0.037676 | 0.037676 | 0 | 0 | 0 | 84.4876 | 232.582 | 232.582 | 0.017958 | 0.049434 | 0.049434 | -0.34917 | -0.96122 | -0.96122 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | EUN | EDUCATION - UNIVERSITY | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 4.6186 | 0.028286 | 5.6572 | Fixture/1000 sf | 73.2632 | 201.6827 | 201.6827 | 0.013686 | 0.037675 | 0.037675 | 0 | 0 | 0 | 78.2524 | 215.4173 | 215.4173 | 0.01643 | 0.045229 | 0.045229 | -0.79811 | -2.1971 | -2.1971 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | GRO | GROCERY | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 5.6924 | 0.035581 | 7.1161 | Fixture/1000 sf | 145.4056 | 456.8087 | 456.8087 | 0.020434 | 0.064195 | 0.064195 | 0 | 0 | 0 | 157.547 | 494.9522 | 494.9522 | 0.026268 | 0.082523 | 0.082523 | -1.2556 | -3.9447 | -3.9447 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | GRO | GROCERY | Existing | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 5.6924 | 0.035581 | 7.1161 | Fixture/1000 sf | 145.4088 | 456.8189 | 456.8189 | 0.020434 | 0.064195 | 0.064195 | 0 | 0 | 0 | 153.6971 | 482.8575 | 482.8575 | 0.026445 | 0.083081 | 0.083081 | -1.6554 | -5.2007 | -5.2007 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | GRO | GROCERY | New | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 5.6924 | 0.035581 | 7.1161 | Fixture/1000 sf | 145.4092 | 456.82 | 456.82 | 0.020433 | 0.064193 | 0.064193 | 0 | 0 | 0 | 156.9547 | 493.0915 | 493.0915 | 0.027985 | 0.087919 | 0.087919 | -1.3445 | -4.2238 | -4.2238 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | HSP | HEALTH/MEDICAL - HOSPITAL | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 3.2792 | 0.017532 | 3.5064 | Fixture/1000 sf | 155.772 | 489.3761 | 489.3761 | 0.02449 | 0.076938 | 0.076938 | 0 | 0 | 0 | 159.0277 | 499.604 | 499.604 | 0.029496 | 0.092664 | 0.092664 | -1.5251 | -4.7914 | -4.7914 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | HSP | HEALTH/MEDICAL - HOSPITAL | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 3.2367 | 0.016208 | 3.2415 | Fixture/1000 sf | 152.1945 | 491.2337 | 491.2337 | 0.023928 | 0.077233 | 0.077233 | 0 | 0 | 0 | 174.4757 | 563.1503 | 563.1503 | 0.029803 | 0.096193 | 0.096193 | -0.78413 | -2.5309 | -2.5309 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | HSP | HEALTH/MEDICAL - HOSPITAL | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 3.2367 | 0.016208 | 3.2415 | Fixture/1000 sf | 152.1906 | 491.2213 | 491.2213 | 0.02393 | 0.077238 | 0.077238 | 0 | 0 | 0 | 167.5314 | 540.7364 | 540.7364 | 0.02879 | 0.092924 | 0.092924 | -0.81596 | -2.6336 | -2.6336 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | HSP | HEALTH/MEDICAL - HOSPITAL | Existing | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 3.2367 | 0.016208 | 3.2415 | Fixture/1000 sf | 152.1945 | 491.2337 | 491.2337 | 0.023928 | 0.077233 | 0.077233 | 0 | 0 | 0 | 174.4757 | 563.1503 | 563.1503 | 0.029513 | 0.095259 | 0.095259 | -0.71758 | -2.3161 | -2.3161 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | HSP | HEALTH/MEDICAL - HOSPITAL | New | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 3.2367 | 0.016208 | 3.2415 | Fixture/1000 sf | 152.1909 | 491.2224 | 491.2224 | 0.023928 | 0.077233 | 0.077233 | 0 | 0 | 0 | 168.1101 | 542.6042 | 542.6042 | 0.028558 | 0.092177 | 0.092177 | -0.67707 | -2.1854 | -2.1854 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | HSP | HEALTH/MEDICAL - HOSPITAL | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 3.2367 | 0.016208 | 3.2415 | Fixture/1000 sf | 152.1949 | 491.2352 | 491.2352 | 0.023928 | 0.077233 | 0.077233 | 0 | 0 | 0 | 175.3438 | 565.9521 | 565.9521 | 0.029803 | 0.096193 | 0.096193 | -0.77255 | -2.4936 | -2.4936 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | EUN | EDUCATION - UNIVERSITY | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 4.6186 | 0.028286 | 5.6572 | Fixture/1000 sf | 73.2639 | 201.6847 | 201.6847 | 0.013686 | 0.037676 | 0.037676 | 0 | 0 | 0 | 78.8759 | 217.1338 | 217.1338 | 0.01724 | 0.04746 | 0.04746 | -0.70147 | -1.931 | -1.931 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | EUN | EDUCATION - UNIVERSITY | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 5.093 | 0.036471 | 7.2942 | Fixture/1000 sf | 69.5942 | 218.6383 | 218.6383 | 0.021323 | 0.066988 | 0.066988 | 0 | 0 | 0 | 76.1082 | 239.1029 | 239.1029 | 0.026534 | 0.08336 | 0.08336 | -0.39091 | -1.2281 | -1.2281 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | EUN | EDUCATION - UNIVERSITY | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 5.093 | 0.036471 | 7.2942 | Fixture/1000 sf | 69.5927 | 218.6337 | 218.6337 | 0.021322 | 0.066984 | 0.066984 | 0 | 0 | 0 | 77.5889 | 243.7547 | 243.7547 | 0.025942 | 0.0815 | 0.0815 | -0.48567 | -1.5258 | -1.5258 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | EUN | EDUCATION - UNIVERSITY | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 5.093 | 0.036471 | 7.2942 | Fixture/1000 sf | 69.5959 | 218.6438 | 218.6438 | 0.021322 | 0.066985 | 0.066985 | 0 | 0 | 0 | 80.5503 | 253.0583 | 253.0583 | 0.027245 | 0.085593 | 0.085593 | -0.17502 | -0.54984 | -0.54984 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | EUN | EDUCATION - UNIVERSITY | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 5.093 | 0.036471 | 7.2942 | Fixture/1000 sf | 69.5932 | 218.6353 | 218.6353 | 0.021322 | 0.066984 | 0.066984 | 0 | 0 | 0 | 80.8465 | 253.9886 | 253.9886 | 0.027008 | 0.084849 | 0.084849 | -0.28696 | -0.90152 | -0.90152 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | EUN | EDUCATION - UNIVERSITY | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 5.093 | 0.036471 | 7.2942 | Fixture/1000 sf | 69.5906 | 218.6269 | 218.6269 | 0.021323 | 0.066988 | 0.066988 | 0 | 0 | 0 | 81.1426 | 254.919 | 254.919 | 0.027067 | 0.085035 | 0.085035 | -0.27808 | -0.87361 | -0.87361 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | EUN | EDUCATION - UNIVERSITY | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 5.093 | 0.036471 | 7.2942 | Fixture/1000 sf | 69.5939 | 218.6373 | 218.6373 | 0.021323 | 0.066987 | 0.066987 | 0 | 0 | 0 | 81.4388 | 255.8494 | 255.8494 | 0.02766 | 0.086896 | 0.086896 | -0.15607 | -0.4903 | -0.4903 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | EUN | EDUCATION - UNIVERSITY | Existing | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 5.093 | 0.036471 | 7.2942 | Fixture/1000 sf | 69.5932 | 218.6353 | 218.6353 | 0.021322 | 0.066985 | 0.066985 | 0 | 0 | 0 | 80.8465 | 253.9886 | 253.9886 | 0.027511 | 0.086431 | 0.086431 | -0.30799 | -0.96758 | -0.96758 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | EUN | EDUCATION - UNIVERSITY | New | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 5.093 | 0.036471 | 7.2942 | Fixture/1000 sf | 69.5912 | 218.629 | 218.629 | 0.021322 | 0.066986 | 0.066986 | 0 | 0 | 0 | 81.7349 | 256.7797 | 256.7797 | 0.028518 | 0.089594 | 0.089594 | -0.17976 | -0.56473 | -0.56473 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | EUN | EDUCATION - UNIVERSITY | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 5.093 | 0.036471 | 7.2942 | Fixture/1000 sf | 69.5926 | 218.6333 | 218.6333 | 0.021321 | 0.066984 | 0.066984 | 0 | 0 | 0 | 80.2542 | 252.1279 | 252.1279 | 0.027304 | 0.085779 | 0.085779 | -0.276 | -0.8671 | -0.8671 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | EUN | EDUCATION - UNIVERSITY | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 5.093 | 0.036471 | 7.2942 | Fixture/1000 sf | 69.5945 | 218.6393 | 218.6393 | 0.021322 | 0.066986 | 0.066986 | 0 | 0 | 0 | 82.031 | 257.7101 | 257.7101 | 0.028785 | 0.090431 | 0.090431 | -0.19368 | -0.60846 | -0.60846 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | EUN | EDUCATION - UNIVERSITY | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 5.093 | 0.036471 | 7.2942 | Fixture/1000 sf | 69.594 | 218.6378 | 218.6378 | 0.013 | 0.040842 | 0.040842 | 0 | 0 | 0 | 78.7735 | 247.4761 | 247.4761 | 0.016377 | 0.051449 | 0.051449 | -0.36425 | -1.1443 | -1.1443 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | EUN | EDUCATION - UNIVERSITY | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 5.093 | 0.036471 | 7.2942 | Fixture/1000 sf | 69.5932 | 218.6353 | 218.6353 | 0.013 | 0.040842 | 0.040842 | 0 | 0 | 0 | 80.8465 | 253.9886 | 253.9886 | 0.018005 | 0.056566 | 0.056566 | -0.34056 | -1.0699 | -1.0699 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | EUN | EDUCATION - UNIVERSITY | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 5.093 | 0.036471 | 7.2942 | Fixture/1000 sf | 69.594 | 218.6378 | 218.6378 | 0.021323 | 0.066987 | 0.066987 | 0 | 0 | 0 | 78.7735 | 247.4761 | 247.4761 | 0.027127 | 0.085221 | 0.085221 | -0.40275 | -1.2653 | -1.2653 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | EUN | EDUCATION - UNIVERSITY | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 5.093 | 0.036471 | 7.2942 | Fixture/1000 sf | 69.5953 | 218.6418 | 218.6418 | 0.021322 | 0.066986 | 0.066986 | 0 | 0 | 0 | 79.9581 | 251.1976 | 251.1976 | 0.027719 | 0.087082 | 0.087082 | -0.36425 | -1.1443 | -1.1443 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | EUN | EDUCATION - UNIVERSITY | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 5.093 | 0.036471 | 7.2942 | Fixture/1000 sf | 69.5905 | 218.6268 | 218.6268 | 0.021323 | 0.066987 | 0.066987 | 0 | 0 | 0 | 83.8079 | 263.2923 | 263.2923 | 0.027393 | 0.086058 | 0.086058 | -0.14689 | -0.46146 | -0.46146 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | EUN | EDUCATION - UNIVERSITY | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 5.093 | 0.036471 | 7.2942 | Fixture/1000 sf | 69.5936 | 218.6364 | 218.6364 | 0.021322 | 0.066985 | 0.066985 | 0 | 0 | 0 | 86.7693 | 272.5959 | 272.5959 | 0.029081 | 0.091361 | 0.091361 | -0.07522 | -0.23631 | -0.23631 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | EUN | EDUCATION - UNIVERSITY | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 5.093 | 0.036471 | 7.2942 | Fixture/1000 sf | 69.5914 | 218.6296 | 218.6296 | 0.013 | 0.040842 | 0.040842 | 0 | 0 | 0 | 73.7391 | 231.66 | 231.66 | 0.015725 | 0.049402 | 0.049402 | -0.79366 | -2.4934 | -2.4934 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | EUN | EDUCATION - UNIVERSITY | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 5.093 | 0.036471 | 7.2942 | Fixture/1000 sf | 69.5921 | 218.6319 | 218.6319 | 0.013001 | 0.040843 | 0.040843 | 0 | 0 | 0 | 74.3314 | 233.5207 | 233.5207 | 0.017028 | 0.053496 | 0.053496 | -0.75812 | -2.3817 | -2.3817 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | EUN | EDUCATION - UNIVERSITY | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 5.1904 | 0.026528 | 5.3056 | Fixture/1000 sf | 67.9952 | 219.4662 | 219.4662 | 0.020833 | 0.067242 | 0.067242 | 0 | 0 | 0 | 77.8341 | 251.223 | 251.223 | 0.026302 | 0.084893 | 0.084893 | -0.28935 | -0.93391 | -0.93391 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | EUN | EDUCATION - UNIVERSITY | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 5.1904 | 0.026528 | 5.3056 | Fixture/1000 sf | 67.9965 | 219.4703 | 219.4703 | 0.020833 | 0.067241 | 0.067241 | 0 | 0 | 0 | 78.9915 | 254.9586 | 254.9586 | 0.02633 | 0.084986 | 0.084986 | -0.19213 | -0.62012 | -0.62012 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | EUN | EDUCATION - UNIVERSITY | Existing | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 5.1904 | 0.026528 | 5.3056 | Fixture/1000 sf | 67.9979 | 219.4748 | 219.4748 | 0.020833 | 0.067241 | 0.067241 | 0 | 0 | 0 | 77.5448 | 250.289 | 250.289 | 0.02607 | 0.084146 | 0.084146 | -0.25202 | -0.81344 | -0.81344 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | EUN | EDUCATION - UNIVERSITY | New | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 5.1904 | 0.026528 | 5.3056 | Fixture/1000 sf | 67.9958 | 219.4682 | 219.4682 | 0.020832 | 0.06724 | 0.06724 | 0 | 0 | 0 | 78.4128 | 253.0908 | 253.0908 | 0.026128 | 0.084332 | 0.084332 | -0.1574 | -0.50805 | -0.50805 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | EUN | EDUCATION - UNIVERSITY | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 5.1904 | 0.026528 | 5.3056 | Fixture/1000 sf | 67.9958 | 219.4682 | 219.4682 | 0.020832 | 0.06724 | 0.06724 | 0 | 0 | 0 | 78.4128 | 253.0908 | 253.0908 | 0.026388 | 0.085173 | 0.085173 | -0.27922 | -0.90123 | -0.90123 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | EUN | EDUCATION - UNIVERSITY | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 5.1904 | 0.026528 | 5.3056 | Fixture/1000 sf | 67.9945 | 219.4639 | 219.4639 | 0.020832 | 0.06724 | 0.06724 | 0 | 0 | 0 | 79.8595 | 257.7604 | 257.7604 | 0.026649 | 0.086014 | 0.086014 | -0.17216 | -0.55568 | -0.55568 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | EUN | EDUCATION - UNIVERSITY | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 5.1904 | 0.026528 | 5.3056 | Fixture/1000 sf | 67.9985 | 219.4768 | 219.4768 | 0.020833 | 0.067242 | 0.067242 | 0 | 0 | 0 | 78.1235 | 252.1569 | 252.1569 | 0.026822 | 0.086574 | 0.086574 | -0.32407 | -1.046 | -1.046 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | EUN | EDUCATION - UNIVERSITY | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 5.1904 | 0.026528 | 5.3056 | Fixture/1000 sf | 67.9977 | 219.4742 | 219.4742 | 0.020833 | 0.067242 | 0.067242 | 0 | 0 | 0 | 80.1489 | 258.6943 | 258.6943 | 0.027575 | 0.089002 | 0.089002 | -0.20428 | -0.65934 | -0.65934 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | EUN | EDUCATION - UNIVERSITY | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 5.1904 | 0.026528 | 5.3056 | Fixture/1000 sf | 67.9946 | 219.4641 | 219.4641 | 0.020833 | 0.067242 | 0.067242 | 0 | 0 | 0 | 77.2554 | 249.3551 | 249.3551 | 0.026562 | 0.085733 | 0.085733 | -0.43402 | -1.4009 | -1.4009 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | EUN | EDUCATION - UNIVERSITY | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 5.1904 | 0.026528 | 5.3056 | Fixture/1000 sf | 67.9991 | 219.4787 | 219.4787 | 0.020833 | 0.067241 | 0.067241 | 0 | 0 | 0 | 78.7022 | 254.0247 | 254.0247 | 0.026591 | 0.085827 | 0.085827 | -0.37326 | -1.2047 | -1.2047 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | EUN | EDUCATION - UNIVERSITY | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 5.1904 | 0.026528 | 5.3056 | Fixture/1000 sf | 67.6196 | 218.2539 | 218.2539 | 0.021078 | 0.068032 | 0.068032 | 0 | 0 | 0 | 77.2554 | 249.3551 | 249.3551 | 0.026562 | 0.085733 | 0.085733 | -0.43402 | -1.4009 | -1.4009 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | EUN | EDUCATION - UNIVERSITY | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 5.1904 | 0.026528 | 5.3056 | Fixture/1000 sf | 67.9962 | 219.4695 | 219.4695 | 0.020832 | 0.06724 | 0.06724 | 0 | 0 | 0 | 84.1997 | 271.7691 | 271.7691 | 0.027719 | 0.089469 | 0.089469 | -0.080438 | -0.25963 | -0.25963 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | GRO | GROCERY | Existing | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 3.1087 | 0.024751 | 4.9502 | Fixture/1000 sf | 153.0755 | 421.3943 | 421.3943 | 0.021512 | 0.059219 | 0.059219 | 0 | 0 | 0 | 122.2109 | 336.4286 | 336.4286 | 0.021356 | 0.058789 | 0.058789 | -2.7529 | -7.5782 | -7.5782 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | GRO | GROCERY | New | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 3.1087 | 0.024751 | 4.9502 | Fixture/1000 sf | 153.0755 | 421.3942 | 421.3942 | 0.021512 | 0.05922 | 0.05922 | 0 | 0 | 0 | 127.8226 | 351.8768 | 351.8768 | 0.02438 | 0.067114 | 0.067114 | -2.8308 | -7.7928 | -7.7928 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | GRO | GROCERY | Existing | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 3.1087 | 0.024751 | 4.9502 | Fixture/1000 sf | 153.076 | 421.3956 | 421.3956 | 0.021512 | 0.059218 | 0.059218 | 0 | 0 | 0 | 139.6696 | 384.4898 | 384.4898 | 0.02784 | 0.07664 | 0.07664 | -2.0327 | -5.5957 | -5.5957 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | GRO | GROCERY | New | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 3.1087 | 0.024751 | 4.9502 | Fixture/1000 sf | 153.0749 | 421.3926 | 421.3926 | 0.021511 | 0.059217 | 0.059217 | 0 | 0 | 0 | 146.8401 | 404.2292 | 404.2292 | 0.028838 | 0.079387 | 0.079387 | -1.9735 | -5.4326 | -5.4326 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | GRO | GROCERY | Existing | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 3.1087 | 0.024751 | 4.9502 | Fixture/1000 sf | 153.0754 | 421.3942 | 421.3942 | 0.021512 | 0.05922 | 0.05922 | 0 | 0 | 0 | 133.4343 | 367.3251 | 367.3251 | 0.026656 | 0.073379 | 0.073379 | -2.3257 | -6.4024 | -6.4024 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | GRO | GROCERY | New | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 3.1087 | 0.024751 | 4.9502 | Fixture/1000 sf | 153.0754 | 421.3941 | 421.3941 | 0.021511 | 0.059217 | 0.059217 | 0 | 0 | 0 | 139.9813 | 385.348 | 385.348 | 0.027248 | 0.07501 | 0.07501 | -2.201 | -6.0591 | -6.0591 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | GRO | GROCERY | Existing | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 3.1087 | 0.024751 | 4.9502 | Fixture/1000 sf | 153.0749 | 421.3926 | 421.3926 | 0.021511 | 0.059217 | 0.059217 | 0 | 0 | 0 | 143.099 | 393.9304 | 393.9304 | 0.027435 | 0.075525 | 0.075525 | -1.9267 | -5.3039 | -5.3039 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | GRO | GROCERY | New | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 3.1087 | 0.024751 | 4.9502 | Fixture/1000 sf | 153.0749 | 421.3926 | 421.3926 | 0.021512 | 0.05922 | 0.05922 | 0 | 0 | 0 | 151.5166 | 417.1028 | 417.1028 | 0.028059 | 0.077241 | 0.077241 | -1.7583 | -4.8405 | -4.8405 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | GRO | GROCERY | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 3.1087 | 0.024751 | 4.9502 | Fixture/1000 sf | 153.0754 | 421.3942 | 421.3942 | 0.021511 | 0.059218 | 0.059218 | 0 | 0 | 0 | 132.499 | 364.7504 | 364.7504 | 0.02625 | 0.072263 | 0.072263 | -2.3257 | -6.4024 | -6.4024 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | GRO | GROCERY | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 3.1087 | 0.024751 | 4.9502 | Fixture/1000 sf | 153.0749 | 421.3926 | 421.3926 | 0.021511 | 0.059217 | 0.059217 | 0 | 0 | 0 | 139.3578 | 383.6316 | 383.6316 | 0.026625 | 0.073293 | 0.073293 | -2.1886 | -6.0248 | -6.0248 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | GRO | GROCERY | Existing | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 3.1087 | 0.024751 | 4.9502 | Fixture/1000 sf | 153.0749 | 421.3926 | 421.3926 | 0.021511 | 0.059218 | 0.059218 | 0 | 0 | 0 | 150.5813 | 414.5281 | 414.5281 | 0.028339 | 0.078014 | 0.078014 | -1.6523 | -4.5487 | -4.5487 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | GRO | GROCERY | New | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 3.1087 | 0.024751 | 4.9502 | Fixture/1000 sf | 153.0813 | 421.4104 | 421.4104 | 0.021511 | 0.059217 | 0.059217 | 0 | 0 | 0 | 156.8165 | 431.6928 | 431.6928 | 0.029524 | 0.081275 | 0.081275 | -1.5744 | -4.3341 | -4.3341 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | GRO | GROCERY | Existing | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 3.1087 | 0.024751 | 4.9502 | Fixture/1000 sf | 153.0754 | 421.394 | 421.394 | 0.021512 | 0.059218 | 0.059218 | 0 | 0 | 0 | 147.4636 | 405.9457 | 405.9457 | 0.027778 | 0.076469 | 0.076469 | -1.7895 | -4.9263 | -4.9263 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | GRO | GROCERY | New | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 3.1087 | 0.024751 | 4.9502 | Fixture/1000 sf | 153.0769 | 421.3981 | 421.3981 | 0.021511 | 0.059217 | 0.059217 | 0 | 0 | 0 | 154.0107 | 423.9687 | 423.9687 | 0.029087 | 0.080073 | 0.080073 | -1.6991 | -4.6774 | -4.6774 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | GRO | GROCERY | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 3.1087 | 0.024751 | 4.9502 | Fixture/1000 sf | 153.0749 | 421.3926 | 421.3926 | 0.021512 | 0.059218 | 0.059218 | 0 | 0 | 0 | 152.4518 | 419.6775 | 419.6775 | 0.027778 | 0.076469 | 0.076469 | -1.5588 | -4.2912 | -4.2912 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | GRO | GROCERY | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 3.1087 | 0.024751 | 4.9502 | Fixture/1000 sf | 153.0694 | 421.3777 | 421.3777 | 0.021511 | 0.059217 | 0.059217 | 0 | 0 | 0 | 158.6871 | 436.8422 | 436.8422 | 0.028963 | 0.07973 | 0.07973 | -1.4902 | -4.1024 | -4.1024 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | GRO | GROCERY | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 3.1087 | 0.024751 | 4.9502 | Fixture/1000 sf | 153.0749 | 421.3926 | 421.3926 | 0.021512 | 0.05922 | 0.05922 | 0 | 0 | 0 | 133.7461 | 368.1833 | 368.1833 | 0.026718 | 0.073551 | 0.073551 | -2.173 | -5.9819 | -5.9819 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | GRO | GROCERY | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 3.1087 | 0.024751 | 4.9502 | Fixture/1000 sf | 153.0754 | 421.3941 | 421.3941 | 0.021511 | 0.059217 | 0.059217 | 0 | 0 | 0 | 139.9813 | 385.348 | 385.348 | 0.027186 | 0.074838 | 0.074838 | -2.0639 | -5.6815 | -5.6815 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | GRO | GROCERY | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 5.6924 | 0.035581 | 7.1161 | Fixture/1000 sf | 145.4052 | 456.8074 | 456.8074 | 0.020434 | 0.064196 | 0.064196 | 0 | 0 | 0 | 144.5168 | 454.0163 | 454.0163 | 0.025616 | 0.080476 | 0.080476 | -2.2655 | -7.1173 | -7.1173 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | GRO | GROCERY | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 5.6924 | 0.035581 | 7.1161 | Fixture/1000 sf | 145.4052 | 456.8075 | 456.8075 | 0.020433 | 0.064194 | 0.064194 | 0 | 0 | 0 | 140.0747 | 440.0609 | 440.0609 | 0.025231 | 0.079267 | 0.079267 | -2.4698 | -7.7592 | -7.7592 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | GRO | GROCERY | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 5.6924 | 0.035581 | 7.1161 | Fixture/1000 sf | 145.4029 | 456.8002 | 456.8002 | 0.020434 | 0.064196 | 0.064196 | 0 | 0 | 0 | 155.7701 | 489.3701 | 489.3701 | 0.025616 | 0.080476 | 0.080476 | -1.4244 | -4.475 | -4.475 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | HSP | HEALTH/MEDICAL - HOSPITAL | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 3.2367 | 0.016208 | 3.2415 | Fixture/1000 sf | 152.1899 | 491.2191 | 491.2191 | 0.023928 | 0.077233 | 0.077233 | 0 | 0 | 0 | 166.374 | 537.0007 | 537.0007 | 0.029513 | 0.095259 | 0.095259 | -1.0416 | -3.3621 | -3.3621 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | HSP | HEALTH/MEDICAL - HOSPITAL | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 3.2367 | 0.016208 | 3.2415 | Fixture/1000 sf | 152.314 | 491.6195 | 491.6195 | 0.024015 | 0.077513 | 0.077513 | 0 | 0 | 0 | 174.7651 | 564.0842 | 564.0842 | 0.029803 | 0.096193 | 0.096193 | -0.73783 | -2.3815 | -2.3815 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | HSP | HEALTH/MEDICAL - HOSPITAL | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 3.2367 | 0.016208 | 3.2415 | Fixture/1000 sf | 152.1955 | 491.2372 | 491.2372 | 0.023928 | 0.077232 | 0.077232 | 0 | 0 | 0 | 176.5012 | 569.6877 | 569.6877 | 0.030092 | 0.097127 | 0.097127 | -0.58159 | -1.8772 | -1.8772 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | HTL | LODGING - HOTEL | Existing | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 3.2339 | 0.019917 | 3.9834 | Fixture/1000 sf | 60.7939 | 167.3566 | 167.3566 | 0.0075445 | 0.020769 | 0.020769 | 0 | 0 | 0 | 53.3114 | 146.7584 | 146.7584 | 0.0091658 | 0.025232 | 0.025232 | -0.37411 | -1.0299 | -1.0299 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | HTL | LODGING - HOTEL | New | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 3.2339 | 0.019917 | 3.9834 | Fixture/1000 sf | 60.7935 | 167.3555 | 167.3555 | 0.0075445 | 0.020769 | 0.020769 | 0 | 0 | 0 | 50.8173 | 139.8925 | 139.8925 | 0.0089788 | 0.024717 | 0.024717 | -0.46764 | -1.2874 | -1.2874 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | HTL | LODGING - HOTEL | Existing | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 3.2339 | 0.019917 | 3.9834 | Fixture/1000 sf | 60.7937 | 167.3562 | 167.3562 | 0.0075447 | 0.020769 | 0.020769 | 0 | 0 | 0 | 58.9231 | 162.2066 | 162.2066 | 0.009384 | 0.025833 | 0.025833 | -0.2678 | -0.73722 | -0.73722 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | HTL | LODGING - HOTEL | New | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 3.2339 | 0.019917 | 3.9834 | Fixture/1000 sf | 60.7935 | 167.3557 | 167.3557 | 0.0075444 | 0.020769 | 0.020769 | 0 | 0 | 0 | 57.6761 | 158.7737 | 158.7737 | 0.0096335 | 0.026519 | 0.026519 | -0.3367 | -0.9269 | -0.9269 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | HTL | LODGING - HOTEL | Existing | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 3.2339 | 0.019917 | 3.9834 | Fixture/1000 sf | 60.7935 | 167.3556 | 167.3556 | 0.0075447 | 0.020769 | 0.020769 | 0 | 0 | 0 | 59.5466 | 163.9231 | 163.9231 | 0.0092905 | 0.025575 | 0.025575 | -0.2625 | -0.72263 | -0.72263 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | GRO | GROCERY | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 5.6924 | 0.035581 | 7.1161 | Fixture/1000 sf | 145.4038 | 456.803 | 456.803 | 0.020434 | 0.064194 | 0.064194 | 0 | 0 | 0 | 153.401 | 481.9272 | 481.9272 | 0.026978 | 0.084756 | 0.084756 | -1.614 | -5.0705 | -5.0705 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | GRO | GROCERY | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 5.6924 | 0.035581 | 7.1161 | Fixture/1000 sf | 145.4069 | 456.8129 | 456.8129 | 0.020434 | 0.064195 | 0.064195 | 0 | 0 | 0 | 158.4354 | 497.7433 | 497.7433 | 0.02837 | 0.089129 | 0.089129 | -1.3415 | -4.2145 | -4.2145 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | GRO | GROCERY | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 5.6924 | 0.035581 | 7.1161 | Fixture/1000 sf | 145.4038 | 456.803 | 456.803 | 0.020434 | 0.064195 | 0.064195 | 0 | 0 | 0 | 153.401 | 481.9272 | 481.9272 | 0.026564 | 0.083453 | 0.083453 | -1.6554 | -5.2007 | -5.2007 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | GRO | GROCERY | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 5.6924 | 0.035581 | 7.1161 | Fixture/1000 sf | 145.4069 | 456.8129 | 456.8129 | 0.020434 | 0.064196 | 0.064196 | 0 | 0 | 0 | 158.4354 | 497.7433 | 497.7433 | 0.027778 | 0.087268 | 0.087268 | -1.5547 | -4.8844 | -4.8844 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | GRO | GROCERY | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 5.6924 | 0.035581 | 7.1161 | Fixture/1000 sf | 145.4122 | 456.8295 | 456.8295 | 0.020434 | 0.064196 | 0.064196 | 0 | 0 | 0 | 149.8473 | 470.7628 | 470.7628 | 0.025557 | 0.08029 | 0.08029 | -1.8746 | -5.8892 | -5.8892 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | GRO | GROCERY | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 5.6924 | 0.035581 | 7.1161 | Fixture/1000 sf | 145.3987 | 456.7871 | 456.7871 | 0.020433 | 0.064193 | 0.064193 | 0 | 0 | 0 | 153.1049 | 480.9968 | 480.9968 | 0.02612 | 0.082058 | 0.082058 | -1.685 | -5.2938 | -5.2938 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | HSP | HEALTH/MEDICAL - HOSPITAL | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 3.2367 | 0.016208 | 3.2415 | Fixture/1000 sf | 152.1914 | 491.224 | 491.224 | 0.023928 | 0.077233 | 0.077233 | 0 | 0 | 0 | 168.9782 | 545.406 | 545.406 | 0.028877 | 0.093205 | 0.093205 | -0.76387 | -2.4655 | -2.4655 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | HSP | HEALTH/MEDICAL - HOSPITAL | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 3.2367 | 0.016208 | 3.2415 | Fixture/1000 sf | 152.1949 | 491.2352 | 491.2352 | 0.02393 | 0.077237 | 0.077237 | 0 | 0 | 0 | 175.3438 | 565.9521 | 565.9521 | 0.030671 | 0.098995 | 0.098995 | -0.83332 | -2.6897 | -2.6897 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | HSP | HEALTH/MEDICAL - HOSPITAL | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 3.2367 | 0.016208 | 3.2415 | Fixture/1000 sf | 152.1913 | 491.2234 | 491.2234 | 0.023928 | 0.077233 | 0.077233 | 0 | 0 | 0 | 168.6888 | 544.472 | 544.472 | 0.029803 | 0.096193 | 0.096193 | -0.81885 | -2.643 | -2.643 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | HSP | HEALTH/MEDICAL - HOSPITAL | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 3.2367 | 0.016208 | 3.2415 | Fixture/1000 sf | 152.1934 | 491.2302 | 491.2302 | 0.02393 | 0.077238 | 0.077238 | 0 | 0 | 0 | 172.4503 | 556.6129 | 556.6129 | 0.030381 | 0.098061 | 0.098061 | -1.0214 | -3.2967 | -3.2967 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | HTL | LODGING - HOTEL | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 3.145 | 0.020487 | 4.0975 | Fixture/1000 sf | 57.7473 | 181.4199 | 181.4199 | 0.0071668 | 0.022515 | 0.022515 | 0 | 0 | 0 | 56.5629 | 177.699 | 177.699 | 0.0090323 | 0.028376 | 0.028376 | -0.20434 | -0.64195 | -0.64195 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | HTL | LODGING - HOTEL | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 3.145 | 0.020487 | 4.0975 | Fixture/1000 sf | 57.7472 | 181.4195 | 181.4195 | 0.0071664 | 0.022514 | 0.022514 | 0 | 0 | 0 | 53.6015 | 168.3954 | 168.3954 | 0.0091508 | 0.028748 | 0.028748 | -0.22951 | -0.72103 | -0.72103 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | HTL | LODGING - HOTEL | New | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 3.2339 | 0.019917 | 3.9834 | Fixture/1000 sf | 60.7937 | 167.356 | 167.356 | 0.0075449 | 0.02077 | 0.02077 | 0 | 0 | 0 | 57.3643 | 157.9155 | 157.9155 | 0.0093217 | 0.025661 | 0.025661 | -0.318 | -0.8754 | -0.8754 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | MTL | LODGING - MOTEL | Existing | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 3.2339 | 0.019917 | 3.9834 | Fixture/1000 sf | 48.3231 | 133.0264 | 133.0264 | 0.0053621 | 0.014761 | 0.014761 | 0 | 0 | 0 | 46.1408 | 127.019 | 127.019 | 0.0063911 | 0.017594 | 0.017594 | -0.48011 | -1.3217 | -1.3217 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | MTL | LODGING - MOTEL | New | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 3.2339 | 0.019917 | 3.9834 | Fixture/1000 sf | 48.323 | 133.026 | 133.026 | 0.0053621 | 0.014761 | 0.014761 | 0 | 0 | 0 | 43.6467 | 120.1531 | 120.1531 | 0.0063911 | 0.017594 | 0.017594 | -0.62352 | -1.7165 | -1.7165 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | MTL | LODGING - MOTEL | New | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 3.2339 | 0.019917 | 3.9834 | Fixture/1000 sf | 48.3209 | 133.0202 | 133.0202 | 0.0053625 | 0.014762 | 0.014762 | 0 | 0 | 0 | 48.6349 | 133.8848 | 133.8848 | 0.0065782 | 0.018109 | 0.018109 | -0.40217 | -1.1071 | -1.1071 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | MTL | LODGING - MOTEL | New | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 3.2339 | 0.019917 | 3.9834 | Fixture/1000 sf | 48.3212 | 133.0212 | 133.0212 | 0.0053623 | 0.014762 | 0.014762 | 0 | 0 | 0 | 49.882 | 137.3178 | 137.3178 | 0.0067029 | 0.018452 | 0.018452 | -0.33982 | -0.93548 | -0.93548 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | MTL | LODGING - MOTEL | Existing | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 3.2339 | 0.019917 | 3.9834 | Fixture/1000 sf | 48.3238 | 133.0282 | 133.0282 | 0.0053625 | 0.014762 | 0.014762 | 0 | 0 | 0 | 50.8173 | 139.8925 | 139.8925 | 0.0065782 | 0.018109 | 0.018109 | -0.25845 | -0.71148 | -0.71148 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | MTL | LODGING - MOTEL | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 3.2339 | 0.019917 | 3.9834 | Fixture/1000 sf | 48.321 | 133.0207 | 133.0207 | 0.0053623 | 0.014762 | 0.014762 | 0 | 0 | 0 | 49.2585 | 135.6013 | 135.6013 | 0.0064535 | 0.017765 | 0.017765 | -0.33047 | -0.90973 | -0.90973 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | NRS | HEALTH/MEDICAL - NURSING HOME | Existing | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 4.3484 | 0.024242 | 4.8484 | Fixture/1000 sf | 129.6937 | 357.0277 | 357.0277 | 0.021076 | 0.058018 | 0.058018 | 0 | 0 | 0 | 125.952 | 346.7274 | 346.7274 | 0.024037 | 0.06617 | 0.06617 | -2.837 | -7.8099 | -7.8099 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | NRS | HEALTH/MEDICAL - NURSING HOME | New | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 4.3484 | 0.024242 | 4.8484 | Fixture/1000 sf | 129.6932 | 357.0262 | 357.0262 | 0.021075 | 0.058016 | 0.058016 | 0 | 0 | 0 | 121.5874 | 334.7121 | 334.7121 | 0.022915 | 0.06308 | 0.06308 | -3.18 | -8.754 | -8.754 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | NRS | HEALTH/MEDICAL - NURSING HOME | Existing | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 4.3484 | 0.024242 | 4.8484 | Fixture/1000 sf | 129.699 | 357.0423 | 357.0423 | 0.021075 | 0.058016 | 0.058016 | 0 | 0 | 0 | 133.4343 | 367.3251 | 367.3251 | 0.026656 | 0.073379 | 0.073379 | -2.0483 | -5.6386 | -5.6386 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | NRS | HEALTH/MEDICAL - NURSING HOME | New | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 4.3484 | 0.024242 | 4.8484 | Fixture/1000 sf | 129.6932 | 357.0262 | 357.0262 | 0.021076 | 0.058018 | 0.058018 | 0 | 0 | 0 | 129.6932 | 357.0262 | 357.0262 | 0.026905 | 0.074066 | 0.074066 | -2.2665 | -6.2394 | -6.2394 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | NRS | HEALTH/MEDICAL - NURSING HOME | Existing | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 4.3484 | 0.024242 | 4.8484 | Fixture/1000 sf | 129.6966 | 357.0357 | 357.0357 | 0.021074 | 0.058015 | 0.058015 | 0 | 0 | 0 | 131.8755 | 363.0339 | 363.0339 | 0.025658 | 0.070633 | 0.070633 | -2.0982 | -5.7759 | -5.7759 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | NRS | HEALTH/MEDICAL - NURSING HOME | New | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 4.3484 | 0.024242 | 4.8484 | Fixture/1000 sf | 129.6929 | 357.0254 | 357.0254 | 0.021075 | 0.058016 | 0.058016 | 0 | 0 | 0 | 126.2638 | 347.5857 | 347.5857 | 0.026063 | 0.071749 | 0.071749 | -2.3725 | -6.5312 | -6.5312 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | NRS | HEALTH/MEDICAL - NURSING HOME | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 3.2792 | 0.017532 | 3.5064 | Fixture/1000 sf | 123.1983 | 387.042 | 387.042 | 0.020019 | 0.062893 | 0.062893 | 0 | 0 | 0 | 141.2592 | 443.7824 | 443.7824 | 0.026712 | 0.083919 | 0.083919 | -0.76701 | -2.4096 | -2.4096 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | NRS | HEALTH/MEDICAL - NURSING HOME | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 3.2792 | 0.017532 | 3.5064 | Fixture/1000 sf | 123.1952 | 387.0321 | 387.0321 | 0.02002 | 0.062894 | 0.062894 | 0 | 0 | 0 | 122.0101 | 383.3089 | 383.3089 | 0.025409 | 0.079825 | 0.079825 | -2.2033 | -6.9219 | -6.9219 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | NRS | HEALTH/MEDICAL - NURSING HOME | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 3.2792 | 0.017532 | 3.5064 | Fixture/1000 sf | 123.1948 | 387.0309 | 387.0309 | 0.020019 | 0.062893 | 0.062893 | 0 | 0 | 0 | 120.2332 | 377.7267 | 377.7267 | 0.025142 | 0.078988 | 0.078988 | -2.3869 | -7.4987 | -7.4987 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | HSP | HEALTH/MEDICAL - HOSPITAL | Existing | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 4.3484 | 0.024242 | 4.8484 | Fixture/1000 sf | 163.9938 | 451.4509 | 451.4509 | 0.025784 | 0.070979 | 0.070979 | 0 | 0 | 0 | 176.1458 | 484.9034 | 484.9034 | 0.029992 | 0.082562 | 0.082562 | -1.4029 | -3.8621 | -3.8621 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | HSP | HEALTH/MEDICAL - HOSPITAL | New | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 4.3484 | 0.024242 | 4.8484 | Fixture/1000 sf | 163.9894 | 451.4388 | 451.4388 | 0.025782 | 0.070974 | 0.070974 | 0 | 0 | 0 | 168.04 | 462.5893 | 462.5893 | 0.029056 | 0.079988 | 0.079988 | -1.3842 | -3.8106 | -3.8106 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | HSP | HEALTH/MEDICAL - HOSPITAL | Existing | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 4.3484 | 0.024242 | 4.8484 | Fixture/1000 sf | 163.9813 | 451.4165 | 451.4165 | 0.025782 | 0.070974 | 0.070974 | 0 | 0 | 0 | 180.8222 | 497.777 | 497.777 | 0.032112 | 0.088398 | 0.088398 | -1.0974 | -3.021 | -3.021 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | HSP | HEALTH/MEDICAL - HOSPITAL | New | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 4.3484 | 0.024242 | 4.8484 | Fixture/1000 sf | 163.9929 | 451.4482 | 451.4482 | 0.025783 | 0.070978 | 0.070978 | 0 | 0 | 0 | 174.2752 | 479.754 | 479.754 | 0.030989 | 0.085309 | 0.085309 | -1.1379 | -3.1326 | -3.1326 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | HSP | HEALTH/MEDICAL - HOSPITAL | Existing | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 4.3484 | 0.024242 | 4.8484 | Fixture/1000 sf | 163.9819 | 451.418 | 451.418 | 0.025783 | 0.070976 | 0.070976 | 0 | 0 | 0 | 181.7575 | 500.3517 | 500.3517 | 0.031176 | 0.085824 | 0.085824 | -1.0351 | -2.8493 | -2.8493 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | HSP | HEALTH/MEDICAL - HOSPITAL | New | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 4.3484 | 0.024242 | 4.8484 | Fixture/1000 sf | 163.9925 | 451.4473 | 451.4473 | 0.025783 | 0.070976 | 0.070976 | 0 | 0 | 0 | 173.6517 | 478.0376 | 478.0376 | 0.03021 | 0.083163 | 0.083163 | -1.0288 | -2.8322 | -2.8322 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | HSP | HEALTH/MEDICAL - HOSPITAL | New | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 4.3484 | 0.024242 | 4.8484 | Fixture/1000 sf | 163.9935 | 451.45 | 451.45 | 0.025782 | 0.070973 | 0.070973 | 0 | 0 | 0 | 175.5223 | 483.187 | 483.187 | 0.030709 | 0.084536 | 0.084536 | -1.0195 | -2.8064 | -2.8064 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | HSP | HEALTH/MEDICAL - HOSPITAL | Existing | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 4.3484 | 0.024242 | 4.8484 | Fixture/1000 sf | 163.9819 | 451.418 | 451.418 | 0.025782 | 0.070975 | 0.070975 | 0 | 0 | 0 | 181.7575 | 500.3517 | 500.3517 | 0.0318 | 0.08754 | 0.08754 | -0.98205 | -2.7034 | -2.7034 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | HSP | HEALTH/MEDICAL - HOSPITAL | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 4.3484 | 0.024242 | 4.8484 | Fixture/1000 sf | 163.9803 | 451.4135 | 451.4135 | 0.025783 | 0.070978 | 0.070978 | 0 | 0 | 0 | 178.9517 | 492.6276 | 492.6276 | 0.030646 | 0.084365 | 0.084365 | -1.1005 | -3.0296 | -3.0296 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | HSP | HEALTH/MEDICAL - HOSPITAL | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 4.3484 | 0.024242 | 4.8484 | Fixture/1000 sf | 163.992 | 451.4459 | 451.4459 | 0.025783 | 0.070976 | 0.070976 | 0 | 0 | 0 | 172.7164 | 475.4628 | 475.4628 | 0.029867 | 0.082219 | 0.082219 | -1.1317 | -3.1154 | -3.1154 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | HSP | HEALTH/MEDICAL - HOSPITAL | New | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 4.3484 | 0.024242 | 4.8484 | Fixture/1000 sf | 163.994 | 451.4514 | 451.4514 | 0.025783 | 0.070976 | 0.070976 | 0 | 0 | 0 | 176.4576 | 485.7617 | 485.7617 | 0.031176 | 0.085824 | 0.085824 | -1.0257 | -2.8236 | -2.8236 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | HSP | HEALTH/MEDICAL - HOSPITAL | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 4.3484 | 0.024242 | 4.8484 | Fixture/1000 sf | 163.9829 | 451.4209 | 451.4209 | 0.025782 | 0.070974 | 0.070974 | 0 | 0 | 0 | 183.6281 | 505.5011 | 505.5011 | 0.032112 | 0.088398 | 0.088398 | -0.96023 | -2.6434 | -2.6434 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | GRO | GROCERY | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 5.6924 | 0.035581 | 7.1161 | Fixture/1000 sf | 145.4024 | 456.7986 | 456.7986 | 0.020434 | 0.064196 | 0.064196 | 0 | 0 | 0 | 152.5126 | 479.1361 | 479.1361 | 0.027363 | 0.085965 | 0.085965 | -1.7147 | -5.3868 | -5.3868 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | GRO | GROCERY | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 5.6924 | 0.035581 | 7.1161 | Fixture/1000 sf | 145.402 | 456.7975 | 456.7975 | 0.020433 | 0.064193 | 0.064193 | 0 | 0 | 0 | 158.1393 | 496.8129 | 496.8129 | 0.028222 | 0.088663 | 0.088663 | -1.614 | -5.0705 | -5.0705 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | GRO | GROCERY | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 5.6924 | 0.035581 | 7.1161 | Fixture/1000 sf | 145.4064 | 456.8113 | 456.8113 | 0.020434 | 0.064197 | 0.064197 | 0 | 0 | 0 | 164.0621 | 515.4202 | 515.4202 | 0.02683 | 0.084291 | 0.084291 | -0.90619 | -2.8469 | -2.8469 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | GRO | GROCERY | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 5.6924 | 0.035581 | 7.1161 | Fixture/1000 sf | 145.3994 | 456.789 | 456.789 | 0.020434 | 0.064195 | 0.064195 | 0 | 0 | 0 | 170.8733 | 536.8185 | 536.8185 | 0.028548 | 0.089687 | 0.089687 | -0.74035 | -2.3259 | -2.3259 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | GRO | GROCERY | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 5.6924 | 0.035581 | 7.1161 | Fixture/1000 sf | 145.4047 | 456.8059 | 456.8059 | 0.020433 | 0.064194 | 0.064194 | 0 | 0 | 0 | 139.4824 | 438.2002 | 438.2002 | 0.025409 | 0.079825 | 0.079825 | -2.3099 | -7.2568 | -7.2568 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | GRO | GROCERY | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 5.6924 | 0.035581 | 7.1161 | Fixture/1000 sf | 145.4047 | 456.8059 | 456.8059 | 0.020434 | 0.064196 | 0.064196 | 0 | 0 | 0 | 143.9245 | 452.1556 | 452.1556 | 0.02609 | 0.081965 | 0.081965 | -2.15 | -6.7544 | -6.7544 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | GRO | GROCERY | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 4.103 | 0.023504 | 4.7008 | Fixture/1000 sf | 142.0666 | 458.5443 | 458.5443 | 0.019965 | 0.064439 | 0.064439 | 0 | 0 | 0 | 143.5157 | 463.2215 | 463.2215 | 0.024537 | 0.079196 | 0.079196 | -1.8026 | -5.8183 | -5.8183 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | GRO | GROCERY | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 4.103 | 0.023504 | 4.7008 | Fixture/1000 sf | 142.0738 | 458.5677 | 458.5677 | 0.019965 | 0.064439 | 0.064439 | 0 | 0 | 0 | 151.0387 | 487.5033 | 487.5033 | 0.024884 | 0.080317 | 0.080317 | -1.3368 | -4.3147 | -4.3147 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | GRO | GROCERY | Existing | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 4.103 | 0.023504 | 4.7008 | Fixture/1000 sf | 142.0685 | 458.5504 | 458.5504 | 0.019964 | 0.064437 | 0.064437 | 0 | 0 | 0 | 141.4903 | 456.6841 | 456.6841 | 0.023929 | 0.077235 | 0.077235 | -1.9155 | -6.1825 | -6.1825 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | GRO | GROCERY | New | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 4.103 | 0.023504 | 4.7008 | Fixture/1000 sf | 142.0676 | 458.5475 | 458.5475 | 0.019965 | 0.06444 | 0.06444 | 0 | 0 | 0 | 149.8813 | 483.7676 | 483.7676 | 0.024247 | 0.078262 | 0.078262 | -1.3368 | -4.3147 | -4.3147 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | GRO | GROCERY | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 4.103 | 0.023504 | 4.7008 | Fixture/1000 sf | 142.0671 | 458.546 | 458.546 | 0.019965 | 0.064441 | 0.064441 | 0 | 0 | 0 | 146.6985 | 473.4946 | 473.4946 | 0.025144 | 0.081157 | 0.081157 | -1.6319 | -5.2673 | -5.2673 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | GRO | GROCERY | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 4.103 | 0.023504 | 4.7008 | Fixture/1000 sf | 142.0632 | 458.5333 | 458.5333 | 0.019964 | 0.064438 | 0.064438 | 0 | 0 | 0 | 152.7748 | 493.1068 | 493.1068 | 0.025462 | 0.082184 | 0.082184 | -1.1776 | -3.801 | -3.801 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | GRO | GROCERY | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 4.103 | 0.023504 | 4.7008 | Fixture/1000 sf | 142.0748 | 458.5708 | 458.5708 | 0.019965 | 0.06444 | 0.06444 | 0 | 0 | 0 | 148.7239 | 480.032 | 480.032 | 0.026186 | 0.084519 | 0.084519 | -1.548 | -4.9964 | -4.9964 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | GRO | GROCERY | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 4.103 | 0.023504 | 4.7008 | Fixture/1000 sf | 142.0645 | 458.5377 | 458.5377 | 0.019964 | 0.064438 | 0.064438 | 0 | 0 | 0 | 153.6428 | 495.9085 | 495.9085 | 0.027459 | 0.088628 | 0.088628 | -1.2587 | -4.0625 | -4.0625 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | GRO | GROCERY | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 4.103 | 0.023504 | 4.7008 | Fixture/1000 sf | 142.0735 | 458.5666 | 458.5666 | 0.019965 | 0.064442 | 0.064442 | 0 | 0 | 0 | 147.8559 | 477.2302 | 477.2302 | 0.026504 | 0.085547 | 0.085547 | -1.6319 | -5.2673 | -5.2673 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | GRO | GROCERY | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 4.103 | 0.023504 | 4.7008 | Fixture/1000 sf | 142.068 | 458.549 | 458.549 | 0.019965 | 0.064441 | 0.064441 | 0 | 0 | 0 | 153.0641 | 494.0407 | 494.0407 | 0.027314 | 0.088162 | 0.088162 | -1.5046 | -4.8564 | -4.8564 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | GRO | GROCERY | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 4.103 | 0.023504 | 4.7008 | Fixture/1000 sf | 142.0689 | 458.5518 | 458.5518 | 0.019966 | 0.064442 | 0.064442 | 0 | 0 | 0 | 159.4297 | 514.5868 | 514.5868 | 0.026041 | 0.084052 | 0.084052 | -0.87093 | -2.8111 | -2.8111 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | GRO | GROCERY | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 4.103 | 0.023504 | 4.7008 | Fixture/1000 sf | 142.0697 | 458.5543 | 458.5543 | 0.019965 | 0.06444 | 0.06444 | 0 | 0 | 0 | 165.7953 | 535.1329 | 535.1329 | 0.027604 | 0.089095 | 0.089095 | -0.69443 | -2.2414 | -2.2414 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | HSP | HEALTH/MEDICAL - HOSPITAL | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 4.3484 | 0.024242 | 4.8484 | Fixture/1000 sf | 163.9801 | 451.413 | 451.413 | 0.025782 | 0.070974 | 0.070974 | 0 | 0 | 0 | 178.6399 | 491.7693 | 491.7693 | 0.031114 | 0.085652 | 0.085652 | -0.9914 | -2.7292 | -2.7292 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | HSP | HEALTH/MEDICAL - HOSPITAL | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 4.3484 | 0.024242 | 4.8484 | Fixture/1000 sf | 163.9924 | 451.4468 | 451.4468 | 0.025782 | 0.070974 | 0.070974 | 0 | 0 | 0 | 173.3399 | 477.1793 | 477.1793 | 0.031083 | 0.085566 | 0.085566 | -1.5713 | -4.3255 | -4.3255 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | HSP | HEALTH/MEDICAL - HOSPITAL | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 4.3484 | 0.024242 | 4.8484 | Fixture/1000 sf | 163.9889 | 451.4373 | 451.4373 | 0.025782 | 0.070975 | 0.070975 | 0 | 0 | 0 | 167.1047 | 460.0146 | 460.0146 | 0.030116 | 0.082906 | 0.082906 | -1.671 | -4.6001 | -4.6001 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | HSP | HEALTH/MEDICAL - HOSPITAL | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 3.2792 | 0.017532 | 3.5064 | Fixture/1000 sf | 155.7665 | 489.3588 | 489.3588 | 0.02449 | 0.076939 | 0.076939 | 0 | 0 | 0 | 175.0193 | 549.8435 | 549.8435 | 0.030206 | 0.094897 | 0.094897 | -1.0691 | -3.3586 | -3.3586 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | HSP | HEALTH/MEDICAL - HOSPITAL | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 3.2792 | 0.017532 | 3.5064 | Fixture/1000 sf | 155.7755 | 489.3869 | 489.3869 | 0.02449 | 0.076938 | 0.076938 | 0 | 0 | 0 | 165.2466 | 519.1416 | 519.1416 | 0.02917 | 0.091641 | 0.091641 | -1.078 | -3.3865 | -3.3865 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | HSP | HEALTH/MEDICAL - HOSPITAL | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 3.2792 | 0.017532 | 3.5064 | Fixture/1000 sf | 155.7694 | 489.3678 | 489.3678 | 0.02449 | 0.076938 | 0.076938 | 0 | 0 | 0 | 180.3498 | 566.59 | 566.59 | 0.030799 | 0.096758 | 0.096758 | -0.7907 | -2.4841 | -2.4841 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | HSP | HEALTH/MEDICAL - HOSPITAL | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 3.2792 | 0.017532 | 3.5064 | Fixture/1000 sf | 155.7645 | 489.3525 | 489.3525 | 0.024491 | 0.07694 | 0.07694 | 0 | 0 | 0 | 171.4656 | 538.6792 | 538.6792 | 0.029614 | 0.093036 | 0.093036 | -0.844 | -2.6515 | -2.6515 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | HSP | HEALTH/MEDICAL - HOSPITAL | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 3.2792 | 0.017532 | 3.5064 | Fixture/1000 sf | 155.77 | 489.3697 | 489.3697 | 0.02449 | 0.076938 | 0.076938 | 0 | 0 | 0 | 181.5344 | 570.3115 | 570.3115 | 0.030799 | 0.096758 | 0.096758 | -0.77589 | -2.4375 | -2.4375 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | HSP | HEALTH/MEDICAL - HOSPITAL | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 3.2792 | 0.017532 | 3.5064 | Fixture/1000 sf | 155.7654 | 489.3551 | 489.3551 | 0.02449 | 0.07694 | 0.07694 | 0 | 0 | 0 | 172.9463 | 543.331 | 543.331 | 0.02991 | 0.093966 | 0.093966 | -0.78773 | -2.4748 | -2.4748 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | HSP | HEALTH/MEDICAL - HOSPITAL | Existing | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 3.2792 | 0.017532 | 3.5064 | Fixture/1000 sf | 155.7705 | 489.3712 | 489.3712 | 0.024491 | 0.076943 | 0.076943 | 0 | 0 | 0 | 182.4228 | 573.1026 | 573.1026 | 0.031687 | 0.099549 | 0.099549 | -0.78773 | -2.4748 | -2.4748 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | HSP | HEALTH/MEDICAL - HOSPITAL | New | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 3.2792 | 0.017532 | 3.5064 | Fixture/1000 sf | 155.7657 | 489.3562 | 489.3562 | 0.02449 | 0.076939 | 0.076939 | 0 | 0 | 0 | 173.5386 | 545.1917 | 545.1917 | 0.030503 | 0.095827 | 0.095827 | -0.7907 | -2.4841 | -2.4841 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | HSP | HEALTH/MEDICAL - HOSPITAL | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 3.2792 | 0.017532 | 3.5064 | Fixture/1000 sf | 155.768 | 489.3634 | 489.3634 | 0.024492 | 0.076943 | 0.076943 | 0 | 0 | 0 | 177.6846 | 558.2168 | 558.2168 | 0.031391 | 0.098618 | 0.098618 | -0.84696 | -2.6608 | -2.6608 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | HSP | HEALTH/MEDICAL - HOSPITAL | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 3.2792 | 0.017532 | 3.5064 | Fixture/1000 sf | 155.7654 | 489.3551 | 489.3551 | 0.02449 | 0.076938 | 0.076938 | 0 | 0 | 0 | 172.9463 | 543.331 | 543.331 | 0.030799 | 0.096758 | 0.096758 | -0.83808 | -2.6329 | -2.6329 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | HSP | HEALTH/MEDICAL - HOSPITAL | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 3.2792 | 0.017532 | 3.5064 | Fixture/1000 sf | 155.7675 | 489.3619 | 489.3619 | 0.024492 | 0.076943 | 0.076943 | 0 | 0 | 0 | 176.7961 | 555.4257 | 555.4257 | 0.031391 | 0.098618 | 0.098618 | -0.9595 | -3.0144 | -3.0144 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | HSP | HEALTH/MEDICAL - HOSPITAL | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 3.2792 | 0.017532 | 3.5064 | Fixture/1000 sf | 155.765 | 489.3541 | 489.3541 | 0.02449 | 0.076938 | 0.076938 | 0 | 0 | 0 | 172.354 | 541.4703 | 541.4703 | 0.030799 | 0.096758 | 0.096758 | -0.96246 | -3.0237 | -3.0237 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | HSP | HEALTH/MEDICAL - HOSPITAL | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 3.2792 | 0.017532 | 3.5064 | Fixture/1000 sf | 155.7672 | 489.3608 | 489.3608 | 0.024492 | 0.076943 | 0.076943 | 0 | 0 | 0 | 176.2039 | 553.565 | 553.565 | 0.031391 | 0.098618 | 0.098618 | -1.0395 | -3.2656 | -3.2656 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | HSP | HEALTH/MEDICAL - HOSPITAL | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 3.2792 | 0.017532 | 3.5064 | Fixture/1000 sf | 155.7638 | 489.3503 | 489.3503 | 0.02449 | 0.076939 | 0.076939 | 0 | 0 | 0 | 170.281 | 534.9578 | 534.9578 | 0.030503 | 0.095827 | 0.095827 | -1.0631 | -3.34 | -3.34 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | HSP | HEALTH/MEDICAL - HOSPITAL | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 3.2792 | 0.017532 | 3.5064 | Fixture/1000 sf | 155.7717 | 489.3749 | 489.3749 | 0.024491 | 0.076943 | 0.076943 | 0 | 0 | 0 | 184.7919 | 580.5455 | 580.5455 | 0.031687 | 0.099549 | 0.099549 | -0.66928 | -2.1026 | -2.1026 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | HSP | HEALTH/MEDICAL - HOSPITAL | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 3.2792 | 0.017532 | 3.5064 | Fixture/1000 sf | 155.77 | 489.3697 | 489.3697 | 0.024492 | 0.076944 | 0.076944 | 0 | 0 | 0 | 181.5344 | 570.3115 | 570.3115 | 0.031095 | 0.097688 | 0.097688 | -0.59524 | -1.87 | -1.87 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | HSP | HEALTH/MEDICAL - HOSPITAL | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 3.2792 | 0.017532 | 3.5064 | Fixture/1000 sf | 155.7757 | 489.3874 | 489.3874 | 0.02449 | 0.076939 | 0.076939 | 0 | 0 | 0 | 165.5428 | 520.072 | 520.072 | 0.030206 | 0.094897 | 0.094897 | -1.4126 | -4.4378 | -4.4378 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | HTL | LODGING - HOTEL | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 3.2339 | 0.019917 | 3.9834 | Fixture/1000 sf | 60.7937 | 167.3562 | 167.3562 | 0.0075447 | 0.020769 | 0.020769 | 0 | 0 | 0 | 58.9231 | 162.2066 | 162.2066 | 0.009197 | 0.025318 | 0.025318 | -0.26718 | -0.73551 | -0.73551 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | HTL | LODGING - HOTEL | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 3.2339 | 0.019917 | 3.9834 | Fixture/1000 sf | 60.7938 | 167.3563 | 167.3563 | 0.0075445 | 0.020769 | 0.020769 | 0 | 0 | 0 | 57.0525 | 157.0572 | 157.0572 | 0.0092593 | 0.02549 | 0.02549 | -0.32735 | -0.90115 | -0.90115 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | HTL | LODGING - HOTEL | Existing | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 3.2339 | 0.019917 | 3.9834 | Fixture/1000 sf | 60.7928 | 167.3535 | 167.3535 | 0.0075444 | 0.020769 | 0.020769 | 0 | 0 | 0 | 61.729 | 169.9308 | 169.9308 | 0.0095399 | 0.026262 | 0.026262 | -0.22759 | -0.62651 | -0.62651 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | HTL | LODGING - HOTEL | New | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 3.2339 | 0.019917 | 3.9834 | Fixture/1000 sf | 60.7954 | 167.3608 | 167.3608 | 0.0075448 | 0.02077 | 0.02077 | 0 | 0 | 0 | 61.1054 | 168.2143 | 168.2143 | 0.0096958 | 0.026691 | 0.026691 | -0.29274 | -0.80588 | -0.80588 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | HTL | LODGING - HOTEL | Existing | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 3.2339 | 0.019917 | 3.9834 | Fixture/1000 sf | 60.7937 | 167.3561 | 167.3561 | 0.0075448 | 0.02077 | 0.02077 | 0 | 0 | 0 | 60.7937 | 167.3561 | 167.3561 | 0.0095088 | 0.026176 | 0.026176 | -0.23632 | -0.65054 | -0.65054 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | HTL | LODGING - HOTEL | New | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 3.2339 | 0.019917 | 3.9834 | Fixture/1000 sf | 60.7939 | 167.3567 | 167.3567 | 0.0075446 | 0.020769 | 0.020769 | 0 | 0 | 0 | 60.1702 | 165.6396 | 165.6396 | 0.0096646 | 0.026605 | 0.026605 | -0.29337 | -0.8076 | -0.8076 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | HTL | LODGING - HOTEL | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 3.2339 | 0.019917 | 3.9834 | Fixture/1000 sf | 60.7919 | 167.3511 | 167.3511 | 0.0075444 | 0.020769 | 0.020769 | 0 | 0 | 0 | 62.6643 | 172.5055 | 172.5055 | 0.0094464 | 0.026005 | 0.026005 | -0.212 | -0.5836 | -0.5836 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | HTL | LODGING - HOTEL | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 3.2339 | 0.019917 | 3.9834 | Fixture/1000 sf | 60.7928 | 167.3535 | 167.3535 | 0.0075446 | 0.020769 | 0.020769 | 0 | 0 | 0 | 61.729 | 169.9308 | 169.9308 | 0.0095711 | 0.026348 | 0.026348 | -0.2678 | -0.73722 | -0.73722 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | HTL | LODGING - HOTEL | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 3.2339 | 0.019917 | 3.9834 | Fixture/1000 sf | 60.7934 | 167.3553 | 167.3553 | 0.0075447 | 0.020769 | 0.020769 | 0 | 0 | 0 | 54.5584 | 150.1913 | 150.1913 | 0.009197 | 0.025318 | 0.025318 | -0.39282 | -1.0814 | -1.0814 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | HTL | LODGING - HOTEL | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 3.2339 | 0.019917 | 3.9834 | Fixture/1000 sf | 60.7938 | 167.3563 | 167.3563 | 0.0075445 | 0.020769 | 0.020769 | 0 | 0 | 0 | 53.6231 | 147.6166 | 147.6166 | 0.0092593 | 0.02549 | 0.02549 | -0.49258 | -1.356 | -1.356 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | HTL | LODGING - HOTEL | New | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 3.2339 | 0.019917 | 3.9834 | Fixture/1000 sf | 60.7939 | 167.3567 | 167.3567 | 0.0075448 | 0.02077 | 0.02077 | 0 | 0 | 0 | 60.1702 | 165.6396 | 165.6396 | 0.0095088 | 0.026176 | 0.026176 | -0.27342 | -0.75267 | -0.75267 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | HTL | LODGING - HOTEL | Existing | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 3.2339 | 0.019917 | 3.9834 | Fixture/1000 sf | 60.7911 | 167.3488 | 167.3488 | 0.0075445 | 0.020769 | 0.020769 | 0 | 0 | 0 | 61.4172 | 169.0725 | 169.0725 | 0.0093529 | 0.025747 | 0.025747 | -0.2173 | -0.59819 | -0.59819 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | MTL | LODGING - MOTEL | Existing | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 3.2339 | 0.019917 | 3.9834 | Fixture/1000 sf | 48.321 | 133.0207 | 133.0207 | 0.0053622 | 0.014761 | 0.014761 | 0 | 0 | 0 | 49.2585 | 135.6013 | 135.6013 | 0.0066405 | 0.01828 | 0.01828 | -0.318 | -0.8754 | -0.8754 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | MTL | LODGING - MOTEL | New | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 3.2339 | 0.019917 | 3.9834 | Fixture/1000 sf | 48.3231 | 133.0264 | 133.0264 | 0.0053624 | 0.014762 | 0.014762 | 0 | 0 | 0 | 48.0114 | 132.1684 | 132.1684 | 0.0067652 | 0.018624 | 0.018624 | -0.42088 | -1.1586 | -1.1586 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | MTL | LODGING - MOTEL | Existing | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 3.2339 | 0.019917 | 3.9834 | Fixture/1000 sf | 48.3212 | 133.0212 | 133.0212 | 0.0053623 | 0.014762 | 0.014762 | 0 | 0 | 0 | 49.882 | 137.3178 | 137.3178 | 0.0064847 | 0.017851 | 0.017851 | -0.30958 | -0.85223 | -0.85223 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | OFL | OFFICE - LARGE | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 4.2972 | 0.025741 | 5.1481 | Fixture/1000 sf | 78.1782 | 245.6059 | 245.6059 | 0.021026 | 0.066055 | 0.066055 | 0 | 0 | 0 | 91.5075 | 287.4816 | 287.4816 | 0.02766 | 0.086896 | 0.086896 | -0.34945 | -1.0978 | -1.0978 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | OFL | OFFICE - LARGE | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 4.2972 | 0.025741 | 5.1481 | Fixture/1000 sf | 78.179 | 245.6084 | 245.6084 | 0.021026 | 0.066056 | 0.066056 | 0 | 0 | 0 | 91.2114 | 286.5513 | 286.5513 | 0.026653 | 0.083733 | 0.083733 | -0.14392 | -0.45216 | -0.45216 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | OFL | OFFICE - LARGE | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 4.2972 | 0.025741 | 5.1481 | Fixture/1000 sf | 78.1832 | 245.6217 | 245.6217 | 0.021026 | 0.066054 | 0.066054 | 0 | 0 | 0 | 92.0998 | 289.3424 | 289.3424 | 0.027926 | 0.087733 | 0.087733 | -0.34648 | -1.0885 | -1.0885 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | OFL | OFFICE - LARGE | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 4.2972 | 0.025741 | 5.1481 | Fixture/1000 sf | 78.1782 | 245.6059 | 245.6059 | 0.021026 | 0.066056 | 0.066056 | 0 | 0 | 0 | 91.5075 | 287.4816 | 287.4816 | 0.026978 | 0.084756 | 0.084756 | -0.13149 | -0.41308 | -0.41308 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | OFL | OFFICE - LARGE | Existing | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 4.2972 | 0.025741 | 5.1481 | Fixture/1000 sf | 78.1782 | 245.6059 | 245.6059 | 0.021026 | 0.066055 | 0.066055 | 0 | 0 | 0 | 91.5075 | 287.4816 | 287.4816 | 0.02837 | 0.089129 | 0.089129 | -0.40571 | -1.2746 | -1.2746 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | OFL | OFFICE - LARGE | New | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 4.2972 | 0.025741 | 5.1481 | Fixture/1000 sf | 78.1782 | 245.6059 | 245.6059 | 0.021026 | 0.066055 | 0.066055 | 0 | 0 | 0 | 91.5075 | 287.4816 | 287.4816 | 0.02766 | 0.086896 | 0.086896 | -0.18775 | -0.58985 | -0.58985 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | OFL | OFFICE - LARGE | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 4.2972 | 0.025741 | 5.1481 | Fixture/1000 sf | 78.179 | 245.6084 | 245.6084 | 0.021026 | 0.066056 | 0.066056 | 0 | 0 | 0 | 91.2114 | 286.5513 | 286.5513 | 0.028074 | 0.088198 | 0.088198 | -0.33168 | -1.042 | -1.042 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | OFL | OFFICE - LARGE | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 4.2972 | 0.025741 | 5.1481 | Fixture/1000 sf | 78.1832 | 245.6217 | 245.6217 | 0.021026 | 0.066057 | 0.066057 | 0 | 0 | 0 | 92.0998 | 289.3424 | 289.3424 | 0.027778 | 0.087268 | 0.087268 | -0.14777 | -0.46425 | -0.46425 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | OFL | OFFICE - LARGE | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 4.2972 | 0.025741 | 5.1481 | Fixture/1000 sf | 78.1806 | 245.6135 | 245.6135 | 0.021025 | 0.066054 | 0.066054 | 0 | 0 | 0 | 90.6191 | 284.6906 | 284.6906 | 0.027571 | 0.086617 | 0.086617 | -0.47086 | -1.4793 | -1.4793 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | OFS | OFFICE - SMALL | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 4.2972 | 0.025741 | 5.1481 | Fixture/1000 sf | 76.7029 | 240.971 | 240.971 | 0.020551 | 0.064565 | 0.064565 | 0 | 0 | 0 | 87.0654 | 273.5262 | 273.5262 | 0.026238 | 0.08243 | 0.08243 | -0.12201 | -0.38331 | -0.38331 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | OFS | OFFICE - SMALL | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 4.2972 | 0.025741 | 5.1481 | Fixture/1000 sf | 76.7029 | 240.971 | 240.971 | 0.020552 | 0.064566 | 0.064566 | 0 | 0 | 0 | 87.0654 | 273.5262 | 273.5262 | 0.026978 | 0.084756 | 0.084756 | -0.055971 | -0.17584 | -0.17584 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | OFS | OFFICE - SMALL | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 4.2972 | 0.025741 | 5.1481 | Fixture/1000 sf | 76.6984 | 240.9569 | 240.9569 | 0.020552 | 0.064568 | 0.064568 | 0 | 0 | 0 | 85.2886 | 267.9441 | 267.9441 | 0.02606 | 0.081872 | 0.081872 | -0.29584 | -0.92943 | -0.92943 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | OFS | OFFICE - SMALL | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 4.2972 | 0.025741 | 5.1481 | Fixture/1000 sf | 76.7038 | 240.9739 | 240.9739 | 0.020552 | 0.064567 | 0.064567 | 0 | 0 | 0 | 84.6963 | 266.0833 | 266.0833 | 0.026564 | 0.083453 | 0.083453 | -0.21885 | -0.68754 | -0.68754 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | OFS | OFFICE - SMALL | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 4.2972 | 0.025741 | 5.1481 | Fixture/1000 sf | 76.7026 | 240.9701 | 240.9701 | 0.020552 | 0.064567 | 0.064567 | 0 | 0 | 0 | 85.5847 | 268.8744 | 268.8744 | 0.026564 | 0.083453 | 0.083453 | -0.22744 | -0.71452 | -0.71452 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | OFS | OFFICE - SMALL | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 4.2972 | 0.025741 | 5.1481 | Fixture/1000 sf | 76.7011 | 240.9653 | 240.9653 | 0.020552 | 0.064567 | 0.064567 | 0 | 0 | 0 | 84.9924 | 267.0137 | 267.0137 | 0.026919 | 0.08457 | 0.08457 | -0.17502 | -0.54984 | -0.54984 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | OFS | OFFICE - SMALL | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 4.2972 | 0.025741 | 5.1481 | Fixture/1000 sf | 76.7001 | 240.9624 | 240.9624 | 0.020552 | 0.064566 | 0.064566 | 0 | 0 | 0 | 92.6921 | 291.2031 | 291.2031 | 0.026179 | 0.082244 | 0.082244 | -0.037314 | -0.11723 | -0.11723 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | OFS | OFFICE - SMALL | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 4.2972 | 0.025741 | 5.1481 | Fixture/1000 sf | 76.6998 | 240.9614 | 240.9614 | 0.020553 | 0.064569 | 0.064569 | 0 | 0 | 0 | 91.2114 | 286.5513 | 286.5513 | 0.027245 | 0.085593 | 0.085593 | -0.0050344 | -0.015816 | -0.015816 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | OFS | OFFICE - SMALL | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 4.2972 | 0.025741 | 5.1481 | Fixture/1000 sf | 76.7022 | 240.9688 | 240.9688 | 0.020552 | 0.064566 | 0.064566 | 0 | 0 | 0 | 77.2928 | 242.8243 | 242.8243 | 0.025527 | 0.080197 | 0.080197 | -0.55971 | -1.7584 | -1.7584 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | HTL | LODGING - HOTEL | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 3.145 | 0.020487 | 4.0975 | Fixture/1000 sf | 57.7464 | 181.417 | 181.417 | 0.0071664 | 0.022514 | 0.022514 | 0 | 0 | 0 | 62.7819 | 197.2366 | 197.2366 | 0.0090619 | 0.028469 | 0.028469 | -0.13504 | -0.42424 | -0.42424 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | HTL | LODGING - HOTEL | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 3.145 | 0.020487 | 4.0975 | Fixture/1000 sf | 57.7496 | 181.427 | 181.427 | 0.0071665 | 0.022515 | 0.022515 | 0 | 0 | 0 | 61.3012 | 192.5848 | 192.5848 | 0.0092692 | 0.02912 | 0.02912 | -0.12793 | -0.40192 | -0.40192 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | HTL | LODGING - HOTEL | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 3.145 | 0.020487 | 4.0975 | Fixture/1000 sf | 57.7471 | 181.4192 | 181.4192 | 0.0071664 | 0.022514 | 0.022514 | 0 | 0 | 0 | 63.9664 | 200.958 | 200.958 | 0.0091508 | 0.028748 | 0.028748 | -0.11994 | -0.3768 | -0.3768 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | HTL | LODGING - HOTEL | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 3.145 | 0.020487 | 4.0975 | Fixture/1000 sf | 57.7449 | 181.4123 | 181.4123 | 0.0071665 | 0.022514 | 0.022514 | 0 | 0 | 0 | 62.4857 | 196.3062 | 196.3062 | 0.0093581 | 0.029399 | 0.029399 | -0.11016 | -0.34609 | -0.34609 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | HTL | LODGING - HOTEL | Existing | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 3.145 | 0.020487 | 4.0975 | Fixture/1000 sf | 57.7494 | 181.4264 | 181.4264 | 0.0071667 | 0.022515 | 0.022515 | 0 | 0 | 0 | 63.3742 | 199.0973 | 199.0973 | 0.0092988 | 0.029213 | 0.029213 | -0.12171 | -0.38238 | -0.38238 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | HTL | LODGING - HOTEL | New | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 3.145 | 0.020487 | 4.0975 | Fixture/1000 sf | 57.7472 | 181.4196 | 181.4196 | 0.0071665 | 0.022514 | 0.022514 | 0 | 0 | 0 | 61.8935 | 194.4455 | 194.4455 | 0.0095357 | 0.029958 | 0.029958 | -0.12349 | -0.38796 | -0.38796 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | HTL | LODGING - HOTEL | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 3.145 | 0.020487 | 4.0975 | Fixture/1000 sf | 57.7457 | 181.4148 | 181.4148 | 0.0071667 | 0.022515 | 0.022515 | 0 | 0 | 0 | 61.5973 | 193.5152 | 193.5152 | 0.00921 | 0.028934 | 0.028934 | -0.12971 | -0.4075 | -0.4075 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | HTL | LODGING - HOTEL | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 3.145 | 0.020487 | 4.0975 | Fixture/1000 sf | 57.7496 | 181.427 | 181.427 | 0.0071668 | 0.022515 | 0.022515 | 0 | 0 | 0 | 61.3012 | 192.5848 | 192.5848 | 0.0096838 | 0.030423 | 0.030423 | -0.14244 | -0.4475 | -0.4475 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | HTL | LODGING - HOTEL | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 3.145 | 0.020487 | 4.0975 | Fixture/1000 sf | 57.7473 | 181.42 | 181.42 | 0.0071667 | 0.022515 | 0.022515 | 0 | 0 | 0 | 59.8205 | 187.933 | 187.933 | 0.00921 | 0.028934 | 0.028934 | -0.17472 | -0.54891 | -0.54891 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | HTL | LODGING - HOTEL | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 3.145 | 0.020487 | 4.0975 | Fixture/1000 sf | 57.7482 | 181.4227 | 181.4227 | 0.0071665 | 0.022514 | 0.022514 | 0 | 0 | 0 | 58.932 | 185.1419 | 185.1419 | 0.0095357 | 0.029958 | 0.029958 | -0.18923 | -0.5945 | -0.5945 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | HTL | LODGING - HOTEL | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 3.145 | 0.020487 | 4.0975 | Fixture/1000 sf | 57.7498 | 181.4277 | 181.4277 | 0.0071665 | 0.022515 | 0.022515 | 0 | 0 | 0 | 59.2282 | 186.0723 | 186.0723 | 0.0092692 | 0.02912 | 0.02912 | -0.17591 | -0.55263 | -0.55263 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | HTL | LODGING - HOTEL | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 3.145 | 0.020487 | 4.0975 | Fixture/1000 sf | 57.7491 | 181.4255 | 181.4255 | 0.0071665 | 0.022514 | 0.022514 | 0 | 0 | 0 | 58.0436 | 182.3508 | 182.3508 | 0.0096246 | 0.030237 | 0.030237 | -0.21352 | -0.67079 | -0.67079 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | HTL | LODGING - HOTEL | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 3.145 | 0.020487 | 4.0975 | Fixture/1000 sf | 57.7462 | 181.4164 | 181.4164 | 0.0071667 | 0.022515 | 0.022515 | 0 | 0 | 0 | 66.9279 | 210.2617 | 210.2617 | 0.0092988 | 0.029213 | 0.029213 | -0.071962 | -0.22608 | -0.22608 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | HTL | LODGING - HOTEL | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 3.145 | 0.020487 | 4.0975 | Fixture/1000 sf | 57.749 | 181.4252 | 181.4252 | 0.0071668 | 0.022515 | 0.022515 | 0 | 0 | 0 | 67.5201 | 212.1224 | 212.1224 | 0.0097727 | 0.030702 | 0.030702 | -0.073739 | -0.23166 | -0.23166 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | HTL | LODGING - HOTEL | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 3.145 | 0.020487 | 4.0975 | Fixture/1000 sf | 57.7473 | 181.42 | 181.42 | 0.0071666 | 0.022515 | 0.022515 | 0 | 0 | 0 | 51.5285 | 161.8829 | 161.8829 | 0.0090027 | 0.028283 | 0.028283 | -0.30206 | -0.94897 | -0.94897 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | HTL | LODGING - HOTEL | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 3.145 | 0.020487 | 4.0975 | Fixture/1000 sf | 57.7474 | 181.4201 | 181.4201 | 0.0071666 | 0.022515 | 0.022515 | 0 | 0 | 0 | 49.7517 | 156.3007 | 156.3007 | 0.0091804 | 0.028841 | 0.028841 | -0.36425 | -1.1443 | -1.1443 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | HTL | LODGING - HOTEL | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 3.3193 | 0.018087 | 3.6174 | Fixture/1000 sf | 56.4222 | 182.1124 | 182.1124 | 0.007002 | 0.0226 | 0.0226 | 0 | 0 | 0 | 60.4733 | 195.1881 | 195.1881 | 0.0087672 | 0.028298 | 0.028298 | -0.14091 | -0.45482 | -0.45482 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | HTL | LODGING - HOTEL | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 3.3193 | 0.018087 | 3.6174 | Fixture/1000 sf | 56.4245 | 182.1199 | 182.1199 | 0.0070023 | 0.022601 | 0.022601 | 0 | 0 | 0 | 59.8947 | 193.3203 | 193.3203 | 0.0089987 | 0.029045 | 0.029045 | -0.13628 | -0.43987 | -0.43987 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | HTL | LODGING - HOTEL | Existing | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 3.3193 | 0.018087 | 3.6174 | Fixture/1000 sf | 56.4243 | 182.1192 | 182.1192 | 0.0070022 | 0.022601 | 0.022601 | 0 | 0 | 0 | 61.9201 | 199.8577 | 199.8577 | 0.0087093 | 0.028111 | 0.028111 | -0.11371 | -0.36703 | -0.36703 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | HTL | LODGING - HOTEL | New | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 3.3193 | 0.018087 | 3.6174 | Fixture/1000 sf | 56.42 | 182.1051 | 182.1051 | 0.0070023 | 0.022601 | 0.022601 | 0 | 0 | 0 | 61.052 | 197.0559 | 197.0559 | 0.0088251 | 0.028484 | 0.028484 | -0.090855 | -0.29325 | -0.29325 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | HTL | LODGING - HOTEL | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 3.3193 | 0.018087 | 3.6174 | Fixture/1000 sf | 56.4214 | 182.1099 | 182.1099 | 0.0070023 | 0.022601 | 0.022601 | 0 | 0 | 0 | 61.3414 | 197.9898 | 197.9898 | 0.0088251 | 0.028484 | 0.028484 | -0.125 | -0.40345 | -0.40345 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | HTL | LODGING - HOTEL | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 3.3193 | 0.018087 | 3.6174 | Fixture/1000 sf | 56.42 | 182.1051 | 182.1051 | 0.0070021 | 0.022601 | 0.022601 | 0 | 0 | 0 | 61.052 | 197.0559 | 197.0559 | 0.0090565 | 0.029232 | 0.029232 | -0.11661 | -0.37637 | -0.37637 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | HTL | LODGING - HOTEL | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 3.3193 | 0.018087 | 3.6174 | Fixture/1000 sf | 56.4222 | 182.1124 | 182.1124 | 0.007002 | 0.0226 | 0.0226 | 0 | 0 | 0 | 60.4733 | 195.1881 | 195.1881 | 0.0089408 | 0.028858 | 0.028858 | -0.13975 | -0.45108 | -0.45108 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | HTL | LODGING - HOTEL | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 3.3193 | 0.018087 | 3.6174 | Fixture/1000 sf | 56.4245 | 182.1199 | 182.1199 | 0.0070024 | 0.022601 | 0.022601 | 0 | 0 | 0 | 59.8947 | 193.3203 | 193.3203 | 0.0093748 | 0.030259 | 0.030259 | -0.15046 | -0.48564 | -0.48564 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | HTL | LODGING - HOTEL | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 3.3193 | 0.018087 | 3.6174 | Fixture/1000 sf | 56.4232 | 182.1156 | 182.1156 | 0.0070023 | 0.022601 | 0.022601 | 0 | 0 | 0 | 57.5799 | 185.8489 | 185.8489 | 0.0089987 | 0.029045 | 0.029045 | -0.18779 | -0.60611 | -0.60611 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | HTL | LODGING - HOTEL | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 3.3193 | 0.018087 | 3.6174 | Fixture/1000 sf | 56.4241 | 182.1184 | 182.1184 | 0.0070021 | 0.0226 | 0.0226 | 0 | 0 | 0 | 56.7118 | 183.0472 | 183.0472 | 0.0093169 | 0.030072 | 0.030072 | -0.22309 | -0.72005 | -0.72005 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | HTL | LODGING - HOTEL | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 3.3193 | 0.018087 | 3.6174 | Fixture/1000 sf | 56.4213 | 182.1093 | 182.1093 | 0.0070019 | 0.0226 | 0.0226 | 0 | 0 | 0 | 65.3922 | 211.0646 | 211.0646 | 0.0090276 | 0.029138 | 0.029138 | -0.080728 | -0.26056 | -0.26056 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | HTL | LODGING - HOTEL | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 3.3193 | 0.018087 | 3.6174 | Fixture/1000 sf | 56.4226 | 182.1137 | 182.1137 | 0.0070024 | 0.022601 | 0.022601 | 0 | 0 | 0 | 65.6816 | 211.9985 | 211.9985 | 0.0094616 | 0.030539 | 0.030539 | -0.07957 | -0.25683 | -0.25683 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | MTL | LODGING - MOTEL | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 3.2339 | 0.019917 | 3.9834 | Fixture/1000 sf | 48.3229 | 133.026 | 133.026 | 0.0053624 | 0.014762 | 0.014762 | 0 | 0 | 0 | 47.3879 | 130.4519 | 130.4519 | 0.0065158 | 0.017937 | 0.017937 | -0.45517 | -1.253 | -1.253 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | MTL | LODGING - MOTEL | Existing | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 3.2339 | 0.019917 | 3.9834 | Fixture/1000 sf | 48.3216 | 133.0221 | 133.0221 | 0.0053623 | 0.014762 | 0.014762 | 0 | 0 | 0 | 51.129 | 140.7507 | 140.7507 | 0.0067029 | 0.018452 | 0.018452 | -0.26749 | -0.73637 | -0.73637 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | MTL | LODGING - MOTEL | New | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 3.2339 | 0.019917 | 3.9834 | Fixture/1000 sf | 48.3236 | 133.0278 | 133.0278 | 0.0053624 | 0.014762 | 0.014762 | 0 | 0 | 0 | 50.1938 | 138.176 | 138.176 | 0.0067652 | 0.018624 | 0.018624 | -0.3367 | -0.9269 | -0.9269 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | MTL | LODGING - MOTEL | Existing | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 3.2339 | 0.019917 | 3.9834 | Fixture/1000 sf | 48.3214 | 133.0217 | 133.0217 | 0.0053623 | 0.014761 | 0.014761 | 0 | 0 | 0 | 50.5055 | 139.0343 | 139.0343 | 0.0066717 | 0.018366 | 0.018366 | -0.28152 | -0.77499 | -0.77499 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | MTL | LODGING - MOTEL | New | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 3.2339 | 0.019917 | 3.9834 | Fixture/1000 sf | 48.3212 | 133.0212 | 133.0212 | 0.0053624 | 0.014762 | 0.014762 | 0 | 0 | 0 | 49.882 | 137.3178 | 137.3178 | 0.0067652 | 0.018624 | 0.018624 | -0.34917 | -0.96122 | -0.96122 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | MTL | LODGING - MOTEL | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 3.2339 | 0.019917 | 3.9834 | Fixture/1000 sf | 48.3217 | 133.0226 | 133.0226 | 0.0053623 | 0.014761 | 0.014761 | 0 | 0 | 0 | 51.7526 | 142.4672 | 142.4672 | 0.0066717 | 0.018366 | 0.018366 | -0.24972 | -0.68745 | -0.68745 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | MTL | LODGING - MOTEL | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 3.2339 | 0.019917 | 3.9834 | Fixture/1000 sf | 48.3238 | 133.0282 | 133.0282 | 0.0053624 | 0.014762 | 0.014762 | 0 | 0 | 0 | 50.8173 | 139.8925 | 139.8925 | 0.0067341 | 0.018538 | 0.018538 | -0.318 | -0.8754 | -0.8754 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | MTL | LODGING - MOTEL | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 3.2339 | 0.019917 | 3.9834 | Fixture/1000 sf | 48.3231 | 133.0264 | 133.0264 | 0.0053623 | 0.014762 | 0.014762 | 0 | 0 | 0 | 46.1408 | 127.019 | 127.019 | 0.0064535 | 0.017765 | 0.017765 | -0.41776 | -1.15 | -1.15 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | MTL | LODGING - MOTEL | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 3.2339 | 0.019917 | 3.9834 | Fixture/1000 sf | 48.3233 | 133.0269 | 133.0269 | 0.0053624 | 0.014762 | 0.014762 | 0 | 0 | 0 | 44.8938 | 123.586 | 123.586 | 0.0065158 | 0.017937 | 0.017937 | -0.49258 | -1.356 | -1.356 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | MTL | LODGING - MOTEL | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 3.145 | 0.020487 | 4.0975 | Fixture/1000 sf | 45.9023 | 144.2073 | 144.2073 | 0.0050937 | 0.016003 | 0.016003 | 0 | 0 | 0 | 47.6787 | 149.7882 | 149.7882 | 0.0064263 | 0.020189 | 0.020189 | -0.2606 | -0.81872 | -0.81872 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | MTL | LODGING - MOTEL | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 3.145 | 0.020487 | 4.0975 | Fixture/1000 sf | 45.9017 | 144.2055 | 144.2055 | 0.0050934 | 0.016002 | 0.016002 | 0 | 0 | 0 | 45.3096 | 142.3453 | 142.3453 | 0.0064855 | 0.020375 | 0.020375 | -0.35833 | -1.1257 | -1.1257 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | MTL | LODGING - MOTEL | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 3.145 | 0.020487 | 4.0975 | Fixture/1000 sf | 45.9012 | 144.204 | 144.204 | 0.0050934 | 0.016002 | 0.016002 | 0 | 0 | 0 | 52.1208 | 163.7436 | 163.7436 | 0.0064855 | 0.020375 | 0.020375 | -0.13652 | -0.4289 | -0.4289 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | NRS | HEALTH/MEDICAL - NURSING HOME | Existing | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 4.3484 | 0.024242 | 4.8484 | Fixture/1000 sf | 129.6898 | 357.0171 | 357.0171 | 0.021076 | 0.058019 | 0.058019 | 0 | 0 | 0 | 135.6167 | 373.3327 | 373.3327 | 0.026282 | 0.072349 | 0.072349 | -1.7615 | -4.849 | -4.849 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | NRS | HEALTH/MEDICAL - NURSING HOME | New | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 4.3484 | 0.024242 | 4.8484 | Fixture/1000 sf | 129.6966 | 357.0357 | 357.0357 | 0.021074 | 0.058015 | 0.058015 | 0 | 0 | 0 | 131.8755 | 363.0339 | 363.0339 | 0.026562 | 0.073122 | 0.073122 | -1.9423 | -5.3468 | -5.3468 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | NRS | HEALTH/MEDICAL - NURSING HOME | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 4.3484 | 0.024242 | 4.8484 | Fixture/1000 sf | 129.6952 | 357.0317 | 357.0317 | 0.021074 | 0.058014 | 0.058014 | 0 | 0 | 0 | 130.9402 | 360.4592 | 360.4592 | 0.02491 | 0.068573 | 0.068573 | -2.1262 | -5.8532 | -5.8532 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | NRS | HEALTH/MEDICAL - NURSING HOME | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 4.3484 | 0.024242 | 4.8484 | Fixture/1000 sf | 129.6934 | 357.0268 | 357.0268 | 0.021075 | 0.058016 | 0.058016 | 0 | 0 | 0 | 126.5756 | 348.4439 | 348.4439 | 0.025003 | 0.068831 | 0.068831 | -2.385 | -6.5655 | -6.5655 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | NRS | HEALTH/MEDICAL - NURSING HOME | Existing | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 4.3484 | 0.024242 | 4.8484 | Fixture/1000 sf | 129.6927 | 357.025 | 357.025 | 0.021076 | 0.058018 | 0.058018 | 0 | 0 | 0 | 137.4872 | 378.4822 | 378.4822 | 0.026905 | 0.074066 | 0.074066 | -1.696 | -4.6688 | -4.6688 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | NRS | HEALTH/MEDICAL - NURSING HOME | New | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 4.3484 | 0.024242 | 4.8484 | Fixture/1000 sf | 129.6889 | 357.0144 | 357.0144 | 0.021075 | 0.058015 | 0.058015 | 0 | 0 | 0 | 134.9931 | 371.6163 | 371.6163 | 0.026843 | 0.073894 | 0.073894 | -1.802 | -4.9606 | -4.9606 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | NRS | HEALTH/MEDICAL - NURSING HOME | Existing | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 4.3484 | 0.024242 | 4.8484 | Fixture/1000 sf | 129.6908 | 357.0197 | 357.0197 | 0.021076 | 0.058018 | 0.058018 | 0 | 0 | 0 | 136.2402 | 375.0492 | 375.0492 | 0.026905 | 0.074066 | 0.074066 | -1.7895 | -4.9263 | -4.9263 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | NRS | HEALTH/MEDICAL - NURSING HOME | New | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 4.3484 | 0.024242 | 4.8484 | Fixture/1000 sf | 129.699 | 357.0423 | 357.0423 | 0.021076 | 0.058019 | 0.058019 | 0 | 0 | 0 | 133.4343 | 367.3251 | 367.3251 | 0.02703 | 0.074409 | 0.074409 | -1.9049 | -5.2438 | -5.2438 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | NRS | HEALTH/MEDICAL - NURSING HOME | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 4.3484 | 0.024242 | 4.8484 | Fixture/1000 sf | 129.6937 | 357.0275 | 357.0275 | 0.021076 | 0.058019 | 0.058019 | 0 | 0 | 0 | 138.1108 | 380.1986 | 380.1986 | 0.026874 | 0.07398 | 0.07398 | -1.6336 | -4.4972 | -4.4972 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | NRS | HEALTH/MEDICAL - NURSING HOME | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 4.3484 | 0.024242 | 4.8484 | Fixture/1000 sf | 129.6903 | 357.0184 | 357.0184 | 0.021075 | 0.058016 | 0.058016 | 0 | 0 | 0 | 135.9284 | 374.191 | 374.191 | 0.026967 | 0.074237 | 0.074237 | -1.724 | -4.746 | -4.746 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | NRS | HEALTH/MEDICAL - NURSING HOME | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 4.3484 | 0.024242 | 4.8484 | Fixture/1000 sf | 129.6927 | 357.0249 | 357.0249 | 0.021074 | 0.058015 | 0.058015 | 0 | 0 | 0 | 129.3814 | 356.168 | 356.168 | 0.025502 | 0.070204 | 0.070204 | -2.4473 | -6.7372 | -6.7372 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | NRS | HEALTH/MEDICAL - NURSING HOME | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 4.3484 | 0.024242 | 4.8484 | Fixture/1000 sf | 129.6926 | 357.0246 | 357.0246 | 0.021074 | 0.058015 | 0.058015 | 0 | 0 | 0 | 126.8873 | 349.3021 | 349.3021 | 0.025658 | 0.070633 | 0.070633 | -2.5907 | -7.1319 | -7.1319 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | MTL | LODGING - MOTEL | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 3.145 | 0.020487 | 4.0975 | Fixture/1000 sf | 45.9009 | 144.2031 | 144.2031 | 0.0050937 | 0.016002 | 0.016002 | 0 | 0 | 0 | 50.9362 | 160.0221 | 160.0221 | 0.0066039 | 0.020747 | 0.020747 | -0.19634 | -0.61683 | -0.61683 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | MTL | LODGING - MOTEL | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 3.145 | 0.020487 | 4.0975 | Fixture/1000 sf | 45.9034 | 144.2108 | 144.2108 | 0.0050936 | 0.016002 | 0.016002 | 0 | 0 | 0 | 53.0092 | 166.5347 | 166.5347 | 0.0065447 | 0.020561 | 0.020561 | -0.11549 | -0.36284 | -0.36284 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | MTL | LODGING - MOTEL | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 3.145 | 0.020487 | 4.0975 | Fixture/1000 sf | 45.9032 | 144.2101 | 144.2101 | 0.0050934 | 0.016002 | 0.016002 | 0 | 0 | 0 | 51.8247 | 162.8132 | 162.8132 | 0.0066928 | 0.021026 | 0.021026 | -0.16258 | -0.51077 | -0.51077 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | MTL | LODGING - MOTEL | Existing | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 3.145 | 0.020487 | 4.0975 | Fixture/1000 sf | 45.9013 | 144.2044 | 144.2044 | 0.0050935 | 0.016002 | 0.016002 | 0 | 0 | 0 | 52.7131 | 165.6043 | 165.6043 | 0.0067224 | 0.021119 | 0.021119 | -0.12675 | -0.39819 | -0.39819 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | MTL | LODGING - MOTEL | New | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 3.145 | 0.020487 | 4.0975 | Fixture/1000 sf | 45.9011 | 144.2035 | 144.2035 | 0.0050937 | 0.016002 | 0.016002 | 0 | 0 | 0 | 51.5285 | 161.8829 | 161.8829 | 0.0068112 | 0.021398 | 0.021398 | -0.16229 | -0.50984 | -0.50984 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | MTL | LODGING - MOTEL | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 3.145 | 0.020487 | 4.0975 | Fixture/1000 sf | 45.9011 | 144.2035 | 144.2035 | 0.0050934 | 0.016002 | 0.016002 | 0 | 0 | 0 | 51.5285 | 161.8829 | 161.8829 | 0.0066928 | 0.021026 | 0.021026 | -0.14392 | -0.45216 | -0.45216 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | MTL | LODGING - MOTEL | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 3.145 | 0.020487 | 4.0975 | Fixture/1000 sf | 45.9029 | 144.2094 | 144.2094 | 0.0050937 | 0.016002 | 0.016002 | 0 | 0 | 0 | 50.6401 | 159.0918 | 159.0918 | 0.0068409 | 0.021491 | 0.021491 | -0.19901 | -0.6252 | -0.6252 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | MTL | LODGING - MOTEL | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 3.145 | 0.020487 | 4.0975 | Fixture/1000 sf | 45.9028 | 144.209 | 144.209 | 0.0050938 | 0.016003 | 0.016003 | 0 | 0 | 0 | 50.0478 | 157.2311 | 157.2311 | 0.0066632 | 0.020933 | 0.020933 | -0.20049 | -0.62985 | -0.62985 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | MTL | LODGING - MOTEL | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 3.145 | 0.020487 | 4.0975 | Fixture/1000 sf | 45.9005 | 144.2017 | 144.2017 | 0.0050936 | 0.016002 | 0.016002 | 0 | 0 | 0 | 49.1594 | 154.44 | 154.44 | 0.006752 | 0.021212 | 0.021212 | -0.25231 | -0.79267 | -0.79267 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | MTL | LODGING - MOTEL | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 3.145 | 0.020487 | 4.0975 | Fixture/1000 sf | 45.9006 | 144.2021 | 144.2021 | 0.0050934 | 0.016002 | 0.016002 | 0 | 0 | 0 | 49.7517 | 156.3007 | 156.3007 | 0.0066928 | 0.021026 | 0.021026 | -0.19338 | -0.60753 | -0.60753 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | MTL | LODGING - MOTEL | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 3.145 | 0.020487 | 4.0975 | Fixture/1000 sf | 45.9003 | 144.2012 | 144.2012 | 0.0050937 | 0.016002 | 0.016002 | 0 | 0 | 0 | 48.5671 | 152.5793 | 152.5793 | 0.0068112 | 0.021398 | 0.021398 | -0.25912 | -0.81407 | -0.81407 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | MTL | LODGING - MOTEL | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 3.145 | 0.020487 | 4.0975 | Fixture/1000 sf | 45.9 | 144.2002 | 144.2002 | 0.0050936 | 0.016002 | 0.016002 | 0 | 0 | 0 | 55.3784 | 173.9776 | 173.9776 | 0.0067816 | 0.021305 | 0.021305 | -0.05982 | -0.18793 | -0.18793 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | MTL | LODGING - MOTEL | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 3.145 | 0.020487 | 4.0975 | Fixture/1000 sf | 45.9037 | 144.2119 | 144.2119 | 0.0050935 | 0.016002 | 0.016002 | 0 | 0 | 0 | 54.7861 | 172.1168 | 172.1168 | 0.0069593 | 0.021863 | 0.021863 | -0.093284 | -0.29306 | -0.29306 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | MTL | LODGING - MOTEL | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 3.145 | 0.020487 | 4.0975 | Fixture/1000 sf | 45.9019 | 144.2061 | 144.2061 | 0.0050937 | 0.016003 | 0.016003 | 0 | 0 | 0 | 44.125 | 138.6238 | 138.6238 | 0.0064263 | 0.020189 | 0.020189 | -0.3376 | -1.0606 | -1.0606 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | MTL | LODGING - MOTEL | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 3.145 | 0.020487 | 4.0975 | Fixture/1000 sf | 45.902 | 144.2064 | 144.2064 | 0.0050938 | 0.016003 | 0.016003 | 0 | 0 | 0 | 42.6443 | 133.972 | 133.972 | 0.0064559 | 0.020282 | 0.020282 | -0.40275 | -1.2653 | -1.2653 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | MTL | LODGING - MOTEL | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 3.3193 | 0.018087 | 3.6174 | Fixture/1000 sf | 44.8498 | 144.7605 | 144.7605 | 0.0049768 | 0.016064 | 0.016064 | 0 | 0 | 0 | 50.0569 | 161.5672 | 161.5672 | 0.0062499 | 0.020173 | 0.020173 | -0.14467 | -0.46696 | -0.46696 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | MTL | LODGING - MOTEL | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 3.3193 | 0.018087 | 3.6174 | Fixture/1000 sf | 44.8497 | 144.7601 | 144.7601 | 0.0049767 | 0.016063 | 0.016063 | 0 | 0 | 0 | 49.4782 | 159.6993 | 159.6993 | 0.0063945 | 0.02064 | 0.02064 | -0.19704 | -0.636 | -0.636 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | MTL | LODGING - MOTEL | Existing | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 3.3193 | 0.018087 | 3.6174 | Fixture/1000 sf | 44.8481 | 144.7551 | 144.7551 | 0.0049768 | 0.016063 | 0.016063 | 0 | 0 | 0 | 51.5036 | 166.2367 | 166.2367 | 0.0062209 | 0.020079 | 0.020079 | -0.1059 | -0.34181 | -0.34181 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | MTL | LODGING - MOTEL | New | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 3.3193 | 0.018087 | 3.6174 | Fixture/1000 sf | 44.8479 | 144.7542 | 144.7542 | 0.0049768 | 0.016064 | 0.016064 | 0 | 0 | 0 | 50.3462 | 162.5011 | 162.5011 | 0.0062499 | 0.020173 | 0.020173 | -0.14149 | -0.45668 | -0.45668 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | MTL | LODGING - MOTEL | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 3.3193 | 0.018087 | 3.6174 | Fixture/1000 sf | 44.848 | 144.7547 | 144.7547 | 0.0049766 | 0.016063 | 0.016063 | 0 | 0 | 0 | 50.9249 | 164.3689 | 164.3689 | 0.0063367 | 0.020453 | 0.020453 | -0.12181 | -0.39318 | -0.39318 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | MTL | LODGING - MOTEL | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 3.3193 | 0.018087 | 3.6174 | Fixture/1000 sf | 44.8499 | 144.7609 | 144.7609 | 0.0049769 | 0.016064 | 0.016064 | 0 | 0 | 0 | 50.6356 | 163.435 | 163.435 | 0.0065103 | 0.021013 | 0.021013 | -0.1629 | -0.52579 | -0.52579 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | MTL | LODGING - MOTEL | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 3.3193 | 0.018087 | 3.6174 | Fixture/1000 sf | 44.8479 | 144.7542 | 144.7542 | 0.0049769 | 0.016064 | 0.016064 | 0 | 0 | 0 | 50.3462 | 162.5011 | 162.5011 | 0.0065103 | 0.021013 | 0.021013 | -0.14294 | -0.46135 | -0.46135 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | MTL | LODGING - MOTEL | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 3.3193 | 0.018087 | 3.6174 | Fixture/1000 sf | 44.8497 | 144.7601 | 144.7601 | 0.0049767 | 0.016063 | 0.016063 | 0 | 0 | 0 | 49.4782 | 159.6993 | 159.6993 | 0.006626 | 0.021387 | 0.021387 | -0.20023 | -0.64627 | -0.64627 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | MTL | LODGING - MOTEL | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 3.3193 | 0.018087 | 3.6174 | Fixture/1000 sf | 44.8475 | 144.7528 | 144.7528 | 0.0049769 | 0.016064 | 0.016064 | 0 | 0 | 0 | 48.6102 | 156.8976 | 156.8976 | 0.0065103 | 0.021013 | 0.021013 | -0.19618 | -0.63319 | -0.63319 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | MTL | LODGING - MOTEL | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 3.3193 | 0.018087 | 3.6174 | Fixture/1000 sf | 44.8492 | 144.7585 | 144.7585 | 0.0049767 | 0.016063 | 0.016063 | 0 | 0 | 0 | 47.1634 | 152.228 | 152.228 | 0.006626 | 0.021387 | 0.021387 | -0.26099 | -0.84239 | -0.84239 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | MTL | LODGING - MOTEL | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 3.3193 | 0.018087 | 3.6174 | Fixture/1000 sf | 44.8487 | 144.7567 | 144.7567 | 0.0049767 | 0.016063 | 0.016063 | 0 | 0 | 0 | 53.8184 | 173.7081 | 173.7081 | 0.006626 | 0.021387 | 0.021387 | -0.060184 | -0.19425 | -0.19425 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | MTL | LODGING - MOTEL | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 3.3193 | 0.018087 | 3.6174 | Fixture/1000 sf | 44.8505 | 144.7626 | 144.7626 | 0.0049766 | 0.016063 | 0.016063 | 0 | 0 | 0 | 53.529 | 172.7741 | 172.7741 | 0.0067418 | 0.02176 | 0.02176 | -0.093748 | -0.30259 | -0.30259 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | NRS | HEALTH/MEDICAL - NURSING HOME | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 3.2792 | 0.017532 | 3.5064 | Fixture/1000 sf | 123.1974 | 387.0391 | 387.0391 | 0.020019 | 0.062891 | 0.062891 | 0 | 0 | 0 | 124.9715 | 392.6125 | 392.6125 | 0.024787 | 0.077871 | 0.077871 | -1.9456 | -6.1125 | -6.1125 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | NRS | HEALTH/MEDICAL - NURSING HOME | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 3.2792 | 0.017532 | 3.5064 | Fixture/1000 sf | 123.1951 | 387.0318 | 387.0318 | 0.020019 | 0.062893 | 0.062893 | 0 | 0 | 0 | 119.6409 | 375.866 | 375.866 | 0.024432 | 0.076755 | 0.076755 | -2.2151 | -6.9591 | -6.9591 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | NRS | HEALTH/MEDICAL - NURSING HOME | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 3.2792 | 0.017532 | 3.5064 | Fixture/1000 sf | 123.1986 | 387.0427 | 387.0427 | 0.02002 | 0.062894 | 0.062894 | 0 | 0 | 0 | 133.5596 | 419.593 | 419.593 | 0.02612 | 0.082058 | 0.082058 | -1.2912 | -4.0564 | -4.0564 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | NRS | HEALTH/MEDICAL - NURSING HOME | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 3.2792 | 0.017532 | 3.5064 | Fixture/1000 sf | 123.1887 | 387.0115 | 387.0115 | 0.020019 | 0.062891 | 0.062891 | 0 | 0 | 0 | 127.0445 | 399.125 | 399.125 | 0.025646 | 0.080569 | 0.080569 | -1.4156 | -4.4471 | -4.4471 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | NRS | HEALTH/MEDICAL - NURSING HOME | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 3.2792 | 0.017532 | 3.5064 | Fixture/1000 sf | 123.189 | 387.0126 | 387.0126 | 0.020019 | 0.062892 | 0.062892 | 0 | 0 | 0 | 134.7441 | 423.3144 | 423.3144 | 0.026031 | 0.081779 | 0.081779 | -1.2556 | -3.9447 | -3.9447 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | NRS | HEALTH/MEDICAL - NURSING HOME | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 3.2792 | 0.017532 | 3.5064 | Fixture/1000 sf | 123.1928 | 387.0247 | 387.0247 | 0.020019 | 0.062891 | 0.062891 | 0 | 0 | 0 | 129.7097 | 407.4983 | 407.4983 | 0.025794 | 0.081034 | 0.081034 | -1.3297 | -4.1773 | -4.1773 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | NRS | HEALTH/MEDICAL - NURSING HOME | Existing | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 3.2792 | 0.017532 | 3.5064 | Fixture/1000 sf | 123.1899 | 387.0154 | 387.0154 | 0.02002 | 0.062894 | 0.062894 | 0 | 0 | 0 | 135.3364 | 425.1751 | 425.1751 | 0.026978 | 0.084756 | 0.084756 | -1.2793 | -4.0192 | -4.0192 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | NRS | HEALTH/MEDICAL - NURSING HOME | New | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 3.2792 | 0.017532 | 3.5064 | Fixture/1000 sf | 123.1942 | 387.0289 | 387.0289 | 0.020019 | 0.062891 | 0.062891 | 0 | 0 | 0 | 130.5982 | 410.2893 | 410.2893 | 0.026771 | 0.084105 | 0.084105 | -1.3534 | -4.2518 | -4.2518 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | NRS | HEALTH/MEDICAL - NURSING HOME | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 3.2792 | 0.017532 | 3.5064 | Fixture/1000 sf | 123.1986 | 387.0427 | 387.0427 | 0.02002 | 0.062894 | 0.062894 | 0 | 0 | 0 | 133.5596 | 419.593 | 419.593 | 0.026978 | 0.084756 | 0.084756 | -1.2793 | -4.0192 | -4.0192 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | NRS | HEALTH/MEDICAL - NURSING HOME | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 3.2792 | 0.017532 | 3.5064 | Fixture/1000 sf | 123.1951 | 387.0317 | 387.0317 | 0.020019 | 0.062893 | 0.062893 | 0 | 0 | 0 | 131.1904 | 412.1501 | 412.1501 | 0.02686 | 0.084384 | 0.084384 | -1.2556 | -3.9447 | -3.9447 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | NRS | HEALTH/MEDICAL - NURSING HOME | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 3.2792 | 0.017532 | 3.5064 | Fixture/1000 sf | 123.1964 | 387.0359 | 387.0359 | 0.020019 | 0.062892 | 0.062892 | 0 | 0 | 0 | 132.0789 | 414.9412 | 414.9412 | 0.026623 | 0.083639 | 0.083639 | -1.4896 | -4.6797 | -4.6797 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | NRS | HEALTH/MEDICAL - NURSING HOME | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 3.2792 | 0.017532 | 3.5064 | Fixture/1000 sf | 123.1933 | 387.0261 | 387.0261 | 0.020019 | 0.062893 | 0.062893 | 0 | 0 | 0 | 130.0059 | 408.4286 | 408.4286 | 0.026593 | 0.083546 | 0.083546 | -1.611 | -5.0612 | -5.0612 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | NRS | HEALTH/MEDICAL - NURSING HOME | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 3.2792 | 0.017532 | 3.5064 | Fixture/1000 sf | 123.1973 | 387.0386 | 387.0386 | 0.02002 | 0.062895 | 0.062895 | 0 | 0 | 0 | 132.6711 | 416.8019 | 416.8019 | 0.026534 | 0.08336 | 0.08336 | -1.5251 | -4.7914 | -4.7914 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | NRS | HEALTH/MEDICAL - NURSING HOME | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 3.2792 | 0.017532 | 3.5064 | Fixture/1000 sf | 123.1933 | 387.0261 | 387.0261 | 0.020019 | 0.062892 | 0.062892 | 0 | 0 | 0 | 130.0059 | 408.4286 | 408.4286 | 0.026031 | 0.081779 | 0.081779 | -1.6614 | -5.2193 | -5.2193 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | NRS | HEALTH/MEDICAL - NURSING HOME | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 3.2792 | 0.017532 | 3.5064 | Fixture/1000 sf | 123.1901 | 387.0162 | 387.0162 | 0.020019 | 0.062893 | 0.062893 | 0 | 0 | 0 | 143.0361 | 449.3645 | 449.3645 | 0.027156 | 0.085314 | 0.085314 | -0.77293 | -2.4282 | -2.4282 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | NRS | HEALTH/MEDICAL - NURSING HOME | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 3.2367 | 0.016208 | 3.2415 | Fixture/1000 sf | 120.3702 | 388.5153 | 388.5153 | 0.019559 | 0.063131 | 0.063131 | 0 | 0 | 0 | 129.3377 | 417.4597 | 417.4597 | 0.025462 | 0.082184 | 0.082184 | -1.2384 | -3.9972 | -3.9972 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | NRS | HEALTH/MEDICAL - NURSING HOME | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 3.2367 | 0.016208 | 3.2415 | Fixture/1000 sf | 120.3626 | 388.491 | 388.491 | 0.01956 | 0.063132 | 0.063132 | 0 | 0 | 0 | 124.4188 | 401.5832 | 401.5832 | 0.025028 | 0.080784 | 0.080784 | -1.3946 | -4.5015 | -4.5015 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | NRS | HEALTH/MEDICAL - NURSING HOME | Existing | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 3.2367 | 0.016208 | 3.2415 | Fixture/1000 sf | 120.3693 | 388.5125 | 388.5125 | 0.01956 | 0.063135 | 0.063135 | 0 | 0 | 0 | 128.759 | 415.5919 | 415.5919 | 0.025086 | 0.08097 | 0.08097 | -1.1313 | -3.6516 | -3.6516 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RFF | RESTAURANT - FAST-FOOD | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 2.2762 | 0.013042 | 2.6084 | Fixture/1000 sf | 143.3296 | 450.2866 | 450.2866 | 0.024076 | 0.075639 | 0.075639 | 0 | 0 | 0 | 153.9933 | 483.7879 | 483.7879 | 0.02991 | 0.093966 | 0.093966 | -1.1609 | -3.647 | -3.647 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RFF | RESTAURANT - FAST-FOOD | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 2.2762 | 0.013042 | 2.6084 | Fixture/1000 sf | 143.333 | 450.2972 | 450.2972 | 0.024076 | 0.075639 | 0.075639 | 0 | 0 | 0 | 158.1393 | 496.8129 | 496.8129 | 0.031687 | 0.099549 | 0.099549 | -1.3386 | -4.2052 | -4.2052 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RFF | RESTAURANT - FAST-FOOD | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 2.2762 | 0.013042 | 2.6084 | Fixture/1000 sf | 143.3271 | 450.2788 | 450.2788 | 0.024076 | 0.075639 | 0.075639 | 0 | 0 | 0 | 165.5428 | 520.072 | 520.072 | 0.029614 | 0.093036 | 0.093036 | -0.37906 | -1.1909 | -1.1909 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RFF | RESTAURANT - FAST-FOOD | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 2.2762 | 0.013042 | 2.6084 | Fixture/1000 sf | 143.3342 | 450.3011 | 450.3011 | 0.024076 | 0.075639 | 0.075639 | 0 | 0 | 0 | 170.281 | 534.9578 | 534.9578 | 0.032279 | 0.10141 | 0.10141 | -0.46494 | -1.4607 | -1.4607 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RFF | RESTAURANT - FAST-FOOD | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 2.2762 | 0.013042 | 2.6084 | Fixture/1000 sf | 143.3322 | 450.2949 | 450.2949 | 0.024077 | 0.07564 | 0.07564 | 0 | 0 | 0 | 143.3322 | 450.2949 | 450.2949 | 0.028844 | 0.090617 | 0.090617 | -2.1056 | -6.6149 | -6.6149 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RFF | RESTAURANT - FAST-FOOD | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 2.2762 | 0.013042 | 2.6084 | Fixture/1000 sf | 143.327 | 450.2784 | 450.2784 | 0.024076 | 0.075639 | 0.075639 | 0 | 0 | 0 | 145.4052 | 456.8074 | 456.8074 | 0.030206 | 0.094897 | 0.094897 | -2.2655 | -7.1173 | -7.1173 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RTL | RETAIL - SINGLE-STORY LARGE | New | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 3.0977 | 0.024297 | 4.8593 | Fixture/1000 sf | 133.123 | 366.468 | 366.468 | 0.026436 | 0.072775 | 0.072775 | 0 | 0 | 0 | 128.7579 | 354.4515 | 354.4515 | 0.030864 | 0.084965 | 0.084965 | -2.0358 | -5.6043 | -5.6043 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RTL | RETAIL - SINGLE-STORY LARGE | Existing | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 3.0977 | 0.024297 | 4.8593 | Fixture/1000 sf | 133.1222 | 366.4657 | 366.4657 | 0.026438 | 0.072781 | 0.072781 | 0 | 0 | 0 | 129.3814 | 356.168 | 356.168 | 0.031488 | 0.086682 | 0.086682 | -1.8768 | -5.1666 | -5.1666 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RTL | RETAIL - SINGLE-STORY LARGE | New | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 3.0977 | 0.024297 | 4.8593 | Fixture/1000 sf | 133.1201 | 366.46 | 366.46 | 0.026437 | 0.072778 | 0.072778 | 0 | 0 | 0 | 139.6696 | 384.4898 | 384.4898 | 0.033047 | 0.090973 | 0.090973 | -1.0569 | -2.9094 | -2.9094 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RTS | RETAIL - SMALL | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 2.89 | 0.019059 | 3.8119 | Fixture/1000 sf | 100.0964 | 314.4647 | 314.4647 | 0.025913 | 0.081409 | 0.081409 | 0 | 0 | 0 | 110.7567 | 347.9551 | 347.9551 | 0.031391 | 0.098618 | 0.098618 | -0.20078 | -0.63078 | -0.63078 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RTS | RETAIL - SMALL | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 2.89 | 0.019059 | 3.8119 | Fixture/1000 sf | 100.0931 | 314.454 | 314.454 | 0.025911 | 0.081404 | 0.081404 | 0 | 0 | 0 | 114.6065 | 360.0498 | 360.0498 | 0.031687 | 0.099549 | 0.099549 | -0.12882 | -0.40471 | -0.40471 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RTS | RETAIL - SMALL | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 2.89 | 0.019059 | 3.8119 | Fixture/1000 sf | 100.0995 | 314.4743 | 314.4743 | 0.025911 | 0.081404 | 0.081404 | 0 | 0 | 0 | 111.9413 | 351.6766 | 351.6766 | 0.031687 | 0.099549 | 0.099549 | -0.1688 | -0.53031 | -0.53031 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | SCN | STORAGE - CONDITIONED | New | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 1.3677 | 0.0091489 | 1.8298 | Fixture/1000 sf | 98.956 | 319.3974 | 319.3974 | 0.020255 | 0.065376 | 0.065376 | 0 | 0 | 0 | 98.667 | 318.4648 | 318.4648 | 0.024942 | 0.080503 | 0.080503 | -0.48899 | -1.5783 | -1.5783 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | SCN | STORAGE - CONDITIONED | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 1.3677 | 0.0091489 | 1.8298 | Fixture/1000 sf | 98.9598 | 319.4096 | 319.4096 | 0.020254 | 0.065375 | 0.065375 | 0 | 0 | 0 | 103.0072 | 332.4735 | 332.4735 | 0.026244 | 0.084706 | 0.084706 | -0.46874 | -1.5129 | -1.5129 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | SCN | STORAGE - CONDITIONED | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 1.3677 | 0.0091489 | 1.8298 | Fixture/1000 sf | 98.9556 | 319.3961 | 319.3961 | 0.020255 | 0.065376 | 0.065376 | 0 | 0 | 0 | 101.2712 | 326.87 | 326.87 | 0.024739 | 0.07985 | 0.07985 | -0.51214 | -1.653 | -1.653 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | SUN | STORAGE - UNCONDITIONED | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 1.3677 | 0.0091489 | 1.8298 | Fixture/1000 sf | 98.9564 | 319.3987 | 319.3987 | 0.020254 | 0.065374 | 0.065374 | 0 | 0 | 0 | 98.9564 | 319.3987 | 319.3987 | 0.020254 | 0.065374 | 0.065374 | 0 | 0 | 0 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | SUN | STORAGE - UNCONDITIONED | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 1.3677 | 0.0091489 | 1.8298 | Fixture/1000 sf | 98.9564 | 319.3987 | 319.3987 | 0.020254 | 0.065374 | 0.065374 | 0 | 0 | 0 | 98.9564 | 319.3987 | 319.3987 | 0.020254 | 0.065374 | 0.065374 | 0 | 0 | 0 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | SUN | STORAGE - UNCONDITIONED | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 1.3677 | 0.0091489 | 1.8298 | Fixture/1000 sf | 98.9564 | 319.3987 | 319.3987 | 0.020254 | 0.065374 | 0.065374 | 0 | 0 | 0 | 98.9564 | 319.3987 | 319.3987 | 0.020254 | 0.065374 | 0.065374 | 0 | 0 | 0 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | SUN | STORAGE - UNCONDITIONED | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 1.3677 | 0.0091489 | 1.8298 | Fixture/1000 sf | 98.9564 | 319.3987 | 319.3987 | 0.020254 | 0.065374 | 0.065374 | 0 | 0 | 0 | 98.9564 | 319.3987 | 319.3987 | 0.020254 | 0.065374 | 0.065374 | 0 | 0 | 0 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | SUN | STORAGE - UNCONDITIONED | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 1.3677 | 0.0091489 | 1.8298 | Fixture/1000 sf | 98.9564 | 319.3987 | 319.3987 | 0.020254 | 0.065374 | 0.065374 | 0 | 0 | 0 | 98.9564 | 319.3987 | 319.3987 | 0.020254 | 0.065374 | 0.065374 | 0 | 0 | 0 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | SUN | STORAGE - UNCONDITIONED | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 1.3677 | 0.0091489 | 1.8298 | Fixture/1000 sf | 98.9564 | 319.3987 | 319.3987 | 0.020254 | 0.065374 | 0.065374 | 0 | 0 | 0 | 98.9564 | 319.3987 | 319.3987 | 0.020254 | 0.065374 | 0.065374 | 0 | 0 | 0 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | NRS | HEALTH/MEDICAL - NURSING HOME | New | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 3.2367 | 0.016208 | 3.2415 | Fixture/1000 sf | 120.3725 | 388.5229 | 388.5229 | 0.01956 | 0.063134 | 0.063134 | 0 | 0 | 0 | 123.2615 | 397.8475 | 397.8475 | 0.025115 | 0.081064 | 0.081064 | -1.3223 | -4.268 | -4.268 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | NRS | HEALTH/MEDICAL - NURSING HOME | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 3.2367 | 0.016208 | 3.2415 | Fixture/1000 sf | 120.3723 | 388.5221 | 388.5221 | 0.01956 | 0.063134 | 0.063134 | 0 | 0 | 0 | 130.7845 | 422.1293 | 422.1293 | 0.025376 | 0.081904 | 0.081904 | -1.2008 | -3.8757 | -3.8757 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | NRS | HEALTH/MEDICAL - NURSING HOME | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 3.2367 | 0.016208 | 3.2415 | Fixture/1000 sf | 120.3662 | 388.5027 | 388.5027 | 0.01956 | 0.063132 | 0.063132 | 0 | 0 | 0 | 126.7336 | 409.0545 | 409.0545 | 0.025173 | 0.081251 | 0.081251 | -1.3107 | -4.2306 | -4.2306 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | NRS | HEALTH/MEDICAL - NURSING HOME | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 3.2367 | 0.016208 | 3.2415 | Fixture/1000 sf | 120.3731 | 388.5248 | 388.5248 | 0.01956 | 0.063132 | 0.063132 | 0 | 0 | 0 | 131.3632 | 423.9971 | 423.9971 | 0.026417 | 0.085266 | 0.085266 | -1.276 | -4.1186 | -4.1186 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | NRS | HEALTH/MEDICAL - NURSING HOME | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 3.2367 | 0.016208 | 3.2415 | Fixture/1000 sf | 120.3684 | 388.5098 | 388.5098 | 0.01956 | 0.063133 | 0.063133 | 0 | 0 | 0 | 128.1803 | 413.724 | 413.724 | 0.026244 | 0.084706 | 0.084706 | -1.2384 | -3.9972 | -3.9972 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | NRS | HEALTH/MEDICAL - NURSING HOME | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 3.2367 | 0.016208 | 3.2415 | Fixture/1000 sf | 120.3706 | 388.5167 | 388.5167 | 0.01956 | 0.063135 | 0.063135 | 0 | 0 | 0 | 129.6271 | 418.3936 | 418.3936 | 0.025925 | 0.083679 | 0.083679 | -1.4901 | -4.8097 | -4.8097 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | NRS | HEALTH/MEDICAL - NURSING HOME | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 3.2367 | 0.016208 | 3.2415 | Fixture/1000 sf | 120.3667 | 388.5041 | 388.5041 | 0.01956 | 0.063134 | 0.063134 | 0 | 0 | 0 | 127.023 | 409.9884 | 409.9884 | 0.025376 | 0.081904 | 0.081904 | -1.6348 | -5.2766 | -5.2766 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | NRS | HEALTH/MEDICAL - NURSING HOME | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 3.2367 | 0.016208 | 3.2415 | Fixture/1000 sf | 120.4711 | 388.841 | 388.841 | 0.019554 | 0.063113 | 0.063113 | 0 | 0 | 0 | 129.3377 | 417.4597 | 417.4597 | 0.025289 | 0.081624 | 0.081624 | -1.1574 | -3.7357 | -3.7357 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | NRS | HEALTH/MEDICAL - NURSING HOME | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 3.2367 | 0.016208 | 3.2415 | Fixture/1000 sf | 120.3716 | 388.5201 | 388.5201 | 0.019559 | 0.063131 | 0.063131 | 0 | 0 | 0 | 138.0181 | 445.4771 | 445.4771 | 0.026041 | 0.084052 | 0.084052 | -0.75519 | -2.4375 | -2.4375 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | OFL | OFFICE - LARGE | Existing | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 3.1486 | 0.018018 | 3.6035 | Fixture/1000 sf | 82.302 | 226.5654 | 226.5654 | 0.022136 | 0.060937 | 0.060937 | 0 | 0 | 0 | 88.5405 | 243.7391 | 243.7391 | 0.027435 | 0.075525 | 0.075525 | -0.77005 | -2.1198 | -2.1198 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | OFL | OFFICE - LARGE | New | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 3.1486 | 0.018018 | 3.6035 | Fixture/1000 sf | 82.302 | 226.5654 | 226.5654 | 0.022136 | 0.060936 | 0.060936 | 0 | 0 | 0 | 88.5405 | 243.7391 | 243.7391 | 0.026656 | 0.073379 | 0.073379 | -0.38035 | -1.047 | -1.047 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | OFL | OFFICE - LARGE | Existing | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 3.1486 | 0.018018 | 3.6035 | Fixture/1000 sf | 82.3089 | 226.5842 | 226.5842 | 0.022135 | 0.060935 | 0.060935 | 0 | 0 | 0 | 91.3464 | 251.4632 | 251.4632 | 0.029181 | 0.080331 | 0.080331 | -0.56429 | -1.5534 | -1.5534 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | OFL | OFFICE - LARGE | New | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 3.1486 | 0.018018 | 3.6035 | Fixture/1000 sf | 82.3062 | 226.5768 | 226.5768 | 0.022135 | 0.060935 | 0.060935 | 0 | 0 | 0 | 92.2817 | 254.0379 | 254.0379 | 0.027653 | 0.076126 | 0.076126 | -0.27497 | -0.75696 | -0.75696 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | OFL | OFFICE - LARGE | Existing | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 3.1486 | 0.018018 | 3.6035 | Fixture/1000 sf | 82.3024 | 226.5663 | 226.5663 | 0.022135 | 0.060933 | 0.060933 | 0 | 0 | 0 | 91.0346 | 250.605 | 250.605 | 0.028277 | 0.077842 | 0.077842 | -0.52376 | -1.4418 | -1.4418 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | OFL | OFFICE - LARGE | New | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 3.1486 | 0.018018 | 3.6035 | Fixture/1000 sf | 82.308 | 226.5817 | 226.5817 | 0.022135 | 0.060934 | 0.060934 | 0 | 0 | 0 | 91.6582 | 252.3214 | 252.3214 | 0.027217 | 0.074924 | 0.074924 | -0.24536 | -0.67543 | -0.67543 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | OFL | OFFICE - LARGE | Existing | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 3.1486 | 0.018018 | 3.6035 | Fixture/1000 sf | 82.3062 | 226.5768 | 226.5768 | 0.022135 | 0.060934 | 0.060934 | 0 | 0 | 0 | 92.2817 | 254.0379 | 254.0379 | 0.029119 | 0.080159 | 0.080159 | -0.47388 | -1.3045 | -1.3045 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | OFL | OFFICE - LARGE | New | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 3.1486 | 0.018018 | 3.6035 | Fixture/1000 sf | 82.3035 | 226.5695 | 226.5695 | 0.022135 | 0.060934 | 0.060934 | 0 | 0 | 0 | 93.217 | 256.6126 | 256.6126 | 0.027591 | 0.075954 | 0.075954 | -0.22821 | -0.62823 | -0.62823 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | OFL | OFFICE - LARGE | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 3.1486 | 0.018018 | 3.6035 | Fixture/1000 sf | 82.3033 | 226.5687 | 226.5687 | 0.022136 | 0.060937 | 0.060937 | 0 | 0 | 0 | 90.7229 | 249.7467 | 249.7467 | 0.027809 | 0.076555 | 0.076555 | -0.50817 | -1.3989 | -1.3989 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | OFL | OFFICE - LARGE | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 3.1486 | 0.018018 | 3.6035 | Fixture/1000 sf | 82.3089 | 226.5842 | 226.5842 | 0.022135 | 0.060934 | 0.060934 | 0 | 0 | 0 | 91.3464 | 251.4632 | 251.4632 | 0.026905 | 0.074066 | 0.074066 | -0.25128 | -0.69174 | -0.69174 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | OFL | OFFICE - LARGE | Existing | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 3.1486 | 0.018018 | 3.6035 | Fixture/1000 sf | 82.3035 | 226.5695 | 226.5695 | 0.022135 | 0.060934 | 0.060934 | 0 | 0 | 0 | 93.217 | 256.6126 | 256.6126 | 0.02943 | 0.081017 | 0.081017 | -0.53935 | -1.4847 | -1.4847 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | OFL | OFFICE - LARGE | New | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 3.1486 | 0.018018 | 3.6035 | Fixture/1000 sf | 82.3018 | 226.5647 | 226.5647 | 0.022135 | 0.060935 | 0.060935 | 0 | 0 | 0 | 93.8405 | 258.3291 | 258.3291 | 0.028059 | 0.077241 | 0.077241 | -0.22322 | -0.6145 | -0.6145 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | OFL | OFFICE - LARGE | Existing | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 3.1486 | 0.018018 | 3.6035 | Fixture/1000 sf | 82.3062 | 226.5768 | 226.5768 | 0.022134 | 0.060932 | 0.060932 | 0 | 0 | 0 | 92.2817 | 254.0379 | 254.0379 | 0.028963 | 0.07973 | 0.07973 | -0.52376 | -1.4418 | -1.4418 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | OFL | OFFICE - LARGE | New | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 3.1486 | 0.018018 | 3.6035 | Fixture/1000 sf | 82.3044 | 226.5719 | 226.5719 | 0.022136 | 0.060937 | 0.060937 | 0 | 0 | 0 | 92.9052 | 255.7544 | 255.7544 | 0.02784 | 0.07664 | 0.07664 | -0.26188 | -0.72092 | -0.72092 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | OFL | OFFICE - LARGE | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 3.1486 | 0.018018 | 3.6035 | Fixture/1000 sf | 82.3081 | 226.5822 | 226.5822 | 0.022135 | 0.060933 | 0.060933 | 0 | 0 | 0 | 94.1523 | 259.1873 | 259.1873 | 0.029399 | 0.080932 | 0.080932 | -0.48947 | -1.3474 | -1.3474 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | OFL | OFFICE - LARGE | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 3.1486 | 0.018018 | 3.6035 | Fixture/1000 sf | 82.3018 | 226.5647 | 226.5647 | 0.022136 | 0.060937 | 0.060937 | 0 | 0 | 0 | 93.8405 | 258.3291 | 258.3291 | 0.02784 | 0.07664 | 0.07664 | -0.24536 | -0.67543 | -0.67543 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | OFL | OFFICE - LARGE | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 4.2972 | 0.025741 | 5.1481 | Fixture/1000 sf | 78.1812 | 245.6154 | 245.6154 | 0.021026 | 0.066055 | 0.066055 | 0 | 0 | 0 | 87.9539 | 276.3173 | 276.3173 | 0.026208 | 0.082337 | 0.082337 | -0.24313 | -0.76383 | -0.76383 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | OFL | OFFICE - LARGE | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 4.2972 | 0.025741 | 5.1481 | Fixture/1000 sf | 78.1814 | 245.616 | 245.616 | 0.021026 | 0.066055 | 0.066055 | 0 | 0 | 0 | 90.323 | 283.7602 | 283.7602 | 0.027275 | 0.085686 | 0.085686 | -0.23395 | -0.73499 | -0.73499 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | OFL | OFFICE - LARGE | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 4.2972 | 0.025741 | 5.1481 | Fixture/1000 sf | 78.1814 | 245.616 | 245.616 | 0.021026 | 0.066057 | 0.066057 | 0 | 0 | 0 | 90.323 | 283.7602 | 283.7602 | 0.028104 | 0.088291 | 0.088291 | -0.43237 | -1.3583 | -1.3583 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | OFL | OFFICE - LARGE | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 4.2972 | 0.025741 | 5.1481 | Fixture/1000 sf | 78.1798 | 245.6109 | 245.6109 | 0.021025 | 0.066053 | 0.066053 | 0 | 0 | 0 | 90.9153 | 285.6209 | 285.6209 | 0.027867 | 0.087547 | 0.087547 | -0.17917 | -0.56287 | -0.56287 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | OFL | OFFICE - LARGE | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 4.2972 | 0.025741 | 5.1481 | Fixture/1000 sf | 78.1795 | 245.6099 | 245.6099 | 0.021026 | 0.066055 | 0.066055 | 0 | 0 | 0 | 95.9497 | 301.4371 | 301.4371 | 0.028015 | 0.088012 | 0.088012 | -0.2073 | -0.65125 | -0.65125 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | OFL | OFFICE - LARGE | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 4.2972 | 0.025741 | 5.1481 | Fixture/1000 sf | 78.1802 | 245.6123 | 245.6123 | 0.021026 | 0.066057 | 0.066057 | 0 | 0 | 0 | 95.6535 | 300.5067 | 300.5067 | 0.027748 | 0.087175 | 0.087175 | -0.082031 | -0.25771 | -0.25771 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | OFL | OFFICE - LARGE | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 4.2972 | 0.025741 | 5.1481 | Fixture/1000 sf | 78.1781 | 245.6057 | 245.6057 | 0.021027 | 0.066058 | 0.066058 | 0 | 0 | 0 | 84.104 | 264.2226 | 264.2226 | 0.026771 | 0.084105 | 0.084105 | -0.7907 | -2.4841 | -2.4841 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | OFL | OFFICE - LARGE | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 4.2972 | 0.025741 | 5.1481 | Fixture/1000 sf | 78.1819 | 245.6174 | 245.6174 | 0.021026 | 0.066054 | 0.066054 | 0 | 0 | 0 | 85.2886 | 267.9441 | 267.9441 | 0.026534 | 0.08336 | 0.08336 | -0.53602 | -1.684 | -1.684 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | OFL | OFFICE - LARGE | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 3.8235 | 0.020086 | 4.0172 | Fixture/1000 sf | 76.386 | 246.5489 | 246.5489 | 0.020544 | 0.06631 | 0.06631 | 0 | 0 | 0 | 88.8293 | 286.7117 | 286.7117 | 0.026128 | 0.084332 | 0.084332 | -0.17419 | -0.56222 | -0.56222 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | OFL | OFFICE - LARGE | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 3.8235 | 0.020086 | 4.0172 | Fixture/1000 sf | 76.386 | 246.5489 | 246.5489 | 0.020543 | 0.066306 | 0.066306 | 0 | 0 | 0 | 88.8293 | 286.7117 | 286.7117 | 0.025868 | 0.083492 | 0.083492 | -0.10243 | -0.33061 | -0.33061 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | OFL | OFFICE - LARGE | Existing | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 3.8235 | 0.020086 | 4.0172 | Fixture/1000 sf | 76.3868 | 246.5514 | 246.5514 | 0.020543 | 0.066306 | 0.066306 | 0 | 0 | 0 | 88.5399 | 285.7778 | 285.7778 | 0.025868 | 0.083492 | 0.083492 | -0.15422 | -0.49778 | -0.49778 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | OFL | OFFICE - LARGE | New | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 3.8235 | 0.020086 | 4.0172 | Fixture/1000 sf | 76.3868 | 246.5514 | 246.5514 | 0.020544 | 0.06631 | 0.06631 | 0 | 0 | 0 | 88.5399 | 285.7778 | 285.7778 | 0.025462 | 0.082184 | 0.082184 | -0.0706 | -0.22788 | -0.22788 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | OFL | OFFICE - LARGE | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 3.8235 | 0.020086 | 4.0172 | Fixture/1000 sf | 76.3852 | 246.5463 | 246.5463 | 0.020544 | 0.066308 | 0.066308 | 0 | 0 | 0 | 89.1186 | 287.6456 | 287.6456 | 0.026388 | 0.085173 | 0.085173 | -0.17361 | -0.56035 | -0.56035 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | OFL | OFFICE - LARGE | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 3.8235 | 0.020086 | 4.0172 | Fixture/1000 sf | 76.3852 | 246.5463 | 246.5463 | 0.020544 | 0.06631 | 0.06631 | 0 | 0 | 0 | 89.1186 | 287.6456 | 287.6456 | 0.026186 | 0.084519 | 0.084519 | -0.090855 | -0.29325 | -0.29325 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | OFL | OFFICE - LARGE | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 3.8235 | 0.020086 | 4.0172 | Fixture/1000 sf | 76.386 | 246.5489 | 246.5489 | 0.020544 | 0.066309 | 0.066309 | 0 | 0 | 0 | 88.8293 | 286.7117 | 286.7117 | 0.026765 | 0.086387 | 0.086387 | -0.20399 | -0.65841 | -0.65841 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | OFL | OFFICE - LARGE | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 3.8235 | 0.020086 | 4.0172 | Fixture/1000 sf | 76.3901 | 246.5623 | 246.5623 | 0.020543 | 0.066307 | 0.066307 | 0 | 0 | 0 | 89.6973 | 289.5134 | 289.5134 | 0.026967 | 0.087041 | 0.087041 | -0.10098 | -0.32594 | -0.32594 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | OFL | OFFICE - LARGE | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 3.8235 | 0.020086 | 4.0172 | Fixture/1000 sf | 76.3892 | 246.5592 | 246.5592 | 0.020543 | 0.066307 | 0.066307 | 0 | 0 | 0 | 87.6719 | 282.976 | 282.976 | 0.02662 | 0.08592 | 0.08592 | -0.2552 | -0.82371 | -0.82371 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | OFL | OFFICE - LARGE | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 3.8235 | 0.020086 | 4.0172 | Fixture/1000 sf | 76.3868 | 246.5514 | 246.5514 | 0.020544 | 0.06631 | 0.06631 | 0 | 0 | 0 | 88.5399 | 285.7778 | 285.7778 | 0.02717 | 0.087695 | 0.087695 | -0.14757 | -0.4763 | -0.4763 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | OFL | OFFICE - LARGE | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 3.8235 | 0.020086 | 4.0172 | Fixture/1000 sf | 76.3872 | 246.5528 | 246.5528 | 0.020543 | 0.066306 | 0.066306 | 0 | 0 | 0 | 93.1695 | 300.7204 | 300.7204 | 0.026909 | 0.086854 | 0.086854 | -0.11834 | -0.38197 | -0.38197 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | OFL | OFFICE - LARGE | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 3.8235 | 0.020086 | 4.0172 | Fixture/1000 sf | 76.3864 | 246.5503 | 246.5503 | 0.020543 | 0.066307 | 0.066307 | 0 | 0 | 0 | 93.4588 | 301.6543 | 301.6543 | 0.026996 | 0.087134 | 0.087134 | -0.052082 | -0.1681 | -0.1681 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | OFS | OFFICE - SMALL | Existing | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 3.1486 | 0.018018 | 3.6035 | Fixture/1000 sf | 80.7482 | 222.288 | 222.288 | 0.021636 | 0.059561 | 0.059561 | 0 | 0 | 0 | 81.37 | 223.9996 | 223.9996 | 0.02544 | 0.070032 | 0.070032 | -0.52064 | -1.4333 | -1.4333 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | OFS | OFFICE - SMALL | New | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 3.1486 | 0.018018 | 3.6035 | Fixture/1000 sf | 80.7463 | 222.2827 | 222.2827 | 0.021637 | 0.059564 | 0.059564 | 0 | 0 | 0 | 80.123 | 220.5667 | 220.5667 | 0.025253 | 0.069517 | 0.069517 | -0.43959 | -1.2101 | -1.2101 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | OFS | OFFICE - SMALL | Existing | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 3.1486 | 0.018018 | 3.6035 | Fixture/1000 sf | 80.743 | 222.2735 | 222.2735 | 0.021636 | 0.059561 | 0.059561 | 0 | 0 | 0 | 85.1112 | 234.2985 | 234.2985 | 0.026282 | 0.072349 | 0.072349 | -0.3367 | -0.9269 | -0.9269 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | OFS | OFFICE - SMALL | New | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 3.1486 | 0.018018 | 3.6035 | Fixture/1000 sf | 80.743 | 222.2735 | 222.2735 | 0.021636 | 0.059559 | 0.059559 | 0 | 0 | 0 | 85.1112 | 234.2985 | 234.2985 | 0.02625 | 0.072263 | 0.072263 | -0.23289 | -0.6411 | -0.6411 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | OFS | OFFICE - SMALL | Existing | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 3.1486 | 0.018018 | 3.6035 | Fixture/1000 sf | 80.743 | 222.2735 | 222.2735 | 0.021636 | 0.05956 | 0.05956 | 0 | 0 | 0 | 85.1112 | 234.2985 | 234.2985 | 0.026188 | 0.072092 | 0.072092 | -0.28869 | -0.79473 | -0.79473 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | OFS | OFFICE - SMALL | New | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 3.1486 | 0.018018 | 3.6035 | Fixture/1000 sf | 80.7473 | 222.2853 | 222.2853 | 0.021636 | 0.05956 | 0.05956 | 0 | 0 | 0 | 83.8641 | 230.8655 | 230.8655 | 0.026188 | 0.072092 | 0.072092 | -0.25876 | -0.71234 | -0.71234 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | OFS | OFFICE - SMALL | Existing | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 3.1486 | 0.018018 | 3.6035 | Fixture/1000 sf | 80.7434 | 222.2747 | 222.2747 | 0.021636 | 0.05956 | 0.05956 | 0 | 0 | 0 | 86.67 | 238.5897 | 238.5897 | 0.026406 | 0.072693 | 0.072693 | -0.22977 | -0.63252 | -0.63252 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | OFS | OFFICE - SMALL | New | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 3.1486 | 0.018018 | 3.6035 | Fixture/1000 sf | 80.7463 | 222.2828 | 222.2828 | 0.021636 | 0.059561 | 0.059561 | 0 | 0 | 0 | 86.3582 | 237.7314 | 237.7314 | 0.026656 | 0.073379 | 0.073379 | -0.18519 | -0.50979 | -0.50979 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | OFS | OFFICE - SMALL | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 3.1486 | 0.018018 | 3.6035 | Fixture/1000 sf | 80.7476 | 222.2863 | 222.2863 | 0.021637 | 0.059564 | 0.059564 | 0 | 0 | 0 | 85.4229 | 235.1567 | 235.1567 | 0.025783 | 0.070976 | 0.070976 | -0.23538 | -0.64797 | -0.64797 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | OFS | OFFICE - SMALL | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 3.1486 | 0.018018 | 3.6035 | Fixture/1000 sf | 80.7489 | 222.29 | 222.29 | 0.021637 | 0.059564 | 0.059564 | 0 | 0 | 0 | 84.4876 | 232.582 | 232.582 | 0.025783 | 0.070976 | 0.070976 | -0.19828 | -0.54584 | -0.54584 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | OFS | OFFICE - SMALL | Existing | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 3.1486 | 0.018018 | 3.6035 | Fixture/1000 sf | 80.7434 | 222.2747 | 222.2747 | 0.021636 | 0.05956 | 0.05956 | 0 | 0 | 0 | 86.67 | 238.5897 | 238.5897 | 0.026406 | 0.072693 | 0.072693 | -0.35541 | -0.97839 | -0.97839 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | OFS | OFFICE - SMALL | New | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 3.1486 | 0.018018 | 3.6035 | Fixture/1000 sf | 80.748 | 222.2873 | 222.2873 | 0.021636 | 0.059562 | 0.059562 | 0 | 0 | 0 | 86.9817 | 239.4479 | 239.4479 | 0.027123 | 0.074667 | 0.074667 | -0.26531 | -0.73036 | -0.73036 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | OFS | OFFICE - SMALL | Existing | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 3.1486 | 0.018018 | 3.6035 | Fixture/1000 sf | 80.7493 | 222.2909 | 222.2909 | 0.021636 | 0.059561 | 0.059561 | 0 | 0 | 0 | 86.0464 | 236.8732 | 236.8732 | 0.026344 | 0.072521 | 0.072521 | -0.34606 | -0.95264 | -0.95264 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | OFS | OFFICE - SMALL | New | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 3.1486 | 0.018018 | 3.6035 | Fixture/1000 sf | 80.7463 | 222.2828 | 222.2828 | 0.021637 | 0.059563 | 0.059563 | 0 | 0 | 0 | 86.3582 | 237.7314 | 237.7314 | 0.026843 | 0.073894 | 0.073894 | -0.25627 | -0.70547 | -0.70547 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | OFS | OFFICE - SMALL | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 3.1486 | 0.018018 | 3.6035 | Fixture/1000 sf | 80.748 | 222.2873 | 222.2873 | 0.021636 | 0.059561 | 0.059561 | 0 | 0 | 0 | 86.9817 | 239.4479 | 239.4479 | 0.026126 | 0.07192 | 0.07192 | -0.32423 | -0.89257 | -0.89257 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | OFS | OFFICE - SMALL | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 3.1486 | 0.018018 | 3.6035 | Fixture/1000 sf | 80.7451 | 222.2793 | 222.2793 | 0.021637 | 0.059563 | 0.059563 | 0 | 0 | 0 | 87.2935 | 240.3061 | 240.3061 | 0.026843 | 0.073894 | 0.073894 | -0.24598 | -0.67715 | -0.67715 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | OFS | OFFICE - SMALL | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 3.1486 | 0.018018 | 3.6035 | Fixture/1000 sf | 80.7464 | 222.2829 | 222.2829 | 0.021637 | 0.059563 | 0.059563 | 0 | 0 | 0 | 80.4347 | 221.4249 | 221.4249 | 0.025845 | 0.071148 | 0.071148 | -0.64847 | -1.7851 | -1.7851 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | OFS | OFFICE - SMALL | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 3.1486 | 0.018018 | 3.6035 | Fixture/1000 sf | 80.7465 | 222.2832 | 222.2832 | 0.021636 | 0.05956 | 0.05956 | 0 | 0 | 0 | 80.7465 | 222.2832 | 222.2832 | 0.026032 | 0.071663 | 0.071663 | -0.57676 | -1.5877 | -1.5877 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | OFS | OFFICE - SMALL | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 4.2972 | 0.025741 | 5.1481 | Fixture/1000 sf | 76.6995 | 240.9605 | 240.9605 | 0.020553 | 0.064568 | 0.064568 | 0 | 0 | 0 | 84.4002 | 265.153 | 265.153 | 0.025705 | 0.080755 | 0.080755 | -0.23958 | -0.75266 | -0.75266 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | OFS | OFFICE - SMALL | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 4.2972 | 0.025741 | 5.1481 | Fixture/1000 sf | 76.7016 | 240.967 | 240.967 | 0.020552 | 0.064566 | 0.064566 | 0 | 0 | 0 | 81.1426 | 254.919 | 254.919 | 0.025379 | 0.079732 | 0.079732 | -0.19575 | -0.61497 | -0.61497 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | OFS | OFFICE - SMALL | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 4.2972 | 0.025741 | 5.1481 | Fixture/1000 sf | 76.6991 | 240.9592 | 240.9592 | 0.020552 | 0.064566 | 0.064566 | 0 | 0 | 0 | 88.25 | 277.2477 | 277.2477 | 0.026031 | 0.081779 | 0.081779 | -0.11668 | -0.36656 | -0.36656 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | OFS | OFFICE - SMALL | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 4.2972 | 0.025741 | 5.1481 | Fixture/1000 sf | 76.7026 | 240.9701 | 240.9701 | 0.020552 | 0.064567 | 0.064567 | 0 | 0 | 0 | 85.5847 | 268.8744 | 268.8744 | 0.025616 | 0.080476 | 0.080476 | -0.078477 | -0.24655 | -0.24655 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | OFS | OFFICE - SMALL | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 4.2972 | 0.025741 | 5.1481 | Fixture/1000 sf | 76.7006 | 240.9638 | 240.9638 | 0.020551 | 0.064565 | 0.064565 | 0 | 0 | 0 | 88.8423 | 279.1084 | 279.1084 | 0.026238 | 0.08243 | 0.08243 | -0.10839 | -0.34051 | -0.34051 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | OFS | OFFICE - SMALL | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 4.2972 | 0.025741 | 5.1481 | Fixture/1000 sf | 76.6972 | 240.9533 | 240.9533 | 0.020552 | 0.064566 | 0.064566 | 0 | 0 | 0 | 86.177 | 270.7351 | 270.7351 | 0.026031 | 0.081779 | 0.081779 | -0.070482 | -0.22143 | -0.22143 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | OFS | OFFICE - SMALL | Existing | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 4.2972 | 0.025741 | 5.1481 | Fixture/1000 sf | 76.6991 | 240.9592 | 240.9592 | 0.020553 | 0.064568 | 0.064568 | 0 | 0 | 0 | 88.25 | 277.2477 | 277.2477 | 0.026505 | 0.083267 | 0.083267 | -0.13149 | -0.41308 | -0.41308 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | OFS | OFFICE - SMALL | New | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 4.2972 | 0.025741 | 5.1481 | Fixture/1000 sf | 76.6972 | 240.9533 | 240.9533 | 0.020552 | 0.064566 | 0.064566 | 0 | 0 | 0 | 86.177 | 270.7351 | 270.7351 | 0.026682 | 0.083826 | 0.083826 | -0.077589 | -0.24375 | -0.24375 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | OFS | OFFICE - SMALL | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 4.2972 | 0.025741 | 5.1481 | Fixture/1000 sf | 76.6992 | 240.9595 | 240.9595 | 0.020552 | 0.064567 | 0.064567 | 0 | 0 | 0 | 77.5889 | 243.7547 | 243.7547 | 0.025616 | 0.080476 | 0.080476 | -0.5064 | -1.5909 | -1.5909 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | OFS | OFFICE - SMALL | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 3.8235 | 0.020086 | 4.0172 | Fixture/1000 sf | 74.9433 | 241.8922 | 241.8922 | 0.02008 | 0.064812 | 0.064812 | 0 | 0 | 0 | 86.5145 | 279.2404 | 279.2404 | 0.025144 | 0.081157 | 0.081157 | -0.058159 | -0.18772 | -0.18772 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | OFS | OFFICE - SMALL | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 3.8235 | 0.020086 | 4.0172 | Fixture/1000 sf | 74.9412 | 241.8856 | 241.8856 | 0.020081 | 0.064815 | 0.064815 | 0 | 0 | 0 | 83.0423 | 268.0334 | 268.0334 | 0.024768 | 0.079943 | 0.079943 | -0.059316 | -0.19145 | -0.19145 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | OFS | OFFICE - SMALL | Existing | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 3.8235 | 0.020086 | 4.0172 | Fixture/1000 sf | 74.9407 | 241.884 | 241.884 | 0.020081 | 0.064815 | 0.064815 | 0 | 0 | 0 | 86.8038 | 280.1743 | 280.1743 | 0.024913 | 0.08041 | 0.08041 | -0.01658 | -0.053513 | -0.053513 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | OFS | OFFICE - SMALL | New | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 3.8235 | 0.020086 | 4.0172 | Fixture/1000 sf | 74.9438 | 241.8941 | 241.8941 | 0.02008 | 0.064813 | 0.064813 | 0 | 0 | 0 | 82.753 | 267.0995 | 267.0995 | 0.02445 | 0.078916 | 0.078916 | -0.013599 | -0.043894 | -0.043894 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | OFS | OFFICE - SMALL | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 3.8235 | 0.020086 | 4.0172 | Fixture/1000 sf | 74.9382 | 241.8759 | 241.8759 | 0.02008 | 0.064812 | 0.064812 | 0 | 0 | 0 | 87.0932 | 281.1082 | 281.1082 | 0.025289 | 0.081624 | 0.081624 | -0.050057 | -0.16157 | -0.16157 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | OFS | OFFICE - SMALL | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 3.8235 | 0.020086 | 4.0172 | Fixture/1000 sf | 74.9427 | 241.8903 | 241.8903 | 0.020081 | 0.064815 | 0.064815 | 0 | 0 | 0 | 83.621 | 269.9012 | 269.9012 | 0.025115 | 0.081064 | 0.081064 | -0.051214 | -0.1653 | -0.1653 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | OFS | OFFICE - SMALL | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 3.8235 | 0.020086 | 4.0172 | Fixture/1000 sf | 74.9407 | 241.884 | 241.884 | 0.02008 | 0.064812 | 0.064812 | 0 | 0 | 0 | 86.8038 | 280.1743 | 280.1743 | 0.025434 | 0.082091 | 0.082091 | -0.075809 | -0.24469 | -0.24469 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | OFS | OFFICE - SMALL | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 3.8235 | 0.020086 | 4.0172 | Fixture/1000 sf | 74.9415 | 241.8866 | 241.8866 | 0.020081 | 0.064814 | 0.064814 | 0 | 0 | 0 | 84.4891 | 272.703 | 272.703 | 0.025954 | 0.083772 | 0.083772 | -0.040508 | -0.13075 | -0.13075 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | OFS | OFFICE - SMALL | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 3.8235 | 0.020086 | 4.0172 | Fixture/1000 sf | 74.9389 | 241.8783 | 241.8783 | 0.02008 | 0.064813 | 0.064813 | 0 | 0 | 0 | 84.7784 | 273.6369 | 273.6369 | 0.025723 | 0.083025 | 0.083025 | -0.18779 | -0.60611 | -0.60611 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | OFS | OFFICE - SMALL | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 3.8235 | 0.020086 | 4.0172 | Fixture/1000 sf | 74.9397 | 241.8808 | 241.8808 | 0.020081 | 0.064814 | 0.064814 | 0 | 0 | 0 | 82.4637 | 266.1656 | 266.1656 | 0.025954 | 0.083772 | 0.083772 | -0.15625 | -0.50431 | -0.50431 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | OFS | OFFICE - SMALL | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 3.8235 | 0.020086 | 4.0172 | Fixture/1000 sf | 74.9406 | 241.8837 | 241.8837 | 0.02008 | 0.064813 | 0.064813 | 0 | 0 | 0 | 92.0121 | 296.9848 | 296.9848 | 0.025376 | 0.081904 | 0.081904 | -0.015538 | -0.050151 | -0.050151 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | OFS | OFFICE - SMALL | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 3.8235 | 0.020086 | 4.0172 | Fixture/1000 sf | 74.9386 | 241.8771 | 241.8771 | 0.02008 | 0.064812 | 0.064812 | 0 | 0 | 0 | 88.5399 | 285.7778 | 285.7778 | 0.026273 | 0.084799 | 0.084799 | 0 | 0 | 0 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RFF | RESTAURANT - FAST-FOOD | New | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 3.5448 | 0.020224 | 4.0448 | Fixture/1000 sf | 150.8925 | 415.3848 | 415.3848 | 0.025346 | 0.069773 | 0.069773 | 0 | 0 | 0 | 141.5402 | 389.6392 | 389.6392 | 0.027716 | 0.076297 | 0.076297 | -2.1262 | -5.8532 | -5.8532 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RFF | RESTAURANT - FAST-FOOD | Existing | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 3.5448 | 0.020224 | 4.0448 | Fixture/1000 sf | 150.8934 | 415.3872 | 415.3872 | 0.025347 | 0.069777 | 0.069777 | 0 | 0 | 0 | 145.9048 | 401.6545 | 401.6545 | 0.029025 | 0.079902 | 0.079902 | -1.9922 | -5.4841 | -5.4841 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RFF | RESTAURANT - FAST-FOOD | Existing | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 3.5448 | 0.020224 | 4.0448 | Fixture/1000 sf | 150.8918 | 415.383 | 415.383 | 0.025346 | 0.069773 | 0.069773 | 0 | 0 | 0 | 155.5695 | 428.2599 | 428.2599 | 0.02968 | 0.081704 | 0.081704 | -1.2658 | -3.4844 | -3.4844 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RFF | RESTAURANT - FAST-FOOD | New | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 3.5448 | 0.020224 | 4.0448 | Fixture/1000 sf | 150.8925 | 415.385 | 415.385 | 0.025346 | 0.069772 | 0.069772 | 0 | 0 | 0 | 152.7636 | 420.5357 | 420.5357 | 0.03102 | 0.085394 | 0.085394 | -1.5557 | -4.2826 | -4.2826 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RFF | RESTAURANT - FAST-FOOD | Existing | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 3.5448 | 0.020224 | 4.0448 | Fixture/1000 sf | 150.8873 | 415.3705 | 415.3705 | 0.025345 | 0.069772 | 0.069772 | 0 | 0 | 0 | 154.0107 | 423.9687 | 423.9687 | 0.029555 | 0.081361 | 0.081361 | -1.3437 | -3.699 | -3.699 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RFF | RESTAURANT - FAST-FOOD | New | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 3.5448 | 0.020224 | 4.0448 | Fixture/1000 sf | 150.8929 | 415.3861 | 415.3861 | 0.025346 | 0.069775 | 0.069775 | 0 | 0 | 0 | 149.3342 | 411.0951 | 411.0951 | 0.030023 | 0.082648 | 0.082648 | -1.5557 | -4.2826 | -4.2826 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RFF | RESTAURANT - FAST-FOOD | Existing | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 3.5448 | 0.020224 | 4.0448 | Fixture/1000 sf | 150.896 | 415.3945 | 415.3945 | 0.025346 | 0.069773 | 0.069773 | 0 | 0 | 0 | 158.0636 | 435.1257 | 435.1257 | 0.02968 | 0.081704 | 0.081704 | -1.0538 | -2.9008 | -2.9008 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RFF | RESTAURANT - FAST-FOOD | New | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 3.5448 | 0.020224 | 4.0448 | Fixture/1000 sf | 150.8918 | 415.383 | 415.383 | 0.025346 | 0.069773 | 0.069773 | 0 | 0 | 0 | 155.5695 | 428.2599 | 428.2599 | 0.030615 | 0.084279 | 0.084279 | -1.2689 | -3.493 | -3.493 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RFF | RESTAURANT - FAST-FOOD | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 3.5448 | 0.020224 | 4.0448 | Fixture/1000 sf | 150.8973 | 415.3981 | 415.3981 | 0.025347 | 0.069776 | 0.069776 | 0 | 0 | 0 | 153.3871 | 422.2522 | 422.2522 | 0.029212 | 0.080417 | 0.080417 | -1.3624 | -3.7505 | -3.7505 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RFF | RESTAURANT - FAST-FOOD | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 3.5448 | 0.020224 | 4.0448 | Fixture/1000 sf | 150.8929 | 415.3861 | 415.3861 | 0.025346 | 0.069774 | 0.069774 | 0 | 0 | 0 | 149.3342 | 411.0951 | 411.0951 | 0.029586 | 0.081447 | 0.081447 | -1.3686 | -3.7677 | -3.7677 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RFF | RESTAURANT - FAST-FOOD | Existing | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 3.5448 | 0.020224 | 4.0448 | Fixture/1000 sf | 150.8958 | 415.3938 | 415.3938 | 0.025346 | 0.069774 | 0.069774 | 0 | 0 | 0 | 158.9989 | 437.7004 | 437.7004 | 0.03021 | 0.083163 | 0.083163 | -1.0382 | -2.8579 | -2.8579 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RFF | RESTAURANT - FAST-FOOD | New | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 3.5448 | 0.020224 | 4.0448 | Fixture/1000 sf | 150.8958 | 415.3938 | 415.3938 | 0.025347 | 0.069775 | 0.069775 | 0 | 0 | 0 | 158.9989 | 437.7004 | 437.7004 | 0.031488 | 0.086682 | 0.086682 | -1.2502 | -3.4415 | -3.4415 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RFF | RESTAURANT - FAST-FOOD | Existing | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 3.5448 | 0.020224 | 4.0448 | Fixture/1000 sf | 150.8911 | 415.3811 | 415.3811 | 0.025347 | 0.069777 | 0.069777 | 0 | 0 | 0 | 158.3753 | 435.984 | 435.984 | 0.02996 | 0.082476 | 0.082476 | -1.0818 | -2.9781 | -2.9781 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RFF | RESTAURANT - FAST-FOOD | New | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 3.5448 | 0.020224 | 4.0448 | Fixture/1000 sf | 150.8914 | 415.3817 | 415.3817 | 0.025347 | 0.069775 | 0.069775 | 0 | 0 | 0 | 157.44 | 433.4093 | 433.4093 | 0.031176 | 0.085824 | 0.085824 | -1.3468 | -3.7076 | -3.7076 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RFF | RESTAURANT - FAST-FOOD | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 3.5448 | 0.020224 | 4.0448 | Fixture/1000 sf | 150.8861 | 415.3672 | 415.3672 | 0.025347 | 0.069776 | 0.069776 | 0 | 0 | 0 | 159.6224 | 439.4169 | 439.4169 | 0.029836 | 0.082133 | 0.082133 | -0.98829 | -2.7206 | -2.7206 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RFF | RESTAURANT - FAST-FOOD | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 3.5448 | 0.020224 | 4.0448 | Fixture/1000 sf | 150.8861 | 415.3672 | 415.3672 | 0.025347 | 0.069775 | 0.069775 | 0 | 0 | 0 | 159.6224 | 439.4169 | 439.4169 | 0.031176 | 0.085824 | 0.085824 | -1.1909 | -3.2785 | -3.2785 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RFF | RESTAURANT - FAST-FOOD | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 3.5448 | 0.020224 | 4.0448 | Fixture/1000 sf | 150.8935 | 415.3875 | 415.3875 | 0.025346 | 0.069773 | 0.069773 | 0 | 0 | 0 | 147.4636 | 405.9457 | 405.9457 | 0.029368 | 0.080846 | 0.080846 | -1.9018 | -5.2352 | -5.2352 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RFF | RESTAURANT - FAST-FOOD | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 3.5448 | 0.020224 | 4.0448 | Fixture/1000 sf | 150.8931 | 415.3865 | 415.3865 | 0.025347 | 0.069776 | 0.069776 | 0 | 0 | 0 | 146.8401 | 404.2292 | 404.2292 | 0.030147 | 0.082991 | 0.082991 | -2.1137 | -5.8188 | -5.8188 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RFF | RESTAURANT - FAST-FOOD | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 2.2762 | 0.013042 | 2.6084 | Fixture/1000 sf | 143.3262 | 450.2759 | 450.2759 | 0.024077 | 0.07564 | 0.07564 | 0 | 0 | 0 | 148.9589 | 467.9717 | 467.9717 | 0.028844 | 0.090617 | 0.090617 | -1.4777 | -4.6425 | -4.6425 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RFF | RESTAURANT - FAST-FOOD | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 2.2762 | 0.013042 | 2.6084 | Fixture/1000 sf | 143.3358 | 450.3061 | 450.3061 | 0.024076 | 0.075637 | 0.075637 | 0 | 0 | 0 | 147.4782 | 463.3199 | 463.3199 | 0.029377 | 0.092292 | 0.092292 | -1.4481 | -4.5495 | -4.5495 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RFF | RESTAURANT - FAST-FOOD | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 2.2762 | 0.013042 | 2.6084 | Fixture/1000 sf | 143.329 | 450.2847 | 450.2847 | 0.024077 | 0.07564 | 0.07564 | 0 | 0 | 0 | 156.6586 | 492.1611 | 492.1611 | 0.029436 | 0.092478 | 0.092478 | -0.8055 | -2.5306 | -2.5306 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RFF | RESTAURANT - FAST-FOOD | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 2.2762 | 0.013042 | 2.6084 | Fixture/1000 sf | 143.3294 | 450.2859 | 450.2859 | 0.024076 | 0.075639 | 0.075639 | 0 | 0 | 0 | 154.8817 | 486.579 | 486.579 | 0.030206 | 0.094897 | 0.094897 | -0.78477 | -2.4655 | -2.4655 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RFF | RESTAURANT - FAST-FOOD | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 2.2762 | 0.013042 | 2.6084 | Fixture/1000 sf | 143.3286 | 450.2834 | 450.2834 | 0.024076 | 0.075638 | 0.075638 | 0 | 0 | 0 | 158.4354 | 497.7433 | 497.7433 | 0.029199 | 0.091734 | 0.091734 | -0.7137 | -2.2422 | -2.2422 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RFF | RESTAURANT - FAST-FOOD | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 2.2762 | 0.013042 | 2.6084 | Fixture/1000 sf | 143.3332 | 450.2979 | 450.2979 | 0.024076 | 0.075639 | 0.075639 | 0 | 0 | 0 | 157.2508 | 494.0219 | 494.0219 | 0.030503 | 0.095827 | 0.095827 | -0.85289 | -2.6794 | -2.6794 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RFF | RESTAURANT - FAST-FOOD | Existing | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 2.2762 | 0.013042 | 2.6084 | Fixture/1000 sf | 143.3371 | 450.3103 | 450.3103 | 0.024076 | 0.075639 | 0.075639 | 0 | 0 | 0 | 158.7315 | 498.6737 | 498.6737 | 0.02991 | 0.093966 | 0.093966 | -0.74035 | -2.3259 | -2.3259 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RFF | RESTAURANT - FAST-FOOD | New | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 2.2762 | 0.013042 | 2.6084 | Fixture/1000 sf | 143.333 | 450.2972 | 450.2972 | 0.024076 | 0.075639 | 0.075639 | 0 | 0 | 0 | 158.1393 | 496.8129 | 496.8129 | 0.031391 | 0.098618 | 0.098618 | -0.921 | -2.8934 | -2.8934 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RFF | RESTAURANT - FAST-FOOD | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 2.2762 | 0.013042 | 2.6084 | Fixture/1000 sf | 143.3336 | 450.2993 | 450.2993 | 0.024077 | 0.075641 | 0.075641 | 0 | 0 | 0 | 155.474 | 488.4397 | 488.4397 | 0.029348 | 0.092199 | 0.092199 | -0.82327 | -2.5864 | -2.5864 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RFF | RESTAURANT - FAST-FOOD | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 2.2762 | 0.013042 | 2.6084 | Fixture/1000 sf | 143.3327 | 450.2966 | 450.2966 | 0.024076 | 0.075639 | 0.075639 | 0 | 0 | 0 | 159.0277 | 499.604 | 499.604 | 0.031687 | 0.099549 | 0.099549 | -0.94469 | -2.9679 | -2.9679 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RFF | RESTAURANT - FAST-FOOD | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 2.2762 | 0.013042 | 2.6084 | Fixture/1000 sf | 143.3381 | 450.3134 | 450.3134 | 0.024075 | 0.075635 | 0.075635 | 0 | 0 | 0 | 155.1779 | 487.5093 | 487.5093 | 0.029555 | 0.09285 | 0.09285 | -1.1016 | -3.4609 | -3.4609 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RFF | RESTAURANT - FAST-FOOD | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 2.2762 | 0.013042 | 2.6084 | Fixture/1000 sf | 143.3286 | 450.2834 | 450.2834 | 0.024076 | 0.075639 | 0.075639 | 0 | 0 | 0 | 158.4354 | 497.7433 | 497.7433 | 0.031391 | 0.098618 | 0.098618 | -1.2704 | -3.9913 | -3.9913 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RFF | RESTAURANT - FAST-FOOD | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 2.7441 | 0.013961 | 2.7923 | Fixture/1000 sf | 140.0438 | 452.0155 | 452.0155 | 0.023524 | 0.075928 | 0.075928 | 0 | 0 | 0 | 156.2469 | 504.3137 | 504.3137 | 0.028935 | 0.093391 | 0.093391 | -0.80438 | -2.5963 | -2.5963 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RFF | RESTAURANT - FAST-FOOD | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 2.7441 | 0.013961 | 2.7923 | Fixture/1000 sf | 140.0451 | 452.0197 | 452.0197 | 0.023524 | 0.075928 | 0.075928 | 0 | 0 | 0 | 151.0387 | 487.5033 | 487.5033 | 0.029513 | 0.095259 | 0.095259 | -0.7986 | -2.5776 | -2.5776 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RFF | RESTAURANT - FAST-FOOD | Existing | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 2.7441 | 0.013961 | 2.7923 | Fixture/1000 sf | 140.0396 | 452.0018 | 452.0018 | 0.023523 | 0.075924 | 0.075924 | 0 | 0 | 0 | 156.5363 | 505.2476 | 505.2476 | 0.028877 | 0.093205 | 0.093205 | -0.73494 | -2.3721 | -2.3721 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RFF | RESTAURANT - FAST-FOOD | New | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 2.7441 | 0.013961 | 2.7923 | Fixture/1000 sf | 140.0454 | 452.0205 | 452.0205 | 0.023524 | 0.075928 | 0.075928 | 0 | 0 | 0 | 150.1707 | 484.7015 | 484.7015 | 0.029224 | 0.094325 | 0.094325 | -0.91144 | -2.9418 | -2.9418 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RFF | RESTAURANT - FAST-FOOD | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 2.7441 | 0.013961 | 2.7923 | Fixture/1000 sf | 140.0394 | 452.0012 | 452.0012 | 0.023523 | 0.075925 | 0.075925 | 0 | 0 | 0 | 157.4043 | 508.0494 | 508.0494 | 0.02879 | 0.092924 | 0.092924 | -0.71468 | -2.3068 | -2.3068 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RFF | RESTAURANT - FAST-FOOD | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 2.7441 | 0.013961 | 2.7923 | Fixture/1000 sf | 140.0488 | 452.0316 | 452.0316 | 0.023524 | 0.075928 | 0.075928 | 0 | 0 | 0 | 153.3535 | 494.9746 | 494.9746 | 0.029803 | 0.096193 | 0.096193 | -0.86514 | -2.7924 | -2.7924 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RFF | RESTAURANT - FAST-FOOD | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 2.7441 | 0.013961 | 2.7923 | Fixture/1000 sf | 140.0394 | 452.0012 | 452.0012 | 0.023524 | 0.075928 | 0.075928 | 0 | 0 | 0 | 157.4043 | 508.0494 | 508.0494 | 0.029224 | 0.094325 | 0.094325 | -0.78991 | -2.5496 | -2.5496 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RFF | RESTAURANT - FAST-FOOD | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 2.7441 | 0.013961 | 2.7923 | Fixture/1000 sf | 140.0483 | 452.03 | 452.03 | 0.023524 | 0.075928 | 0.075928 | 0 | 0 | 0 | 155.0895 | 500.5781 | 500.5781 | 0.03096 | 0.099929 | 0.099929 | -0.95774 | -3.0913 | -3.0913 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RT3 | RETAIL - MULTISTORY LARGE | New | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 3.0977 | 0.024297 | 4.8593 | Fixture/1000 sf | 105.376 | 290.0847 | 290.0847 | 0.023695 | 0.065228 | 0.065228 | 0 | 0 | 0 | 109.1169 | 300.3827 | 300.3827 | 0.028495 | 0.078443 | 0.078443 | -0.74511 | -2.0512 | -2.0512 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RT3 | RETAIL - MULTISTORY LARGE | Existing | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 3.0977 | 0.024297 | 4.8593 | Fixture/1000 sf | 105.3773 | 290.0881 | 290.0881 | 0.023682 | 0.065193 | 0.065193 | 0 | 0 | 0 | 115.0403 | 316.6891 | 316.6891 | 0.028246 | 0.077756 | 0.077756 | -0.3897 | -1.0728 | -1.0728 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RT3 | RETAIL - MULTISTORY LARGE | New | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 3.0977 | 0.024297 | 4.8593 | Fixture/1000 sf | 105.3722 | 290.0742 | 290.0742 | 0.023693 | 0.065224 | 0.065224 | 0 | 0 | 0 | 113.1698 | 311.5397 | 311.5397 | 0.028963 | 0.07973 | 0.07973 | -0.51129 | -1.4075 | -1.4075 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RT3 | RETAIL - MULTISTORY LARGE | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 3.0977 | 0.024297 | 4.8593 | Fixture/1000 sf | 105.3722 | 290.0742 | 290.0742 | 0.023664 | 0.065144 | 0.065144 | 0 | 0 | 0 | 113.1698 | 311.5397 | 311.5397 | 0.027716 | 0.076297 | 0.076297 | -0.47076 | -1.2959 | -1.2959 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RT3 | RETAIL - MULTISTORY LARGE | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 3.0977 | 0.024297 | 4.8593 | Fixture/1000 sf | 105.3736 | 290.0779 | 290.0779 | 0.023695 | 0.065228 | 0.065228 | 0 | 0 | 0 | 110.0521 | 302.9574 | 302.9574 | 0.028121 | 0.077413 | 0.077413 | -0.59547 | -1.6392 | -1.6392 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RT3 | RETAIL - MULTISTORY LARGE | Existing | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 3.0977 | 0.024297 | 4.8593 | Fixture/1000 sf | 105.3804 | 290.0967 | 290.0967 | 0.023665 | 0.065147 | 0.065147 | 0 | 0 | 0 | 112.5462 | 309.8233 | 309.8233 | 0.028339 | 0.078014 | 0.078014 | -0.63911 | -1.7594 | -1.7594 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RT3 | RETAIL - MULTISTORY LARGE | New | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 3.0977 | 0.024297 | 4.8593 | Fixture/1000 sf | 105.3722 | 290.0742 | 290.0742 | 0.023694 | 0.065227 | 0.065227 | 0 | 0 | 0 | 113.1698 | 311.5397 | 311.5397 | 0.028682 | 0.078958 | 0.078958 | -0.66405 | -1.828 | -1.828 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RT3 | RETAIL - MULTISTORY LARGE | Existing | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 3.0977 | 0.024297 | 4.8593 | Fixture/1000 sf | 105.3763 | 290.0854 | 290.0854 | 0.023665 | 0.065146 | 0.065146 | 0 | 0 | 0 | 112.858 | 310.6815 | 310.6815 | 0.028495 | 0.078443 | 0.078443 | -0.60794 | -1.6736 | -1.6736 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RT3 | RETAIL - MULTISTORY LARGE | New | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 3.0977 | 0.024297 | 4.8593 | Fixture/1000 sf | 105.3722 | 290.0742 | 290.0742 | 0.023694 | 0.065226 | 0.065226 | 0 | 0 | 0 | 113.1698 | 311.5397 | 311.5397 | 0.029617 | 0.081532 | 0.081532 | -0.72017 | -1.9825 | -1.9825 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RTL | RETAIL - SINGLE-STORY LARGE | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 2.89 | 0.019059 | 3.8119 | Fixture/1000 sf | 126.4521 | 397.264 | 397.264 | 0.025113 | 0.078896 | 0.078896 | 0 | 0 | 0 | 144.8129 | 454.9467 | 454.9467 | 0.030799 | 0.096758 | 0.096758 | -0.29318 | -0.92106 | -0.92106 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RTL | RETAIL - SINGLE-STORY LARGE | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 2.89 | 0.019059 | 3.8119 | Fixture/1000 sf | 126.4554 | 397.2744 | 397.2744 | 0.025113 | 0.078895 | 0.078895 | 0 | 0 | 0 | 140.0747 | 440.0609 | 440.0609 | 0.031391 | 0.098618 | 0.098618 | -0.39979 | -1.256 | -1.256 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RTL | RETAIL - SINGLE-STORY LARGE | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 2.89 | 0.019059 | 3.8119 | Fixture/1000 sf | 126.4503 | 397.2584 | 397.2584 | 0.025113 | 0.078895 | 0.078895 | 0 | 0 | 0 | 145.4052 | 456.8074 | 456.8074 | 0.031095 | 0.097688 | 0.097688 | -0.25409 | -0.79825 | -0.79825 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RTL | RETAIL - SINGLE-STORY LARGE | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 2.89 | 0.019059 | 3.8119 | Fixture/1000 sf | 126.4499 | 397.2572 | 397.2572 | 0.025112 | 0.078894 | 0.078894 | 0 | 0 | 0 | 141.8515 | 445.6431 | 445.6431 | 0.031983 | 0.10048 | 0.10048 | -0.34056 | -1.0699 | -1.0699 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RTL | RETAIL - SINGLE-STORY LARGE | Existing | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 2.89 | 0.019059 | 3.8119 | Fixture/1000 sf | 126.4492 | 397.255 | 397.255 | 0.025113 | 0.078894 | 0.078894 | 0 | 0 | 0 | 143.9245 | 452.1556 | 452.1556 | 0.031687 | 0.099549 | 0.099549 | -0.30206 | -0.94897 | -0.94897 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RTL | RETAIL - SINGLE-STORY LARGE | New | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 2.89 | 0.019059 | 3.8119 | Fixture/1000 sf | 126.4481 | 397.2515 | 397.2515 | 0.025112 | 0.078892 | 0.078892 | 0 | 0 | 0 | 142.4438 | 447.5038 | 447.5038 | 0.033168 | 0.1042 | 0.1042 | -0.34056 | -1.0699 | -1.0699 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RTL | RETAIL - SINGLE-STORY LARGE | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 2.89 | 0.019059 | 3.8119 | Fixture/1000 sf | 126.4517 | 397.2629 | 397.2629 | 0.025113 | 0.078895 | 0.078895 | 0 | 0 | 0 | 141.2592 | 443.7824 | 443.7824 | 0.031391 | 0.098618 | 0.098618 | -0.3376 | -1.0606 | -1.0606 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RTL | RETAIL - SINGLE-STORY LARGE | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 2.89 | 0.019059 | 3.8119 | Fixture/1000 sf | 126.4575 | 397.281 | 397.281 | 0.025112 | 0.078892 | 0.078892 | 0 | 0 | 0 | 143.0361 | 449.3645 | 449.3645 | 0.033168 | 0.1042 | 0.1042 | -0.39683 | -1.2467 | -1.2467 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RTL | RETAIL - SINGLE-STORY LARGE | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 2.89 | 0.019059 | 3.8119 | Fixture/1000 sf | 126.4543 | 397.2711 | 397.2711 | 0.025113 | 0.078895 | 0.078895 | 0 | 0 | 0 | 138.594 | 435.4091 | 435.4091 | 0.031391 | 0.098618 | 0.098618 | -0.69593 | -2.1863 | -2.1863 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RTS | RETAIL - SMALL | Existing | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 3.1602 | 0.018913 | 3.7827 | Fixture/1000 sf | 97.8006 | 315.6683 | 315.6683 | 0.025318 | 0.081718 | 0.081718 | 0 | 0 | 0 | 110.2409 | 355.8214 | 355.8214 | 0.030381 | 0.098061 | 0.098061 | -0.091144 | -0.29418 | -0.29418 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RTS | RETAIL - SMALL | New | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 3.1602 | 0.018913 | 3.7827 | Fixture/1000 sf | 97.802 | 315.6726 | 315.6726 | 0.025318 | 0.081718 | 0.081718 | 0 | 0 | 0 | 107.3474 | 346.4822 | 346.4822 | 0.030381 | 0.098061 | 0.098061 | -0.11921 | -0.38477 | -0.38477 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RTS | RETAIL - SMALL | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 3.1602 | 0.018913 | 3.7827 | Fixture/1000 sf | 97.8021 | 315.6731 | 315.6731 | 0.025317 | 0.081715 | 0.081715 | 0 | 0 | 0 | 110.8196 | 357.6892 | 357.6892 | 0.03096 | 0.099929 | 0.099929 | -0.12992 | -0.41933 | -0.41933 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RFF | RESTAURANT - FAST-FOOD | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 2.7441 | 0.013961 | 2.7923 | Fixture/1000 sf | 140.0486 | 452.0308 | 452.0308 | 0.023524 | 0.075928 | 0.075928 | 0 | 0 | 0 | 154.2215 | 497.7763 | 497.7763 | 0.029803 | 0.096193 | 0.096193 | -1.1227 | -3.6236 | -3.6236 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RFF | RESTAURANT - FAST-FOOD | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 2.7441 | 0.013961 | 2.7923 | Fixture/1000 sf | 140.0486 | 452.0308 | 452.0308 | 0.023524 | 0.075928 | 0.075928 | 0 | 0 | 0 | 154.2215 | 497.7763 | 497.7763 | 0.031249 | 0.10086 | 0.10086 | -1.357 | -4.3801 | -4.3801 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RFF | RESTAURANT - FAST-FOOD | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 2.7441 | 0.013961 | 2.7923 | Fixture/1000 sf | 140.0493 | 452.033 | 452.033 | 0.023524 | 0.075928 | 0.075928 | 0 | 0 | 0 | 166.9527 | 538.8686 | 538.8686 | 0.029513 | 0.095259 | 0.095259 | -0.36168 | -1.1674 | -1.1674 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RFF | RESTAURANT - FAST-FOOD | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 2.7441 | 0.013961 | 2.7923 | Fixture/1000 sf | 140.0455 | 452.0208 | 452.0208 | 0.023524 | 0.075928 | 0.075928 | 0 | 0 | 0 | 166.374 | 537.0007 | 537.0007 | 0.031539 | 0.1018 | 0.1018 | -0.47163 | -1.5223 | -1.5223 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RSD | RESTAURANT - SIT-DOWN | New | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 3.5448 | 0.020224 | 4.0448 | Fixture/1000 sf | 150.5805 | 414.526 | 414.526 | 0.02494 | 0.068656 | 0.068656 | 0 | 0 | 0 | 139.0461 | 382.7733 | 382.7733 | 0.0289 | 0.079558 | 0.079558 | -1.2346 | -3.3986 | -3.3986 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RSD | RESTAURANT - SIT-DOWN | Existing | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 3.5448 | 0.020224 | 4.0448 | Fixture/1000 sf | 150.5812 | 414.5279 | 414.5279 | 0.02494 | 0.068656 | 0.068656 | 0 | 0 | 0 | 150.2695 | 413.6698 | 413.6698 | 0.029524 | 0.081275 | 0.081275 | -1.6118 | -4.4371 | -4.4371 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RSD | RESTAURANT - SIT-DOWN | New | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 3.5448 | 0.020224 | 4.0448 | Fixture/1000 sf | 150.5808 | 414.5267 | 414.5267 | 0.024941 | 0.068659 | 0.068659 | 0 | 0 | 0 | 148.0872 | 407.6622 | 407.6622 | 0.030366 | 0.083592 | 0.083592 | -1.8363 | -5.055 | -5.055 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RSD | RESTAURANT - SIT-DOWN | Existing | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 3.5448 | 0.020224 | 4.0448 | Fixture/1000 sf | 150.5765 | 414.5149 | 414.5149 | 0.024941 | 0.068659 | 0.068659 | 0 | 0 | 0 | 156.193 | 429.9763 | 429.9763 | 0.029555 | 0.081361 | 0.081361 | -1.1785 | -3.2441 | -3.2441 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RSD | RESTAURANT - SIT-DOWN | New | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 3.5448 | 0.020224 | 4.0448 | Fixture/1000 sf | 150.5851 | 414.5386 | 414.5386 | 0.024942 | 0.068662 | 0.068662 | 0 | 0 | 0 | 155.5695 | 428.2599 | 428.2599 | 0.030833 | 0.08488 | 0.08488 | -1.3375 | -3.6818 | -3.6818 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RSD | RESTAURANT - SIT-DOWN | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 3.5448 | 0.020224 | 4.0448 | Fixture/1000 sf | 150.5813 | 414.5281 | 414.5281 | 0.02494 | 0.068656 | 0.068656 | 0 | 0 | 0 | 150.5813 | 414.5281 | 414.5281 | 0.029337 | 0.08076 | 0.08076 | -1.5495 | -4.2654 | -4.2654 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RSD | RESTAURANT - SIT-DOWN | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 3.5448 | 0.020224 | 4.0448 | Fixture/1000 sf | 150.5808 | 414.5267 | 414.5267 | 0.024941 | 0.068659 | 0.068659 | 0 | 0 | 0 | 148.0872 | 407.6622 | 407.6622 | 0.029617 | 0.081532 | 0.081532 | -1.777 | -4.8919 | -4.8919 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RSD | RESTAURANT - SIT-DOWN | Existing | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 3.5448 | 0.020224 | 4.0448 | Fixture/1000 sf | 150.5808 | 414.5267 | 414.5267 | 0.024941 | 0.068659 | 0.068659 | 0 | 0 | 0 | 155.8812 | 429.1181 | 429.1181 | 0.029368 | 0.080846 | 0.080846 | -1.2782 | -3.5188 | -3.5188 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RSD | RESTAURANT - SIT-DOWN | New | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 3.5448 | 0.020224 | 4.0448 | Fixture/1000 sf | 150.5824 | 414.5312 | 414.5312 | 0.024941 | 0.068659 | 0.068659 | 0 | 0 | 0 | 156.8165 | 431.6928 | 431.6928 | 0.031488 | 0.086682 | 0.086682 | -1.4279 | -3.9307 | -3.9307 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RSD | RESTAURANT - SIT-DOWN | Existing | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 3.5448 | 0.020224 | 4.0448 | Fixture/1000 sf | 150.5791 | 414.5222 | 414.5222 | 0.02494 | 0.068656 | 0.068656 | 0 | 0 | 0 | 154.9459 | 426.5434 | 426.5434 | 0.028277 | 0.077842 | 0.077842 | -1.3125 | -3.6132 | -3.6132 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RSD | RESTAURANT - SIT-DOWN | New | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 3.5448 | 0.020224 | 4.0448 | Fixture/1000 sf | 150.5851 | 414.5386 | 414.5386 | 0.024941 | 0.068659 | 0.068659 | 0 | 0 | 0 | 155.5695 | 428.2599 | 428.2599 | 0.030989 | 0.085309 | 0.085309 | -1.4372 | -3.9565 | -3.9565 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RSD | RESTAURANT - SIT-DOWN | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 3.5448 | 0.020224 | 4.0448 | Fixture/1000 sf | 150.5781 | 414.5194 | 414.5194 | 0.024941 | 0.068659 | 0.068659 | 0 | 0 | 0 | 157.1283 | 432.551 | 432.551 | 0.029617 | 0.081532 | 0.081532 | -1.1847 | -3.2613 | -3.2613 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RSD | RESTAURANT - SIT-DOWN | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 3.5448 | 0.020224 | 4.0448 | Fixture/1000 sf | 150.584 | 414.5356 | 414.5356 | 0.024941 | 0.068659 | 0.068659 | 0 | 0 | 0 | 157.7518 | 434.2675 | 434.2675 | 0.031488 | 0.086682 | 0.086682 | -1.3499 | -3.7162 | -3.7162 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RSD | RESTAURANT - SIT-DOWN | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 3.5448 | 0.020224 | 4.0448 | Fixture/1000 sf | 150.5814 | 414.5283 | 414.5283 | 0.02494 | 0.068656 | 0.068656 | 0 | 0 | 0 | 143.099 | 393.9304 | 393.9304 | 0.028402 | 0.078185 | 0.078185 | -2.0919 | -5.7588 | -5.7588 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RSD | RESTAURANT - SIT-DOWN | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 3.5448 | 0.020224 | 4.0448 | Fixture/1000 sf | 150.5813 | 414.5281 | 414.5281 | 0.024941 | 0.068659 | 0.068659 | 0 | 0 | 0 | 142.7872 | 393.0722 | 393.0722 | 0.029742 | 0.081876 | 0.081876 | -1.671 | -4.6001 | -4.6001 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RSD | RESTAURANT - SIT-DOWN | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 2.2762 | 0.013042 | 2.6084 | Fixture/1000 sf | 143.0356 | 449.3631 | 449.3631 | 0.02369 | 0.074426 | 0.074426 | 0 | 0 | 0 | 148.0705 | 465.1807 | 465.1807 | 0.02917 | 0.091641 | 0.091641 | -1.688 | -5.3031 | -5.3031 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RSD | RESTAURANT - SIT-DOWN | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 2.2762 | 0.013042 | 2.6084 | Fixture/1000 sf | 143.0423 | 449.3841 | 449.3841 | 0.023691 | 0.074429 | 0.074429 | 0 | 0 | 0 | 146.5898 | 460.5289 | 460.5289 | 0.029555 | 0.09285 | 0.09285 | -1.9012 | -5.9729 | -5.9729 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RSD | RESTAURANT - SIT-DOWN | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 2.2762 | 0.013042 | 2.6084 | Fixture/1000 sf | 143.031 | 449.3485 | 449.3485 | 0.023691 | 0.074429 | 0.074429 | 0 | 0 | 0 | 158.4354 | 497.7433 | 497.7433 | 0.029436 | 0.092478 | 0.092478 | -0.87658 | -2.7539 | -2.7539 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RSD | RESTAURANT - SIT-DOWN | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 2.2762 | 0.013042 | 2.6084 | Fixture/1000 sf | 143.0357 | 449.3634 | 449.3634 | 0.023691 | 0.074429 | 0.074429 | 0 | 0 | 0 | 156.0663 | 490.3004 | 490.3004 | 0.02991 | 0.093966 | 0.093966 | -1.0572 | -3.3214 | -3.3214 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RSD | RESTAURANT - SIT-DOWN | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 2.2762 | 0.013042 | 2.6084 | Fixture/1000 sf | 143.0415 | 449.3814 | 449.3814 | 0.023691 | 0.074429 | 0.074429 | 0 | 0 | 0 | 159.62 | 501.4648 | 501.4648 | 0.028548 | 0.089687 | 0.089687 | -0.72258 | -2.2701 | -2.2701 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RSD | RESTAURANT - SIT-DOWN | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 2.2762 | 0.013042 | 2.6084 | Fixture/1000 sf | 143.0348 | 449.3605 | 449.3605 | 0.023691 | 0.074429 | 0.074429 | 0 | 0 | 0 | 158.1393 | 496.8129 | 496.8129 | 0.030206 | 0.094897 | 0.094897 | -0.86769 | -2.726 | -2.726 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RSD | RESTAURANT - SIT-DOWN | Existing | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 2.2762 | 0.013042 | 2.6084 | Fixture/1000 sf | 143.0362 | 449.365 | 449.365 | 0.02369 | 0.074426 | 0.074426 | 0 | 0 | 0 | 159.0277 | 499.604 | 499.604 | 0.028755 | 0.090338 | 0.090338 | -0.81735 | -2.5678 | -2.5678 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RSD | RESTAURANT - SIT-DOWN | New | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 2.2762 | 0.013042 | 2.6084 | Fixture/1000 sf | 143.0362 | 449.365 | 449.365 | 0.023691 | 0.074429 | 0.074429 | 0 | 0 | 0 | 159.0277 | 499.604 | 499.604 | 0.031391 | 0.098618 | 0.098618 | -0.92396 | -2.9027 | -2.9027 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RSD | RESTAURANT - SIT-DOWN | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 2.2762 | 0.013042 | 2.6084 | Fixture/1000 sf | 143.041 | 449.3802 | 449.3802 | 0.023691 | 0.074429 | 0.074429 | 0 | 0 | 0 | 156.6586 | 492.1611 | 492.1611 | 0.027304 | 0.085779 | 0.085779 | -0.85881 | -2.698 | -2.698 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RSD | RESTAURANT - SIT-DOWN | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 2.2762 | 0.013042 | 2.6084 | Fixture/1000 sf | 143.0415 | 449.3814 | 449.3814 | 0.023691 | 0.074429 | 0.074429 | 0 | 0 | 0 | 159.62 | 501.4648 | 501.4648 | 0.031391 | 0.098618 | 0.098618 | -0.94469 | -2.9679 | -2.9679 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RSD | RESTAURANT - SIT-DOWN | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 2.2762 | 0.013042 | 2.6084 | Fixture/1000 sf | 143.0421 | 449.3834 | 449.3834 | 0.023691 | 0.074429 | 0.074429 | 0 | 0 | 0 | 154.5856 | 485.6486 | 485.6486 | 0.029496 | 0.092664 | 0.092664 | -1.3089 | -4.1122 | -4.1122 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RSD | RESTAURANT - SIT-DOWN | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 2.2762 | 0.013042 | 2.6084 | Fixture/1000 sf | 143.0333 | 449.3559 | 449.3559 | 0.023691 | 0.074429 | 0.074429 | 0 | 0 | 0 | 157.2508 | 494.0219 | 494.0219 | 0.031983 | 0.10048 | 0.10048 | -1.46 | -4.5867 | -4.5867 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RSD | RESTAURANT - SIT-DOWN | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 2.2762 | 0.013042 | 2.6084 | Fixture/1000 sf | 143.0352 | 449.3617 | 449.3617 | 0.023691 | 0.074429 | 0.074429 | 0 | 0 | 0 | 153.1049 | 480.9968 | 480.9968 | 0.027423 | 0.086151 | 0.086151 | -1.3978 | -4.3913 | -4.3913 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RSD | RESTAURANT - SIT-DOWN | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 2.2762 | 0.013042 | 2.6084 | Fixture/1000 sf | 143.0318 | 449.3512 | 449.3512 | 0.023691 | 0.074429 | 0.074429 | 0 | 0 | 0 | 156.3624 | 491.2308 | 491.2308 | 0.031391 | 0.098618 | 0.098618 | -1.5162 | -4.7634 | -4.7634 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RSD | RESTAURANT - SIT-DOWN | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 2.2762 | 0.013042 | 2.6084 | Fixture/1000 sf | 143.0413 | 449.3809 | 449.3809 | 0.023691 | 0.074429 | 0.074429 | 0 | 0 | 0 | 167.6158 | 526.5845 | 526.5845 | 0.02991 | 0.093966 | 0.093966 | -0.34352 | -1.0792 | -1.0792 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RSD | RESTAURANT - SIT-DOWN | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 2.2762 | 0.013042 | 2.6084 | Fixture/1000 sf | 143.0394 | 449.3751 | 449.3751 | 0.023691 | 0.074429 | 0.074429 | 0 | 0 | 0 | 171.7617 | 539.6096 | 539.6096 | 0.032576 | 0.10234 | 0.10234 | -0.42348 | -1.3304 | -1.3304 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RSD | RESTAURANT - SIT-DOWN | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 2.2762 | 0.013042 | 2.6084 | Fixture/1000 sf | 143.0358 | 449.3638 | 449.3638 | 0.023691 | 0.074429 | 0.074429 | 0 | 0 | 0 | 141.8515 | 445.6431 | 445.6431 | 0.028015 | 0.088012 | 0.088012 | -2.304 | -7.2382 | -7.2382 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RSD | RESTAURANT - SIT-DOWN | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 2.2762 | 0.013042 | 2.6084 | Fixture/1000 sf | 143.0318 | 449.3512 | 449.3512 | 0.023691 | 0.074429 | 0.074429 | 0 | 0 | 0 | 143.3322 | 450.2949 | 450.2949 | 0.029614 | 0.093036 | 0.093036 | -1.8035 | -5.6659 | -5.6659 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RSD | RESTAURANT - SIT-DOWN | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 2.7441 | 0.013961 | 2.7923 | Fixture/1000 sf | 139.7484 | 451.0618 | 451.0618 | 0.023148 | 0.074713 | 0.074713 | 0 | 0 | 0 | 156.8256 | 506.1816 | 506.1816 | 0.028935 | 0.093391 | 0.093391 | -0.88251 | -2.8484 | -2.8484 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RSD | RESTAURANT - SIT-DOWN | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 2.7441 | 0.013961 | 2.7923 | Fixture/1000 sf | 139.7538 | 451.0795 | 451.0795 | 0.023148 | 0.074713 | 0.074713 | 0 | 0 | 0 | 152.4854 | 492.1728 | 492.1728 | 0.029224 | 0.094325 | 0.094325 | -1.0735 | -3.4648 | -3.4648 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RSD | RESTAURANT - SIT-DOWN | Existing | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 2.7441 | 0.013961 | 2.7923 | Fixture/1000 sf | 139.7484 | 451.0618 | 451.0618 | 0.023148 | 0.074713 | 0.074713 | 0 | 0 | 0 | 156.8256 | 506.1816 | 506.1816 | 0.029513 | 0.095259 | 0.095259 | -0.81017 | -2.615 | -2.615 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RSD | RESTAURANT - SIT-DOWN | New | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 2.7441 | 0.013961 | 2.7923 | Fixture/1000 sf | 139.7524 | 451.0748 | 451.0748 | 0.023148 | 0.074713 | 0.074713 | 0 | 0 | 0 | 151.6174 | 489.3711 | 489.3711 | 0.029803 | 0.096193 | 0.096193 | -1.0185 | -3.2874 | -3.2874 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RSD | RESTAURANT - SIT-DOWN | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 2.7441 | 0.013961 | 2.7923 | Fixture/1000 sf | 139.7585 | 451.0945 | 451.0945 | 0.023148 | 0.074713 | 0.074713 | 0 | 0 | 0 | 157.983 | 509.9172 | 509.9172 | 0.028067 | 0.09059 | 0.09059 | -0.73205 | -2.3628 | -2.3628 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RSD | RESTAURANT - SIT-DOWN | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 2.7441 | 0.013961 | 2.7923 | Fixture/1000 sf | 139.7567 | 451.0887 | 451.0887 | 0.023148 | 0.074713 | 0.074713 | 0 | 0 | 0 | 154.2215 | 497.7763 | 497.7763 | 0.029513 | 0.095259 | 0.095259 | -0.87961 | -2.8391 | -2.8391 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RSD | RESTAURANT - SIT-DOWN | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 2.7441 | 0.013961 | 2.7923 | Fixture/1000 sf | 139.7484 | 451.0618 | 451.0618 | 0.023147 | 0.07471 | 0.07471 | 0 | 0 | 0 | 156.8256 | 506.1816 | 506.1816 | 0.026707 | 0.0862 | 0.0862 | -0.86225 | -2.7831 | -2.7831 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RSD | RESTAURANT - SIT-DOWN | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 2.7441 | 0.013961 | 2.7923 | Fixture/1000 sf | 139.7595 | 451.0976 | 451.0976 | 0.023148 | 0.074713 | 0.074713 | 0 | 0 | 0 | 155.9576 | 503.3798 | 503.3798 | 0.03096 | 0.099929 | 0.099929 | -0.95484 | -3.0819 | -3.0819 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RSD | RESTAURANT - SIT-DOWN | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 2.7441 | 0.013961 | 2.7923 | Fixture/1000 sf | 139.7524 | 451.0748 | 451.0748 | 0.023148 | 0.074713 | 0.074713 | 0 | 0 | 0 | 151.6174 | 489.3711 | 489.3711 | 0.026678 | 0.086107 | 0.086107 | -1.412 | -4.5575 | -4.5575 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RSD | RESTAURANT - SIT-DOWN | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 2.7441 | 0.013961 | 2.7923 | Fixture/1000 sf | 139.7576 | 451.0918 | 451.0918 | 0.023148 | 0.074713 | 0.074713 | 0 | 0 | 0 | 152.1961 | 491.2389 | 491.2389 | 0.030671 | 0.098995 | 0.098995 | -1.5364 | -4.9591 | -4.9591 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RSD | RESTAURANT - SIT-DOWN | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 2.7441 | 0.013961 | 2.7923 | Fixture/1000 sf | 139.7553 | 451.0842 | 451.0842 | 0.023148 | 0.074713 | 0.074713 | 0 | 0 | 0 | 168.9782 | 545.406 | 545.406 | 0.029803 | 0.096193 | 0.096193 | -0.32985 | -1.0647 | -1.0647 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RSD | RESTAURANT - SIT-DOWN | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 2.7441 | 0.013961 | 2.7923 | Fixture/1000 sf | 139.754 | 451.0801 | 451.0801 | 0.023148 | 0.074713 | 0.074713 | 0 | 0 | 0 | 168.1101 | 542.6042 | 542.6042 | 0.031828 | 0.10273 | 0.10273 | -0.42823 | -1.3822 | -1.3822 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RT3 | RETAIL - MULTISTORY LARGE | New | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 3.0977 | 0.024297 | 4.8593 | Fixture/1000 sf | 105.3754 | 290.0829 | 290.0829 | 0.023694 | 0.065225 | 0.065225 | 0 | 0 | 0 | 101.6346 | 279.785 | 279.785 | 0.027996 | 0.07707 | 0.07707 | -1.5245 | -4.1968 | -4.1968 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RT3 | RETAIL - MULTISTORY LARGE | Existing | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 3.0977 | 0.024297 | 4.8593 | Fixture/1000 sf | 105.3757 | 290.0838 | 290.0838 | 0.023664 | 0.065143 | 0.065143 | 0 | 0 | 0 | 103.1934 | 284.0762 | 284.0762 | 0.028027 | 0.077155 | 0.077155 | -1.3375 | -3.6818 | -3.6818 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RT3 | RETAIL - MULTISTORY LARGE | Existing | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 3.0977 | 0.024297 | 4.8593 | Fixture/1000 sf | 105.3804 | 290.0967 | 290.0967 | 0.023663 | 0.065141 | 0.065141 | 0 | 0 | 0 | 112.5462 | 309.8233 | 309.8233 | 0.028152 | 0.077499 | 0.077499 | -0.64535 | -1.7765 | -1.7765 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RT3 | RETAIL - MULTISTORY LARGE | New | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 3.0977 | 0.024297 | 4.8593 | Fixture/1000 sf | 105.3712 | 290.0713 | 290.0713 | 0.023695 | 0.065228 | 0.065228 | 0 | 0 | 0 | 110.9874 | 305.5321 | 305.5321 | 0.029087 | 0.080073 | 0.080073 | -0.78252 | -2.1542 | -2.1542 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RT3 | RETAIL - MULTISTORY LARGE | Existing | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 3.0977 | 0.024297 | 4.8593 | Fixture/1000 sf | 105.3722 | 290.0742 | 290.0742 | 0.023665 | 0.065145 | 0.065145 | 0 | 0 | 0 | 113.1698 | 311.5397 | 311.5397 | 0.02809 | 0.077327 | 0.077327 | -0.58611 | -1.6135 | -1.6135 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RT3 | RETAIL - MULTISTORY LARGE | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 3.0977 | 0.024297 | 4.8593 | Fixture/1000 sf | 105.3722 | 290.0742 | 290.0742 | 0.023664 | 0.065143 | 0.065143 | 0 | 0 | 0 | 113.1698 | 311.5397 | 311.5397 | 0.028215 | 0.07767 | 0.07767 | -0.58923 | -1.6221 | -1.6221 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RT3 | RETAIL - MULTISTORY LARGE | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 3.0977 | 0.024297 | 4.8593 | Fixture/1000 sf | 105.3756 | 290.0835 | 290.0835 | 0.023694 | 0.065227 | 0.065227 | 0 | 0 | 0 | 114.4168 | 314.9727 | 314.9727 | 0.029462 | 0.081103 | 0.081103 | -0.64535 | -1.7765 | -1.7765 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RT3 | RETAIL - MULTISTORY LARGE | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 3.0977 | 0.024297 | 4.8593 | Fixture/1000 sf | 105.3757 | 290.0838 | 290.0838 | 0.023664 | 0.065143 | 0.065143 | 0 | 0 | 0 | 103.1934 | 284.0762 | 284.0762 | 0.027653 | 0.076126 | 0.076126 | -1.4216 | -3.9136 | -3.9136 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RT3 | RETAIL - MULTISTORY LARGE | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 3.0977 | 0.024297 | 4.8593 | Fixture/1000 sf | 105.3752 | 290.0826 | 290.0826 | 0.023694 | 0.065227 | 0.065227 | 0 | 0 | 0 | 104.1287 | 286.6509 | 286.6509 | 0.028277 | 0.077842 | 0.077842 | -1.4403 | -3.9651 | -3.9651 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RT3 | RETAIL - MULTISTORY LARGE | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 2.89 | 0.019059 | 3.8119 | Fixture/1000 sf | 100.0933 | 314.4548 | 314.4548 | 0.022495 | 0.07067 | 0.07067 | 0 | 0 | 0 | 109.5721 | 344.2337 | 344.2337 | 0.027304 | 0.085779 | 0.085779 | -0.41756 | -1.3118 | -1.3118 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RT3 | RETAIL - MULTISTORY LARGE | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 2.89 | 0.019059 | 3.8119 | Fixture/1000 sf | 100.093 | 314.4537 | 314.4537 | 0.022507 | 0.070709 | 0.070709 | 0 | 0 | 0 | 106.0185 | 333.0694 | 333.0694 | 0.02763 | 0.086803 | 0.086803 | -0.52417 | -1.6467 | -1.6467 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RT3 | RETAIL - MULTISTORY LARGE | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 2.89 | 0.019059 | 3.8119 | Fixture/1000 sf | 100.0975 | 314.468 | 314.468 | 0.02248 | 0.070622 | 0.070622 | 0 | 0 | 0 | 116.3834 | 365.632 | 365.632 | 0.0276 | 0.08671 | 0.08671 | -0.099799 | -0.31353 | -0.31353 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RT3 | RETAIL - MULTISTORY LARGE | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 2.89 | 0.019059 | 3.8119 | Fixture/1000 sf | 100.0973 | 314.4674 | 314.4674 | 0.022506 | 0.070706 | 0.070706 | 0 | 0 | 0 | 112.8297 | 354.4677 | 354.4677 | 0.027896 | 0.08764 | 0.08764 | -0.13178 | -0.41401 | -0.41401 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RT3 | RETAIL - MULTISTORY LARGE | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 2.89 | 0.019059 | 3.8119 | Fixture/1000 sf | 100.0975 | 314.468 | 314.468 | 0.022478 | 0.070619 | 0.070619 | 0 | 0 | 0 | 116.3834 | 365.632 | 365.632 | 0.027334 | 0.085872 | 0.085872 | -0.090027 | -0.28283 | -0.28283 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RT3 | RETAIL - MULTISTORY LARGE | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 2.89 | 0.019059 | 3.8119 | Fixture/1000 sf | 100.0915 | 314.4492 | 314.4492 | 0.022506 | 0.070707 | 0.070707 | 0 | 0 | 0 | 114.0143 | 358.1891 | 358.1891 | 0.028104 | 0.088291 | 0.088291 | -0.11105 | -0.34889 | -0.34889 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RT3 | RETAIL - MULTISTORY LARGE | Existing | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 2.89 | 0.019059 | 3.8119 | Fixture/1000 sf | 100.0946 | 314.4587 | 314.4587 | 0.022479 | 0.07062 | 0.07062 | 0 | 0 | 0 | 115.1988 | 361.9106 | 361.9106 | 0.027719 | 0.087082 | 0.087082 | -0.14007 | -0.44006 | -0.44006 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RT3 | RETAIL - MULTISTORY LARGE | New | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 2.89 | 0.019059 | 3.8119 | Fixture/1000 sf | 100.0995 | 314.4743 | 314.4743 | 0.022506 | 0.070706 | 0.070706 | 0 | 0 | 0 | 111.9413 | 351.6766 | 351.6766 | 0.026949 | 0.084663 | 0.084663 | -0.17502 | -0.54984 | -0.54984 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RT3 | RETAIL - MULTISTORY LARGE | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 2.89 | 0.019059 | 3.8119 | Fixture/1000 sf | 100.0921 | 314.451 | 314.451 | 0.022505 | 0.070702 | 0.070702 | 0 | 0 | 0 | 112.5336 | 353.5373 | 353.5373 | 0.027393 | 0.086058 | 0.086058 | -0.15992 | -0.5024 | -0.5024 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RT3 | RETAIL - MULTISTORY LARGE | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 2.89 | 0.019059 | 3.8119 | Fixture/1000 sf | 100.0973 | 314.4674 | 314.4674 | 0.022507 | 0.070707 | 0.070707 | 0 | 0 | 0 | 112.8297 | 354.4677 | 354.4677 | 0.027926 | 0.087733 | 0.087733 | -0.20404 | -0.64102 | -0.64102 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RT3 | RETAIL - MULTISTORY LARGE | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 2.89 | 0.019059 | 3.8119 | Fixture/1000 sf | 100.0987 | 314.4716 | 314.4716 | 0.02248 | 0.070622 | 0.070622 | 0 | 0 | 0 | 109.8683 | 345.1641 | 345.1641 | 0.027778 | 0.087268 | 0.087268 | -0.53009 | -1.6653 | -1.6653 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RT3 | RETAIL - MULTISTORY LARGE | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 2.89 | 0.019059 | 3.8119 | Fixture/1000 sf | 100.0927 | 314.4529 | 314.4529 | 0.022506 | 0.070706 | 0.070706 | 0 | 0 | 0 | 111.0529 | 348.8855 | 348.8855 | 0.029199 | 0.091734 | 0.091734 | -0.57451 | -1.8049 | -1.8049 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RT3 | RETAIL - MULTISTORY LARGE | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 2.89 | 0.019059 | 3.8119 | Fixture/1000 sf | 100.0955 | 314.4618 | 314.4618 | 0.022493 | 0.070665 | 0.070665 | 0 | 0 | 0 | 108.6837 | 341.4426 | 341.4426 | 0.027689 | 0.086989 | 0.086989 | -0.55971 | -1.7584 | -1.7584 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RT3 | RETAIL - MULTISTORY LARGE | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 2.89 | 0.019059 | 3.8119 | Fixture/1000 sf | 100.0927 | 314.4529 | 314.4529 | 0.022507 | 0.070708 | 0.070708 | 0 | 0 | 0 | 111.0529 | 348.8855 | 348.8855 | 0.029081 | 0.091361 | 0.091361 | -0.58932 | -1.8514 | -1.8514 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RT3 | RETAIL - MULTISTORY LARGE | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 2.89 | 0.019059 | 3.8119 | Fixture/1000 sf | 100.094 | 314.4569 | 314.4569 | 0.022504 | 0.070698 | 0.070698 | 0 | 0 | 0 | 116.6795 | 366.5624 | 366.5624 | 0.028015 | 0.088012 | 0.088012 | -0.036129 | -0.1135 | -0.1135 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RT3 | RETAIL - MULTISTORY LARGE | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 2.89 | 0.019059 | 3.8119 | Fixture/1000 sf | 100.0973 | 314.4674 | 314.4674 | 0.022508 | 0.07071 | 0.07071 | 0 | 0 | 0 | 112.8297 | 354.4677 | 354.4677 | 0.026534 | 0.08336 | 0.08336 | -0.021381 | -0.067172 | -0.067172 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RT3 | RETAIL - MULTISTORY LARGE | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 2.89 | 0.019059 | 3.8119 | Fixture/1000 sf | 100.0953 | 314.4612 | 314.4612 | 0.022479 | 0.070621 | 0.070621 | 0 | 0 | 0 | 98.6149 | 309.8103 | 309.8103 | 0.027067 | 0.085035 | 0.085035 | -1.2586 | -3.954 | -3.954 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RT3 | RETAIL - MULTISTORY LARGE | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 2.89 | 0.019059 | 3.8119 | Fixture/1000 sf | 100.0958 | 314.4626 | 314.4626 | 0.022507 | 0.07071 | 0.07071 | 0 | 0 | 0 | 99.7995 | 313.5318 | 313.5318 | 0.027837 | 0.087454 | 0.087454 | -1.2793 | -4.0192 | -4.0192 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RT3 | RETAIL - MULTISTORY LARGE | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 3.1602 | 0.018913 | 3.7827 | Fixture/1000 sf | 97.7965 | 315.6549 | 315.6549 | 0.021964 | 0.070892 | 0.070892 | 0 | 0 | 0 | 111.977 | 361.4248 | 361.4248 | 0.026822 | 0.086574 | 0.086574 | -0.093169 | -0.30072 | -0.30072 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RT3 | RETAIL - MULTISTORY LARGE | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 3.1602 | 0.018913 | 3.7827 | Fixture/1000 sf | 97.8006 | 315.6683 | 315.6683 | 0.021991 | 0.07098 | 0.07098 | 0 | 0 | 0 | 110.2409 | 355.8214 | 355.8214 | 0.027199 | 0.087788 | 0.087788 | -0.13194 | -0.42586 | -0.42586 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RT3 | RETAIL - MULTISTORY LARGE | Existing | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 3.1602 | 0.018913 | 3.7827 | Fixture/1000 sf | 97.7979 | 315.6596 | 315.6596 | 0.021963 | 0.07089 | 0.07089 | 0 | 0 | 0 | 112.5557 | 363.2927 | 363.2927 | 0.026417 | 0.085266 | 0.085266 | -0.040219 | -0.12981 | -0.12981 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RT3 | RETAIL - MULTISTORY LARGE | New | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 3.1602 | 0.018913 | 3.7827 | Fixture/1000 sf | 97.7955 | 315.6519 | 315.6519 | 0.02199 | 0.070976 | 0.070976 | 0 | 0 | 0 | 109.9515 | 354.8874 | 354.8874 | 0.026707 | 0.0862 | 0.0862 | -0.050925 | -0.16437 | -0.16437 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RT3 | RETAIL - MULTISTORY LARGE | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 3.1602 | 0.018913 | 3.7827 | Fixture/1000 sf | 97.795 | 315.6501 | 315.6501 | 0.02199 | 0.070976 | 0.070976 | 0 | 0 | 0 | 111.3983 | 359.557 | 359.557 | 0.02743 | 0.088535 | 0.088535 | -0.11024 | -0.35582 | -0.35582 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RT3 | RETAIL - MULTISTORY LARGE | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 3.1602 | 0.018913 | 3.7827 | Fixture/1000 sf | 97.7979 | 315.6596 | 315.6596 | 0.021963 | 0.070889 | 0.070889 | 0 | 0 | 0 | 112.5557 | 363.2927 | 363.2927 | 0.026562 | 0.085733 | 0.085733 | -0.083332 | -0.26897 | -0.26897 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RT3 | RETAIL - MULTISTORY LARGE | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 3.1602 | 0.018913 | 3.7827 | Fixture/1000 sf | 97.795 | 315.6501 | 315.6501 | 0.021963 | 0.070891 | 0.070891 | 0 | 0 | 0 | 111.3983 | 359.557 | 359.557 | 0.026938 | 0.086947 | 0.086947 | -0.1522 | -0.49124 | -0.49124 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RT3 | RETAIL - MULTISTORY LARGE | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 3.1602 | 0.018913 | 3.7827 | Fixture/1000 sf | 97.7955 | 315.6519 | 315.6519 | 0.02199 | 0.070975 | 0.070975 | 0 | 0 | 0 | 109.9515 | 354.8874 | 354.8874 | 0.027227 | 0.087881 | 0.087881 | -0.20312 | -0.65561 | -0.65561 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RT3 | RETAIL - MULTISTORY LARGE | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 3.1602 | 0.018913 | 3.7827 | Fixture/1000 sf | 97.7998 | 315.6656 | 315.6656 | 0.02199 | 0.070976 | 0.070976 | 0 | 0 | 0 | 108.2155 | 349.284 | 349.284 | 0.028356 | 0.091524 | 0.091524 | -0.59605 | -1.9239 | -1.9239 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RT3 | RETAIL - MULTISTORY LARGE | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 3.1602 | 0.018913 | 3.7827 | Fixture/1000 sf | 97.7952 | 315.6507 | 315.6507 | 0.021963 | 0.070891 | 0.070891 | 0 | 0 | 0 | 106.4794 | 343.6805 | 343.6805 | 0.027112 | 0.087508 | 0.087508 | -0.55554 | -1.7931 | -1.7931 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RT3 | RETAIL - MULTISTORY LARGE | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 3.1602 | 0.018913 | 3.7827 | Fixture/1000 sf | 97.8002 | 315.667 | 315.667 | 0.021978 | 0.070939 | 0.070939 | 0 | 0 | 0 | 115.1598 | 371.6979 | 371.6979 | 0.027517 | 0.088815 | 0.088815 | -0.035879 | -0.11581 | -0.11581 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RT3 | RETAIL - MULTISTORY LARGE | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 3.1602 | 0.018913 | 3.7827 | Fixture/1000 sf | 97.7955 | 315.6519 | 315.6519 | 0.021991 | 0.070978 | 0.070978 | 0 | 0 | 0 | 109.9515 | 354.8874 | 354.8874 | 0.025868 | 0.083492 | 0.083492 | -0.020399 | -0.065841 | -0.065841 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RTL | RETAIL - SINGLE-STORY LARGE | Existing | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 3.0977 | 0.024297 | 4.8593 | Fixture/1000 sf | 133.1233 | 366.469 | 366.469 | 0.026438 | 0.072781 | 0.072781 | 0 | 0 | 0 | 140.6049 | 387.0645 | 387.0645 | 0.031488 | 0.086682 | 0.086682 | -0.9384 | -2.5833 | -2.5833 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RTL | RETAIL - SINGLE-STORY LARGE | Existing | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 3.0977 | 0.024297 | 4.8593 | Fixture/1000 sf | 133.1213 | 366.4634 | 366.4634 | 0.026438 | 0.072781 | 0.072781 | 0 | 0 | 0 | 141.2284 | 388.781 | 388.781 | 0.031176 | 0.085824 | 0.085824 | -0.89476 | -2.4631 | -2.4631 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RTL | RETAIL - SINGLE-STORY LARGE | New | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 3.0977 | 0.024297 | 4.8593 | Fixture/1000 sf | 133.1209 | 366.4622 | 366.4622 | 0.026438 | 0.07278 | 0.07278 | 0 | 0 | 0 | 137.4872 | 378.4822 | 378.4822 | 0.032112 | 0.088398 | 0.088398 | -0.99452 | -2.7378 | -2.7378 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RTL | RETAIL - SINGLE-STORY LARGE | Existing | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 3.0977 | 0.024297 | 4.8593 | Fixture/1000 sf | 133.1257 | 366.4754 | 366.4754 | 0.026438 | 0.072781 | 0.072781 | 0 | 0 | 0 | 143.7225 | 395.6469 | 395.6469 | 0.031488 | 0.086682 | 0.086682 | -0.6547 | -1.8023 | -1.8023 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RTL | RETAIL - SINGLE-STORY LARGE | New | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 3.0977 | 0.024297 | 4.8593 | Fixture/1000 sf | 133.1173 | 366.4523 | 366.4523 | 0.026438 | 0.072779 | 0.072779 | 0 | 0 | 0 | 142.4754 | 392.2139 | 392.2139 | 0.032423 | 0.089257 | 0.089257 | -0.74199 | -2.0426 | -2.0426 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RTL | RETAIL - SINGLE-STORY LARGE | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 3.0977 | 0.024297 | 4.8593 | Fixture/1000 sf | 133.1233 | 366.469 | 366.469 | 0.026436 | 0.072775 | 0.072775 | 0 | 0 | 0 | 140.6049 | 387.0645 | 387.0645 | 0.030864 | 0.084965 | 0.084965 | -0.87917 | -2.4202 | -2.4202 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RTL | RETAIL - SINGLE-STORY LARGE | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 3.0977 | 0.024297 | 4.8593 | Fixture/1000 sf | 133.1263 | 366.477 | 366.477 | 0.026438 | 0.072781 | 0.072781 | 0 | 0 | 0 | 137.799 | 379.3404 | 379.3404 | 0.031176 | 0.085824 | 0.085824 | -1.0257 | -2.8236 | -2.8236 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RTL | RETAIL - SINGLE-STORY LARGE | Existing | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 3.0977 | 0.024297 | 4.8593 | Fixture/1000 sf | 133.1266 | 366.4778 | 366.4778 | 0.026438 | 0.07278 | 0.07278 | 0 | 0 | 0 | 141.5402 | 389.6392 | 389.6392 | 0.0318 | 0.08754 | 0.08754 | -0.90411 | -2.4889 | -2.4889 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RTL | RETAIL - SINGLE-STORY LARGE | New | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 3.0977 | 0.024297 | 4.8593 | Fixture/1000 sf | 133.1257 | 366.4754 | 366.4754 | 0.026437 | 0.072778 | 0.072778 | 0 | 0 | 0 | 143.7225 | 395.6469 | 395.6469 | 0.033047 | 0.090973 | 0.090973 | -0.95711 | -2.6348 | -2.6348 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RTL | RETAIL - SINGLE-STORY LARGE | Existing | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 3.0977 | 0.024297 | 4.8593 | Fixture/1000 sf | 133.1266 | 366.4778 | 366.4778 | 0.026438 | 0.07278 | 0.07278 | 0 | 0 | 0 | 141.5402 | 389.6392 | 389.6392 | 0.0318 | 0.08754 | 0.08754 | -0.82617 | -2.2743 | -2.2743 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RTL | RETAIL - SINGLE-STORY LARGE | New | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 3.0977 | 0.024297 | 4.8593 | Fixture/1000 sf | 133.1225 | 366.4667 | 366.4667 | 0.026437 | 0.072778 | 0.072778 | 0 | 0 | 0 | 142.7872 | 393.0722 | 393.0722 | 0.033359 | 0.091831 | 0.091831 | -0.9384 | -2.5833 | -2.5833 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RTL | RETAIL - SINGLE-STORY LARGE | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 3.0977 | 0.024297 | 4.8593 | Fixture/1000 sf | 133.1225 | 366.4667 | 366.4667 | 0.026438 | 0.07278 | 0.07278 | 0 | 0 | 0 | 142.7872 | 393.0722 | 393.0722 | 0.0318 | 0.08754 | 0.08754 | -0.80123 | -2.2057 | -2.2057 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RTL | RETAIL - SINGLE-STORY LARGE | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 3.0977 | 0.024297 | 4.8593 | Fixture/1000 sf | 133.1237 | 366.4699 | 366.4699 | 0.026437 | 0.072778 | 0.072778 | 0 | 0 | 0 | 144.346 | 397.3633 | 397.3633 | 0.033047 | 0.090973 | 0.090973 | -0.89164 | -2.4546 | -2.4546 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RTL | RETAIL - SINGLE-STORY LARGE | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 3.0977 | 0.024297 | 4.8593 | Fixture/1000 sf | 133.1224 | 366.4664 | 366.4664 | 0.026437 | 0.072776 | 0.072776 | 0 | 0 | 0 | 129.6932 | 357.0262 | 357.0262 | 0.030553 | 0.084107 | 0.084107 | -1.8238 | -5.0207 | -5.0207 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | PGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RTL | RETAIL - SINGLE-STORY LARGE | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 3.0977 | 0.024297 | 4.8593 | Fixture/1000 sf | 133.1224 | 366.4663 | 366.4663 | 0.026438 | 0.07278 | 0.07278 | 0 | 0 | 0 | 131.252 | 361.3174 | 361.3174 | 0.0318 | 0.08754 | 0.08754 | -1.9298 | -5.3125 | -5.3125 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RTL | RETAIL - SINGLE-STORY LARGE | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 2.89 | 0.019059 | 3.8119 | Fixture/1000 sf | 126.4502 | 397.2582 | 397.2582 | 0.025113 | 0.078896 | 0.078896 | 0 | 0 | 0 | 136.2248 | 427.9662 | 427.9662 | 0.030503 | 0.095827 | 0.095827 | -0.7522 | -2.3631 | -2.3631 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RTL | RETAIL - SINGLE-STORY LARGE | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 2.89 | 0.019059 | 3.8119 | Fixture/1000 sf | 126.4568 | 397.2789 | 397.2789 | 0.025113 | 0.078896 | 0.078896 | 0 | 0 | 0 | 132.375 | 415.8715 | 415.8715 | 0.030799 | 0.096758 | 0.096758 | -0.88842 | -2.7911 | -2.7911 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RTL | RETAIL - SINGLE-STORY LARGE | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 2.89 | 0.019059 | 3.8119 | Fixture/1000 sf | 126.4554 | 397.2744 | 397.2744 | 0.025112 | 0.078892 | 0.078892 | 0 | 0 | 0 | 140.0747 | 440.0609 | 440.0609 | 0.032872 | 0.10327 | 0.10327 | -0.77589 | -2.4375 | -2.4375 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RTL | RETAIL - SINGLE-STORY LARGE | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 2.89 | 0.019059 | 3.8119 | Fixture/1000 sf | 126.4465 | 397.2464 | 397.2464 | 0.025113 | 0.078894 | 0.078894 | 0 | 0 | 0 | 137.4094 | 431.6877 | 431.6877 | 0.031687 | 0.099549 | 0.099549 | -0.7137 | -2.2422 | -2.2422 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RTL | RETAIL - SINGLE-STORY LARGE | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 2.89 | 0.019059 | 3.8119 | Fixture/1000 sf | 126.4506 | 397.2594 | 397.2594 | 0.025112 | 0.078892 | 0.078892 | 0 | 0 | 0 | 139.7785 | 439.1305 | 439.1305 | 0.032872 | 0.10327 | 0.10327 | -0.78773 | -2.4748 | -2.4748 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RTL | RETAIL - SINGLE-STORY LARGE | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 2.89 | 0.019059 | 3.8119 | Fixture/1000 sf | 126.4542 | 397.2705 | 397.2705 | 0.025113 | 0.078894 | 0.078894 | 0 | 0 | 0 | 147.7743 | 464.2503 | 464.2503 | 0.031687 | 0.099549 | 0.099549 | -0.11846 | -0.37214 | -0.37214 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RTL | RETAIL - SINGLE-STORY LARGE | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 2.89 | 0.019059 | 3.8119 | Fixture/1000 sf | 126.4483 | 397.2521 | 397.2521 | 0.025114 | 0.078897 | 0.078897 | 0 | 0 | 0 | 151.6242 | 476.345 | 476.345 | 0.033464 | 0.10513 | 0.10513 | -0.11964 | -0.37587 | -0.37587 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RTL | RETAIL - SINGLE-STORY LARGE | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 2.89 | 0.019059 | 3.8119 | Fixture/1000 sf | 126.4528 | 397.2662 | 397.2662 | 0.025113 | 0.078897 | 0.078897 | 0 | 0 | 0 | 124.0831 | 389.8214 | 389.8214 | 0.030206 | 0.094897 | 0.094897 | -1.6169 | -5.0798 | -5.0798 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SCE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RTL | RETAIL - SINGLE-STORY LARGE | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 2.89 | 0.019059 | 3.8119 | Fixture/1000 sf | 126.4527 | 397.266 | 397.266 | 0.025113 | 0.078895 | 0.078895 | 0 | 0 | 0 | 125.5638 | 394.4732 | 394.4732 | 0.031095 | 0.097688 | 0.097688 | -1.7058 | -5.3589 | -5.3589 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RTL | RETAIL - SINGLE-STORY LARGE | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 3.1602 | 0.018913 | 3.7827 | Fixture/1000 sf | 123.5497 | 398.7777 | 398.7777 | 0.024537 | 0.079197 | 0.079197 | 0 | 0 | 0 | 140.0435 | 452.0145 | 452.0145 | 0.030092 | 0.097127 | 0.097127 | -0.29513 | -0.95259 | -0.95259 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RTL | RETAIL - SINGLE-STORY LARGE | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 3.1602 | 0.018913 | 3.7827 | Fixture/1000 sf | 123.554 | 398.7916 | 398.7916 | 0.024537 | 0.079196 | 0.079196 | 0 | 0 | 0 | 136.8607 | 441.7415 | 441.7415 | 0.030671 | 0.098995 | 0.098995 | -0.40508 | -1.3075 | -1.3075 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RTL | RETAIL - SINGLE-STORY LARGE | Existing | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 3.1602 | 0.018913 | 3.7827 | Fixture/1000 sf | 123.5525 | 398.7867 | 398.7867 | 0.024537 | 0.079197 | 0.079197 | 0 | 0 | 0 | 140.9116 | 454.8163 | 454.8163 | 0.030092 | 0.097127 | 0.097127 | -0.21498 | -0.6939 | -0.6939 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RTL | RETAIL - SINGLE-STORY LARGE | New | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 3.1602 | 0.018913 | 3.7827 | Fixture/1000 sf | 123.5529 | 398.7882 | 398.7882 | 0.024537 | 0.079198 | 0.079198 | 0 | 0 | 0 | 135.414 | 437.0719 | 437.0719 | 0.029513 | 0.095259 | 0.095259 | -0.29224 | -0.94325 | -0.94325 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RTL | RETAIL - SINGLE-STORY LARGE | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 3.1602 | 0.018913 | 3.7827 | Fixture/1000 sf | 123.5479 | 398.7721 | 398.7721 | 0.024537 | 0.079197 | 0.079197 | 0 | 0 | 0 | 140.6222 | 453.8824 | 453.8824 | 0.030092 | 0.097127 | 0.097127 | -0.25434 | -0.82091 | -0.82091 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RTL | RETAIL - SINGLE-STORY LARGE | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 3.1602 | 0.018913 | 3.7827 | Fixture/1000 sf | 123.5486 | 398.7743 | 398.7743 | 0.024536 | 0.079195 | 0.079195 | 0 | 0 | 0 | 138.5968 | 447.345 | 447.345 | 0.031249 | 0.10086 | 0.10086 | -0.34432 | -1.1114 | -1.1114 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Replacing T8) - Emerging | LED fixture: 33W, 3500 lumens | LF fixture: T8, 48inch, 32W lamp (2), Total fixture Watts = 59; Ballast specs: Instant Start, Electronic, NLO, 2 per lamp; Lamp specs: 3175 lumens, CRI=70, rated hours = 20000 | LF fixture: T8, 48inch, 2970 lumens, 32W lamp(s), Total average fixture Watts = 90; Ballast specs: Instant Start, Electronic, NLO | Lighting | InGen | Ltg_Wired | LinFluor_fixt | T8 to LED | 1 | 1 | 0 | 0.8 |  | 2011 | 1 | Linear Fluorescent | Fixture | RTL | RETAIL - SINGLE-STORY LARGE | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 3.1602 | 0.018913 | 3.7827 | Fixture/1000 sf | 123.5514 | 398.7834 | 398.7834 | 0.024537 | 0.079196 | 0.079196 | 0 | 0 | 0 | 139.4648 | 450.1467 | 450.1467 | 0.030671 | 0.098995 | 0.098995 | -0.33853 | -1.0927 | -1.0927 | 200 | 16 | 16 | 16 | 5.3333 | 0.5 | 313.7462 | 20.05 | 20.05 | 137.8003 | 137.8003 | 137.8003 | 0 | 0 | 0.2 | 1 | 1 | 0 | 0 | [7 empty] | LED Luminaire - General Service | None | None | LED Luminaire - General Service | 0 | 0 | 0 | Lighting - LED Fixture
| Lighting - LED Fixture (Replacing T8) - Emerging | SDGE | COM | Electric | COMLighting - LED Fixture (Repla
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