M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFS | OFFICE - SMALL | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.16578 | 0.0092117 | 0.1842 | Cap-Tons/1000 sf | 5917.5 | 7177.5 | 6085.5 | 0.17183 | 0.97883 | 0.27883 | 0 | 0 | 0 | 5917.5 | 7177.5 | 6085.5 | 0.17183 | 0.97883 | 0.27883 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.29153 | 0.0162 | 0.32393 | Cap-Tons/1000 sf | 13660 | 15840 | 13968 | 0.12464 | 0.90564 | 0.23064 | 0 | 0 | 0 | 13660 | 15840 | 13968 | 0.12464 | 0.90564 | 0.23064 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.19242 | 0.010692 | 0.2138 | Cap-Tons/1000 sf | 14040 | 15840 | 14290 | 0.11077 | 0.97477 | 0.22677 | 0 | 0 | 0 | 14040 | 15840 | 14290 | 0.11077 | 0.97477 | 0.22677 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.083367 | 0.0046324 | 0.092632 | Cap-Tons/1000 sf | 4477.5 | 6077.5 | 4723.5 | 0.27372 | 1.0397 | 0.39072 | 0 | 0 | 0 | 4477.5 | 6077.5 | 4723.5 | 0.27372 | 1.0397 | 0.39072 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.10107 | 0.0056162 | 0.1123 | Cap-Tons/1000 sf | 4457.5 | 6077.5 | 4709.5 | 0.26676 | 1.0008 | 0.37776 | 0 | 0 | 0 | 4457.5 | 6077.5 | 4709.5 | 0.26676 | 1.0008 | 0.37776 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.1869 | 0.010385 | 0.20767 | Cap-Tons/1000 sf | 10341.5 | 10642.5 | 10642.5 | 0.0025148 | 0.088915 | 0.088915 | 0 | 0 | 0 | 10341.5 | 10642.5 | 10642.5 | 0.0025148 | 0.088915 | 0.088915 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HTL | LODGING - HOTEL | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.10457 | 0.0058107 | 0.11619 | Cap-Tons/1000 sf | 6253.5 | 6627.5 | 6627.5 | 0.0075954 | 0.1346 | 0.1346 | 0 | 0 | 0 | 6253.5 | 6627.5 | 6627.5 | 0.0075954 | 0.1346 | 0.1346 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | MTL | LODGING - MOTEL | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.10457 | 0.0058107 | 0.11619 | Cap-Tons/1000 sf | 6253.5 | 6627.5 | 6627.5 | 0.0075954 | 0.1346 | 0.1346 | 0 | 0 | 0 | 6253.5 | 6627.5 | 6627.5 | 0.0075954 | 0.1346 | 0.1346 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.12949 | 0.0071952 | 0.14388 | Cap-Tons/1000 sf | 3872.5 | 5252.5 | 4093.5 | 0.31645 | 1.2044 | 0.45045 | 0 | 0 | 0 | 3872.5 | 5252.5 | 4093.5 | 0.31645 | 1.2044 | 0.45045 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.15684 | 0.0087149 | 0.17427 | Cap-Tons/1000 sf | 1930.5 | 3217.5 | 2115.5 | 0.212 | 0.53 | 0.2539 | 0 | 0 | 0 | 1930.5 | 3217.5 | 2115.5 | 0.212 | 0.53 | 0.2539 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.18544 | 0.010304 | 0.20605 | Cap-Tons/1000 sf | 4122.5 | 5252.5 | 4389.5 | 0.095389 | 0.44339 | 0.16009 | 0 | 0 | 0 | 4122.5 | 5252.5 | 4389.5 | 0.095389 | 0.44339 | 0.16009 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.12957 | 0.0088032 | 0.14717 | Cap-Tons/1000 sf | 4856.5 | 5252.5 | 5252.5 | 0.010274 | 0.13627 | 0.13627 | 0 | 0 | 0 | 4856.5 | 5252.5 | 5252.5 | 0.010274 | 0.13627 | 0.13627 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.14709 | 0.0099939 | 0.16708 | Cap-Tons/1000 sf | 2874.5 | 3217.5 | 3217.5 | 0.0011825 | 0.011093 | 0.011093 | 0 | 0 | 0 | 2874.5 | 3217.5 | 3217.5 | 0.0011825 | 0.011093 | 0.011093 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.17624 | 0.011975 | 0.20019 | Cap-Tons/1000 sf | 4798.5 | 5252.5 | 5252.5 | 0.0050239 | 0.058124 | 0.058124 | 0 | 0 | 0 | 4798.5 | 5252.5 | 5252.5 | 0.0050239 | 0.058124 | 0.058124 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.14499 | 0.0098513 | 0.16469 | Cap-Tons/1000 sf | 2786.5 | 3217.5 | 3217.5 | 0.0015065 | 0.011247 | 0.011247 | 0 | 0 | 0 | 2786.5 | 3217.5 | 3217.5 | 0.0015065 | 0.011247 | 0.011247 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EUN | EDUCATION - UNIVERSITY | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.12971 | 0.0088131 | 0.14734 | Cap-Tons/1000 sf | 4934.5 | 5252.5 | 5252.5 | 0.0080555 | 0.13306 | 0.13306 | 0 | 0 | 0 | 4934.5 | 5252.5 | 5252.5 | 0.0080555 | 0.13306 | 0.13306 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | GRO | GROCERY | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.2306 | 0.015668 | 0.26194 | Cap-Tons/1000 sf | 7210 | 7920 | 7920 | 0.010635 | 0.11864 | 0.11864 | 0 | 0 | 0 | 7210 | 7920 | 7920 | 0.010635 | 0.11864 | 0.11864 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.18386 | 0.012492 | 0.20884 | Cap-Tons/1000 sf | 10289.5 | 10642.5 | 10642.5 | 0.0029161 | 0.087916 | 0.087916 | 0 | 0 | 0 | 10289.5 | 10642.5 | 10642.5 | 0.0029161 | 0.087916 | 0.087916 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HTL | LODGING - HOTEL | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.10324 | 0.0070147 | 0.11727 | Cap-Tons/1000 sf | 6112.5 | 6627.5 | 6627.5 | 0.010447 | 0.13445 | 0.13445 | 0 | 0 | 0 | 6112.5 | 6627.5 | 6627.5 | 0.010447 | 0.13445 | 0.13445 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | MTL | LODGING - MOTEL | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.10324 | 0.0070147 | 0.11727 | Cap-Tons/1000 sf | 6112.5 | 6627.5 | 6627.5 | 0.010447 | 0.13445 | 0.13445 | 0 | 0 | 0 | 6112.5 | 6627.5 | 6627.5 | 0.010447 | 0.13445 | 0.13445 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.18386 | 0.012492 | 0.20884 | Cap-Tons/1000 sf | 10038.5 | 10642.5 | 10642.5 | 0.0045367 | 0.079937 | 0.079937 | 0 | 0 | 0 | 10038.5 | 10642.5 | 10642.5 | 0.0045367 | 0.079937 | 0.079937 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFL | OFFICE - LARGE | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.13686 | 0.009299 | 0.15546 | Cap-Tons/1000 sf | 9628.5 | 9817.5 | 9817.5 | 0.0025714 | 0.13357 | 0.13357 | 0 | 0 | 0 | 9628.5 | 9817.5 | 9817.5 | 0.0025714 | 0.13357 | 0.13357 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFS | OFFICE - SMALL | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.15528 | 0.01055 | 0.17638 | Cap-Tons/1000 sf | 6957.5 | 7177.5 | 7177.5 | 0.0043004 | 0.1403 | 0.1403 | 0 | 0 | 0 | 6957.5 | 7177.5 | 7177.5 | 0.0043004 | 0.1403 | 0.1403 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.27074 | 0.018395 | 0.30753 | Cap-Tons/1000 sf | 15069 | 15840 | 15840 | 0.0059863 | 0.12299 | 0.12299 | 0 | 0 | 0 | 15069 | 15840 | 15840 | 0.0059863 | 0.12299 | 0.12299 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.18244 | 0.012395 | 0.20723 | Cap-Tons/1000 sf | 15186 | 15840 | 15840 | 0.0063738 | 0.15437 | 0.15437 | 0 | 0 | 0 | 15186 | 15840 | 15840 | 0.0063738 | 0.15437 | 0.15437 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.083286 | 0.0056587 | 0.094603 | Cap-Tons/1000 sf | 5477.5 | 6077.5 | 6077.5 | 0.016759 | 0.16976 | 0.16976 | 0 | 0 | 0 | 5477.5 | 6077.5 | 6077.5 | 0.016759 | 0.16976 | 0.16976 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.096963 | 0.006588 | 0.11014 | Cap-Tons/1000 sf | 5466.5 | 6077.5 | 6077.5 | 0.01643 | 0.16343 | 0.16343 | 0 | 0 | 0 | 5466.5 | 6077.5 | 6077.5 | 0.01643 | 0.16343 | 0.16343 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTS | RETAIL - SMALL | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.10735 | 0.0072936 | 0.12193 | Cap-Tons/1000 sf | 5618.5 | 6077.5 | 6077.5 | 0.011764 | 0.15576 | 0.15576 | 0 | 0 | 0 | 5618.5 | 6077.5 | 6077.5 | 0.011764 | 0.15576 | 0.15576 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | SCN | STORAGE - CONDITIONED | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.058722 | 0.0039897 | 0.066701 | Cap-Tons/1000 sf | 868.5 | 1307.5 | 1307.5 | 0.039679 | 0.11818 | 0.11818 | 0 | 0 | 0 | 868.5 | 1307.5 | 1307.5 | 0.039679 | 0.11818 | 0.11818 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ASM | ASSEMBLY | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.22348 | 0.012418 | 0.24831 | Cap-Tons/1000 sf | 2685.5 | 3965.5 | 2908.5 | 0.29075 | 0.90075 | 0.38875 | 0 | 0 | 0 | 2685.5 | 3965.5 | 2908.5 | 0.29075 | 0.90075 | 0.38875 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.12949 | 0.0071952 | 0.14388 | Cap-Tons/1000 sf | 4142.5 | 5252.5 | 4308.5 | 0.13746 | 0.65046 | 0.21196 | 0 | 0 | 0 | 4142.5 | 5252.5 | 4308.5 | 0.13746 | 0.65046 | 0.21196 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.15684 | 0.0087149 | 0.17427 | Cap-Tons/1000 sf | 2458.5 | 3217.5 | 2564.5 | 0.0093852 | 0.039785 | 0.013275 | 0 | 0 | 0 | 2458.5 | 3217.5 | 2564.5 | 0.0093852 | 0.039785 | 0.013275 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.18544 | 0.010304 | 0.20605 | Cap-Tons/1000 sf | 4649.5 | 5252.5 | 4788.5 | 0.015822 | 0.13782 | 0.038322 | 0 | 0 | 0 | 4649.5 | 5252.5 | 4788.5 | 0.015822 | 0.13782 | 0.038322 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.1526 | 0.0084793 | 0.16956 | Cap-Tons/1000 sf | 2401.5 | 3217.5 | 2516.5 | 0.0060822 | 0.023982 | 0.0083022 | 0 | 0 | 0 | 2401.5 | 3217.5 | 2516.5 | 0.0060822 | 0.023982 | 0.0083022 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EUN | EDUCATION - UNIVERSITY | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.13025 | 0.0072376 | 0.14473 | Cap-Tons/1000 sf | 4022.5 | 5252.5 | 4210.5 | 0.15472 | 0.66072 | 0.23082 | 0 | 0 | 0 | 4022.5 | 5252.5 | 4210.5 | 0.15472 | 0.66072 | 0.23082 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | GRO | GROCERY | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.23968 | 0.013318 | 0.26631 | Cap-Tons/1000 sf | 6210 | 7920 | 6543 | 0.085087 | 0.39409 | 0.13549 | 0 | 0 | 0 | 6210 | 7920 | 6543 | 0.085087 | 0.39409 | 0.13549 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.1869 | 0.010385 | 0.20767 | Cap-Tons/1000 sf | 8762.5 | 10642.5 | 9033.5 | 0.10105 | 0.57205 | 0.16775 | 0 | 0 | 0 | 8762.5 | 10642.5 | 9033.5 | 0.10105 | 0.57205 | 0.16775 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HTL | LODGING - HOTEL | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.10457 | 0.0058107 | 0.11619 | Cap-Tons/1000 sf | 4757.5 | 6627.5 | 5058.5 | 0.21933 | 0.77733 | 0.30663 | 0 | 0 | 0 | 4757.5 | 6627.5 | 5058.5 | 0.21933 | 0.77733 | 0.30663 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | MTL | LODGING - MOTEL | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.10457 | 0.0058107 | 0.11619 | Cap-Tons/1000 sf | 4757.5 | 6627.5 | 5058.5 | 0.21933 | 0.77733 | 0.30663 | 0 | 0 | 0 | 4757.5 | 6627.5 | 5058.5 | 0.21933 | 0.77733 | 0.30663 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.1869 | 0.010385 | 0.20767 | Cap-Tons/1000 sf | 8882.5 | 10642.5 | 9144.5 | 0.081833 | 0.49483 | 0.13963 | 0 | 0 | 0 | 8882.5 | 10642.5 | 9144.5 | 0.081833 | 0.49483 | 0.13963 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFL | OFFICE - LARGE | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.13653 | 0.0075866 | 0.1517 | Cap-Tons/1000 sf | 8707.5 | 9817.5 | 8890.5 | 0.06718 | 0.59418 | 0.15428 | 0 | 0 | 0 | 8707.5 | 9817.5 | 8890.5 | 0.06718 | 0.59418 | 0.15428 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFS | OFFICE - SMALL | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.16578 | 0.0092117 | 0.1842 | Cap-Tons/1000 sf | 6067.5 | 7177.5 | 6215.5 | 0.10775 | 0.69675 | 0.18625 | 0 | 0 | 0 | 6067.5 | 7177.5 | 6215.5 | 0.10775 | 0.69675 | 0.18625 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.29153 | 0.0162 | 0.32393 | Cap-Tons/1000 sf | 13800 | 15840 | 14087 | 0.085296 | 0.6623 | 0.1627 | 0 | 0 | 0 | 13800 | 15840 | 14087 | 0.085296 | 0.6623 | 0.1627 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.19242 | 0.010692 | 0.2138 | Cap-Tons/1000 sf | 14190 | 15840 | 14422 | 0.081512 | 0.78251 | 0.17581 | 0 | 0 | 0 | 14190 | 15840 | 14422 | 0.081512 | 0.78251 | 0.17581 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.083367 | 0.0046324 | 0.092632 | Cap-Tons/1000 sf | 4887.5 | 6077.5 | 5069.5 | 0.14463 | 0.73863 | 0.23543 | 0 | 0 | 0 | 4887.5 | 6077.5 | 5069.5 | 0.14463 | 0.73863 | 0.23543 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.10107 | 0.0056162 | 0.1123 | Cap-Tons/1000 sf | 4627.5 | 6077.5 | 4857.5 | 0.20555 | 0.86155 | 0.30555 | 0 | 0 | 0 | 4627.5 | 6077.5 | 4857.5 | 0.20555 | 0.86155 | 0.30555 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTS | RETAIL - SMALL | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.10985 | 0.0061039 | 0.12206 | Cap-Tons/1000 sf | 4757.5 | 6077.5 | 4962.5 | 0.18617 | 0.85717 | 0.28917 | 0 | 0 | 0 | 4757.5 | 6077.5 | 4962.5 | 0.18617 | 0.85717 | 0.28917 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | SCN | STORAGE - CONDITIONED | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.060165 | 0.0033432 | 0.066851 | Cap-Tons/1000 sf | 922.5 | 1307.5 | 992.1 | 0.10809 | 0.36709 | 0.14859 | 0 | 0 | 0 | 922.5 | 1307.5 | 992.1 | 0.10809 | 0.36709 | 0.14859 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ASM | ASSEMBLY | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.22348 | 0.012418 | 0.24831 | Cap-Tons/1000 sf | 3749.5 | 3965.5 | 3965.5 | 0.0057089 | 0.10481 | 0.10481 | 0 | 0 | 0 | 3749.5 | 3965.5 | 3965.5 | 0.0057089 | 0.10481 | 0.10481 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.12949 | 0.0071952 | 0.14388 | Cap-Tons/1000 sf | 5114.5 | 5252.5 | 5252.5 | 0.0017727 | 0.067473 | 0.067473 | 0 | 0 | 0 | 5114.5 | 5252.5 | 5252.5 | 0.0017727 | 0.067473 | 0.067473 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTS | RETAIL - SMALL | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.10985 | 0.0061039 | 0.12206 | Cap-Tons/1000 sf | 4637.5 | 6077.5 | 4860.5 | 0.22761 | 0.96061 | 0.33961 | 0 | 0 | 0 | 4637.5 | 6077.5 | 4860.5 | 0.22761 | 0.96061 | 0.33961 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | SCN | STORAGE - CONDITIONED | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.060165 | 0.0033432 | 0.066851 | Cap-Tons/1000 sf | 784.5 | 1307.5 | 881.6 | 0.30933 | 0.77333 | 0.38163 | 0 | 0 | 0 | 784.5 | 1307.5 | 881.6 | 0.30933 | 0.77333 | 0.38163 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ASM | ASSEMBLY | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.22348 | 0.012418 | 0.24831 | Cap-Tons/1000 sf | 3736.5 | 3965.5 | 3965.5 | 0.0063126 | 0.10931 | 0.10931 | 0 | 0 | 0 | 3736.5 | 3965.5 | 3965.5 | 0.0063126 | 0.10931 | 0.10931 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.12949 | 0.0071952 | 0.14388 | Cap-Tons/1000 sf | 5042.5 | 5252.5 | 5252.5 | 0.0056639 | 0.14166 | 0.14166 | 0 | 0 | 0 | 5042.5 | 5252.5 | 5252.5 | 0.0056639 | 0.14166 | 0.14166 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.15684 | 0.0087149 | 0.17427 | Cap-Tons/1000 sf | 3078.5 | 3217.5 | 3217.5 | 0.0051925 | 0.12019 | 0.12019 | 0 | 0 | 0 | 3078.5 | 3217.5 | 3217.5 | 0.0051925 | 0.12019 | 0.12019 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.18544 | 0.010304 | 0.20605 | Cap-Tons/1000 sf | 5073.5 | 5252.5 | 5252.5 | 0.0040221 | 0.11802 | 0.11802 | 0 | 0 | 0 | 5073.5 | 5252.5 | 5252.5 | 0.0040221 | 0.11802 | 0.11802 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.1526 | 0.0084793 | 0.16956 | Cap-Tons/1000 sf | 3075.5 | 3217.5 | 3217.5 | 0.0055867 | 0.12659 | 0.12659 | 0 | 0 | 0 | 3075.5 | 3217.5 | 3217.5 | 0.0055867 | 0.12659 | 0.12659 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EUN | EDUCATION - UNIVERSITY | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.13025 | 0.0072376 | 0.14473 | Cap-Tons/1000 sf | 5005.5 | 5252.5 | 5252.5 | 0.0070564 | 0.15006 | 0.15006 | 0 | 0 | 0 | 5005.5 | 5252.5 | 5252.5 | 0.0070564 | 0.15006 | 0.15006 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | GRO | GROCERY | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.23968 | 0.013318 | 0.26631 | Cap-Tons/1000 sf | 7637 | 7920 | 7920 | 0.0034277 | 0.095928 | 0.095928 | 0 | 0 | 0 | 7637 | 7920 | 7920 | 0.0034277 | 0.095928 | 0.095928 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EUN | EDUCATION - UNIVERSITY | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.13025 | 0.0072376 | 0.14473 | Cap-Tons/1000 sf | 5047.5 | 5252.5 | 5252.5 | 0.0036512 | 0.093551 | 0.093551 | 0 | 0 | 0 | 5047.5 | 5252.5 | 5252.5 | 0.0036512 | 0.093551 | 0.093551 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | GRO | GROCERY | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.23968 | 0.013318 | 0.26631 | Cap-Tons/1000 sf | 7653 | 7920 | 7920 | 0.0027492 | 0.081549 | 0.081549 | 0 | 0 | 0 | 7653 | 7920 | 7920 | 0.0027492 | 0.081549 | 0.081549 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.1869 | 0.010385 | 0.20767 | Cap-Tons/1000 sf | 10369.5 | 10642.5 | 10642.5 | 0.0018561 | 0.072356 | 0.072356 | 0 | 0 | 0 | 10369.5 | 10642.5 | 10642.5 | 0.0018561 | 0.072356 | 0.072356 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HTL | LODGING - HOTEL | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.10457 | 0.0058107 | 0.11619 | Cap-Tons/1000 sf | 6332.5 | 6627.5 | 6627.5 | 0.0042672 | 0.095867 | 0.095867 | 0 | 0 | 0 | 6332.5 | 6627.5 | 6627.5 | 0.0042672 | 0.095867 | 0.095867 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | MTL | LODGING - MOTEL | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.10457 | 0.0058107 | 0.11619 | Cap-Tons/1000 sf | 6332.5 | 6627.5 | 6627.5 | 0.0042672 | 0.095867 | 0.095867 | 0 | 0 | 0 | 6332.5 | 6627.5 | 6627.5 | 0.0042672 | 0.095867 | 0.095867 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.1869 | 0.010385 | 0.20767 | Cap-Tons/1000 sf | 10418.5 | 10642.5 | 10642.5 | 0.0010815 | 0.051381 | 0.051381 | 0 | 0 | 0 | 10418.5 | 10642.5 | 10642.5 | 0.0010815 | 0.051381 | 0.051381 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFL | OFFICE - LARGE | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.13653 | 0.0075866 | 0.1517 | Cap-Tons/1000 sf | 9595.5 | 9817.5 | 9817.5 | 0.0024987 | 0.1105 | 0.1105 | 0 | 0 | 0 | 9595.5 | 9817.5 | 9817.5 | 0.0024987 | 0.1105 | 0.1105 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFS | OFFICE - SMALL | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.16578 | 0.0092117 | 0.1842 | Cap-Tons/1000 sf | 7009.5 | 7177.5 | 7177.5 | 0.0022889 | 0.097789 | 0.097789 | 0 | 0 | 0 | 7009.5 | 7177.5 | 7177.5 | 0.0022889 | 0.097789 | 0.097789 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.29153 | 0.0162 | 0.32393 | Cap-Tons/1000 sf | 15551 | 15840 | 15840 | 0.0015573 | 0.085357 | 0.085357 | 0 | 0 | 0 | 15551 | 15840 | 15840 | 0.0015573 | 0.085357 | 0.085357 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.19242 | 0.010692 | 0.2138 | Cap-Tons/1000 sf | 15606 | 15840 | 15840 | 0.0014994 | 0.1015 | 0.1015 | 0 | 0 | 0 | 15606 | 15840 | 15840 | 0.0014994 | 0.1015 | 0.1015 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.083367 | 0.0046324 | 0.092632 | Cap-Tons/1000 sf | 5883.5 | 6077.5 | 6077.5 | 0.0034952 | 0.1095 | 0.1095 | 0 | 0 | 0 | 5883.5 | 6077.5 | 6077.5 | 0.0034952 | 0.1095 | 0.1095 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.10107 | 0.0056162 | 0.1123 | Cap-Tons/1000 sf | 5827.5 | 6077.5 | 6077.5 | 0.0050193 | 0.12202 | 0.12202 | 0 | 0 | 0 | 5827.5 | 6077.5 | 6077.5 | 0.0050193 | 0.12202 | 0.12202 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTS | RETAIL - SMALL | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.10985 | 0.0061039 | 0.12206 | Cap-Tons/1000 sf | 5838.5 | 6077.5 | 6077.5 | 0.0051578 | 0.13116 | 0.13116 | 0 | 0 | 0 | 5838.5 | 6077.5 | 6077.5 | 0.0051578 | 0.13116 | 0.13116 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | SCN | STORAGE - CONDITIONED | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.060165 | 0.0033432 | 0.066851 | Cap-Tons/1000 sf | 1237.6 | 1307.5 | 1307.5 | 0.0021463 | 0.040146 | 0.040146 | 0 | 0 | 0 | 1237.6 | 1307.5 | 1307.5 | 0.0021463 | 0.040146 | 0.040146 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ASM | ASSEMBLY | Existing | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.22348 | 0.012418 | 0.24831 | Cap-Tons/1000 sf | 2815.5 | 3965.5 | 3012.5 | 0.23813 | 0.82113 | 0.33173 | 0 | 0 | 0 | 2815.5 | 3965.5 | 3012.5 | 0.23813 | 0.82113 | 0.33173 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | Existing | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.12949 | 0.0071952 | 0.14388 | Cap-Tons/1000 sf | 4102.5 | 5252.5 | 4278.5 | 0.20155 | 0.92055 | 0.31055 | 0 | 0 | 0 | 4102.5 | 5252.5 | 4278.5 | 0.20155 | 0.92055 | 0.31055 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | Existing | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.15684 | 0.0087149 | 0.17427 | Cap-Tons/1000 sf | 2275.5 | 3217.5 | 2406.5 | 0.30634 | 1.0463 | 0.40604 | 0 | 0 | 0 | 2275.5 | 3217.5 | 2406.5 | 0.30634 | 1.0463 | 0.40604 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | Existing | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.18544 | 0.010304 | 0.20605 | Cap-Tons/1000 sf | 4491.5 | 5252.5 | 4660.5 | 0.084377 | 0.58238 | 0.17728 | 0 | 0 | 0 | 4491.5 | 5252.5 | 4660.5 | 0.084377 | 0.58238 | 0.17728 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | Existing | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.1526 | 0.0084793 | 0.16956 | Cap-Tons/1000 sf | 2241.5 | 3217.5 | 2377.5 | 0.35356 | 1.1656 | 0.46256 | 0 | 0 | 0 | 2241.5 | 3217.5 | 2377.5 | 0.35356 | 1.1656 | 0.46256 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EUN | EDUCATION - UNIVERSITY | Existing | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.13025 | 0.0072376 | 0.14473 | Cap-Tons/1000 sf | 3892.5 | 5252.5 | 4098.5 | 0.25645 | 0.99045 | 0.36745 | 0 | 0 | 0 | 3892.5 | 5252.5 | 4098.5 | 0.25645 | 0.99045 | 0.36745 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | GRO | GROCERY | Existing | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.23968 | 0.013318 | 0.26631 | Cap-Tons/1000 sf | 6540 | 7920 | 6808 | 0.060771 | 0.34877 | 0.10797 | 0 | 0 | 0 | 6540 | 7920 | 6808 | 0.060771 | 0.34877 | 0.10797 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | Existing | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.1869 | 0.010385 | 0.20767 | Cap-Tons/1000 sf | 8862.5 | 10642.5 | 9118.5 | 0.090783 | 0.54278 | 0.15488 | 0 | 0 | 0 | 8862.5 | 10642.5 | 9118.5 | 0.090783 | 0.54278 | 0.15488 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HTL | LODGING - HOTEL | Existing | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.10457 | 0.0058107 | 0.11619 | Cap-Tons/1000 sf | 4587.5 | 6627.5 | 4917.5 | 0.28149 | 0.91449 | 0.38149 | 0 | 0 | 0 | 4587.5 | 6627.5 | 4917.5 | 0.28149 | 0.91449 | 0.38149 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | MTL | LODGING - MOTEL | Existing | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.10457 | 0.0058107 | 0.11619 | Cap-Tons/1000 sf | 4587.5 | 6627.5 | 4917.5 | 0.28149 | 0.91449 | 0.38149 | 0 | 0 | 0 | 4587.5 | 6627.5 | 4917.5 | 0.28149 | 0.91449 | 0.38149 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | Existing | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.1869 | 0.010385 | 0.20767 | Cap-Tons/1000 sf | 8862.5 | 10642.5 | 9128.5 | 0.093394 | 0.55839 | 0.15889 | 0 | 0 | 0 | 8862.5 | 10642.5 | 9128.5 | 0.093394 | 0.55839 | 0.15889 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFL | OFFICE - LARGE | Existing | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.13653 | 0.0075866 | 0.1517 | Cap-Tons/1000 sf | 8687.5 | 9817.5 | 8872.5 | 0.073751 | 0.64075 | 0.16705 | 0 | 0 | 0 | 8687.5 | 9817.5 | 8872.5 | 0.073751 | 0.64075 | 0.16705 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFS | OFFICE - SMALL | Existing | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.16578 | 0.0092117 | 0.1842 | Cap-Tons/1000 sf | 5957.5 | 7177.5 | 6119.5 | 0.13987 | 0.82287 | 0.23097 | 0 | 0 | 0 | 5957.5 | 7177.5 | 6119.5 | 0.13987 | 0.82287 | 0.23097 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | Existing | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.29153 | 0.0162 | 0.32393 | Cap-Tons/1000 sf | 13650 | 15840 | 13959 | 0.11199 | 0.80999 | 0.20639 | 0 | 0 | 0 | 13650 | 15840 | 13959 | 0.11199 | 0.80999 | 0.20639 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | Existing | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.19242 | 0.010692 | 0.2138 | Cap-Tons/1000 sf | 14140 | 15840 | 14376 | 0.094498 | 0.8805 | 0.2005 | 0 | 0 | 0 | 14140 | 15840 | 14376 | 0.094498 | 0.8805 | 0.2005 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | Existing | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.083367 | 0.0046324 | 0.092632 | Cap-Tons/1000 sf | 4817.5 | 6077.5 | 5009.5 | 0.16111 | 0.77711 | 0.25531 | 0 | 0 | 0 | 4817.5 | 6077.5 | 5009.5 | 0.16111 | 0.77711 | 0.25531 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | SCN | STORAGE - CONDITIONED | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.060165 | 0.0033432 | 0.066851 | Cap-Tons/1000 sf | 784.5 | 1307.5 | 909.5 | 0.48867 | 1.2217 | 0.60167 | 0 | 0 | 0 | 784.5 | 1307.5 | 909.5 | 0.48867 | 1.2217 | 0.60167 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ASM | ASSEMBLY | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.22348 | 0.012418 | 0.24831 | Cap-Tons/1000 sf | 3663.5 | 3965.5 | 3965.5 | 0.01319 | 0.17319 | 0.17319 | 0 | 0 | 0 | 3663.5 | 3965.5 | 3965.5 | 0.01319 | 0.17319 | 0.17319 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.12949 | 0.0071952 | 0.14388 | Cap-Tons/1000 sf | 5016.5 | 5252.5 | 5252.5 | 0.0074801 | 0.16648 | 0.16648 | 0 | 0 | 0 | 5016.5 | 5252.5 | 5252.5 | 0.0074801 | 0.16648 | 0.16648 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.15684 | 0.0087149 | 0.17427 | Cap-Tons/1000 sf | 3069.5 | 3217.5 | 3217.5 | 0.0013597 | 0.02956 | 0.02956 | 0 | 0 | 0 | 3069.5 | 3217.5 | 3217.5 | 0.0013597 | 0.02956 | 0.02956 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.18544 | 0.010304 | 0.20605 | Cap-Tons/1000 sf | 5066.5 | 5252.5 | 5252.5 | 0.0020118 | 0.056812 | 0.056812 | 0 | 0 | 0 | 5066.5 | 5252.5 | 5252.5 | 0.0020118 | 0.056812 | 0.056812 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.1526 | 0.0084793 | 0.16956 | Cap-Tons/1000 sf | 3055.5 | 3217.5 | 3217.5 | 0.0015906 | 0.031591 | 0.031591 | 0 | 0 | 0 | 3055.5 | 3217.5 | 3217.5 | 0.0015906 | 0.031591 | 0.031591 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.1869 | 0.010385 | 0.20767 | Cap-Tons/1000 sf | 10305.5 | 10642.5 | 10642.5 | 0.0036298 | 0.11463 | 0.11463 | 0 | 0 | 0 | 10305.5 | 10642.5 | 10642.5 | 0.0036298 | 0.11463 | 0.11463 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HTL | LODGING - HOTEL | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.10457 | 0.0058107 | 0.11619 | Cap-Tons/1000 sf | 6173.5 | 6627.5 | 6627.5 | 0.011105 | 0.1621 | 0.1621 | 0 | 0 | 0 | 6173.5 | 6627.5 | 6627.5 | 0.011105 | 0.1621 | 0.1621 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | MTL | LODGING - MOTEL | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.10457 | 0.0058107 | 0.11619 | Cap-Tons/1000 sf | 6173.5 | 6627.5 | 6627.5 | 0.011105 | 0.1621 | 0.1621 | 0 | 0 | 0 | 6173.5 | 6627.5 | 6627.5 | 0.011105 | 0.1621 | 0.1621 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.1869 | 0.010385 | 0.20767 | Cap-Tons/1000 sf | 10317.5 | 10642.5 | 10642.5 | 0.003528 | 0.11553 | 0.11553 | 0 | 0 | 0 | 10317.5 | 10642.5 | 10642.5 | 0.003528 | 0.11553 | 0.11553 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFL | OFFICE - LARGE | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.13653 | 0.0075866 | 0.1517 | Cap-Tons/1000 sf | 9543.5 | 9817.5 | 9817.5 | 0.0041918 | 0.15019 | 0.15019 | 0 | 0 | 0 | 9543.5 | 9817.5 | 9817.5 | 0.0041918 | 0.15019 | 0.15019 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFS | OFFICE - SMALL | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.16578 | 0.0092117 | 0.1842 | Cap-Tons/1000 sf | 6895.5 | 7177.5 | 7177.5 | 0.0065025 | 0.1655 | 0.1655 | 0 | 0 | 0 | 6895.5 | 7177.5 | 7177.5 | 0.0065025 | 0.1655 | 0.1655 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | Existing | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.10107 | 0.0056162 | 0.1123 | Cap-Tons/1000 sf | 4887.5 | 6077.5 | 5073.5 | 0.13148 | 0.67148 | 0.21358 | 0 | 0 | 0 | 4887.5 | 6077.5 | 5073.5 | 0.13148 | 0.67148 | 0.21358 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTS | RETAIL - SMALL | Existing | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.10985 | 0.0061039 | 0.12206 | Cap-Tons/1000 sf | 4697.5 | 6077.5 | 4910.5 | 0.20564 | 0.90564 | 0.31264 | 0 | 0 | 0 | 4697.5 | 6077.5 | 4910.5 | 0.20564 | 0.90564 | 0.31264 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | SCN | STORAGE - CONDITIONED | Existing | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.060165 | 0.0033432 | 0.066851 | Cap-Tons/1000 sf | 938.5 | 1307.5 | 1002.8 | 0.11284 | 0.39984 | 0.15794 | 0 | 0 | 0 | 938.5 | 1307.5 | 1002.8 | 0.11284 | 0.39984 | 0.15794 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ASM | ASSEMBLY | New | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.22348 | 0.012418 | 0.24831 | Cap-Tons/1000 sf | 3775.5 | 3965.5 | 3965.5 | 0.0047456 | 0.099046 | 0.099046 | 0 | 0 | 0 | 3775.5 | 3965.5 | 3965.5 | 0.0047456 | 0.099046 | 0.099046 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | New | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.12949 | 0.0071952 | 0.14388 | Cap-Tons/1000 sf | 5052.5 | 5252.5 | 5252.5 | 0.0050668 | 0.13307 | 0.13307 | 0 | 0 | 0 | 5052.5 | 5252.5 | 5252.5 | 0.0050668 | 0.13307 | 0.13307 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | New | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.15684 | 0.0087149 | 0.17427 | Cap-Tons/1000 sf | 3079.5 | 3217.5 | 3217.5 | 0.0049294 | 0.11493 | 0.11493 | 0 | 0 | 0 | 3079.5 | 3217.5 | 3217.5 | 0.0049294 | 0.11493 | 0.11493 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | New | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.18544 | 0.010304 | 0.20605 | Cap-Tons/1000 sf | 5081.5 | 5252.5 | 5252.5 | 0.0036007 | 0.1106 | 0.1106 | 0 | 0 | 0 | 5081.5 | 5252.5 | 5252.5 | 0.0036007 | 0.1106 | 0.1106 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | New | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.1526 | 0.0084793 | 0.16956 | Cap-Tons/1000 sf | 3069.5 | 3217.5 | 3217.5 | 0.0059306 | 0.12893 | 0.12893 | 0 | 0 | 0 | 3069.5 | 3217.5 | 3217.5 | 0.0059306 | 0.12893 | 0.12893 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EUN | EDUCATION - UNIVERSITY | New | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.13025 | 0.0072376 | 0.14473 | Cap-Tons/1000 sf | 5020.5 | 5252.5 | 5252.5 | 0.0060074 | 0.13601 | 0.13601 | 0 | 0 | 0 | 5020.5 | 5252.5 | 5252.5 | 0.0060074 | 0.13601 | 0.13601 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | GRO | GROCERY | New | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.23968 | 0.013318 | 0.26631 | Cap-Tons/1000 sf | 7697 | 7920 | 7920 | 0.0020107 | 0.071411 | 0.071411 | 0 | 0 | 0 | 7697 | 7920 | 7920 | 0.0020107 | 0.071411 | 0.071411 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | New | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.1869 | 0.010385 | 0.20767 | Cap-Tons/1000 sf | 10387.5 | 10642.5 | 10642.5 | 0.0016448 | 0.068645 | 0.068645 | 0 | 0 | 0 | 10387.5 | 10642.5 | 10642.5 | 0.0016448 | 0.068645 | 0.068645 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HTL | LODGING - HOTEL | New | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.10457 | 0.0058107 | 0.11619 | Cap-Tons/1000 sf | 6260.5 | 6627.5 | 6627.5 | 0.0068001 | 0.1228 | 0.1228 | 0 | 0 | 0 | 6260.5 | 6627.5 | 6627.5 | 0.0068001 | 0.1228 | 0.1228 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | MTL | LODGING - MOTEL | New | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.10457 | 0.0058107 | 0.11619 | Cap-Tons/1000 sf | 6260.5 | 6627.5 | 6627.5 | 0.0068001 | 0.1228 | 0.1228 | 0 | 0 | 0 | 6260.5 | 6627.5 | 6627.5 | 0.0068001 | 0.1228 | 0.1228 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | New | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.1869 | 0.010385 | 0.20767 | Cap-Tons/1000 sf | 10402.5 | 10642.5 | 10642.5 | 0.0014027 | 0.062203 | 0.062203 | 0 | 0 | 0 | 10402.5 | 10642.5 | 10642.5 | 0.0014027 | 0.062203 | 0.062203 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFL | OFFICE - LARGE | New | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.13653 | 0.0075866 | 0.1517 | Cap-Tons/1000 sf | 9601.5 | 9817.5 | 9817.5 | 0.0024971 | 0.1135 | 0.1135 | 0 | 0 | 0 | 9601.5 | 9817.5 | 9817.5 | 0.0024971 | 0.1135 | 0.1135 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFS | OFFICE - SMALL | New | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.16578 | 0.0092117 | 0.1842 | Cap-Tons/1000 sf | 6985.5 | 7177.5 | 7177.5 | 0.0031059 | 0.11611 | 0.11611 | 0 | 0 | 0 | 6985.5 | 7177.5 | 7177.5 | 0.0031059 | 0.11611 | 0.11611 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | New | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.29153 | 0.0162 | 0.32393 | Cap-Tons/1000 sf | 15497 | 15840 | 15840 | 0.0024125 | 0.11141 | 0.11141 | 0 | 0 | 0 | 15497 | 15840 | 15840 | 0.0024125 | 0.11141 | 0.11141 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | New | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.19242 | 0.010692 | 0.2138 | Cap-Tons/1000 sf | 15609 | 15840 | 15840 | 0.0015539 | 0.10655 | 0.10655 | 0 | 0 | 0 | 15609 | 15840 | 15840 | 0.0015539 | 0.10655 | 0.10655 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | New | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.083367 | 0.0046324 | 0.092632 | Cap-Tons/1000 sf | 5872.5 | 6077.5 | 6077.5 | 0.0038399 | 0.11384 | 0.11384 | 0 | 0 | 0 | 5872.5 | 6077.5 | 6077.5 | 0.0038399 | 0.11384 | 0.11384 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | New | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.10107 | 0.0056162 | 0.1123 | Cap-Tons/1000 sf | 5888.5 | 6077.5 | 6077.5 | 0.0029176 | 0.093818 | 0.093818 | 0 | 0 | 0 | 5888.5 | 6077.5 | 6077.5 | 0.0029176 | 0.093818 | 0.093818 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTS | RETAIL - SMALL | New | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.10985 | 0.0061039 | 0.12206 | Cap-Tons/1000 sf | 5831.5 | 6077.5 | 6077.5 | 0.0054418 | 0.13444 | 0.13444 | 0 | 0 | 0 | 5831.5 | 6077.5 | 6077.5 | 0.0054418 | 0.13444 | 0.13444 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | SCN | STORAGE - CONDITIONED | New | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.060165 | 0.0033432 | 0.066851 | Cap-Tons/1000 sf | 1243.6 | 1307.5 | 1307.5 | 0.0022763 | 0.046576 | 0.046576 | 0 | 0 | 0 | 1243.6 | 1307.5 | 1307.5 | 0.0022763 | 0.046576 | 0.046576 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ASM | ASSEMBLY | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.22348 | 0.012418 | 0.24831 | Cap-Tons/1000 sf | 2605.5 | 3965.5 | 2839.5 | 0.32989 | 0.96189 | 0.43189 | 0 | 0 | 0 | 2605.5 | 3965.5 | 2839.5 | 0.32989 | 0.96189 | 0.43189 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.12949 | 0.0071952 | 0.14388 | Cap-Tons/1000 sf | 3992.5 | 5252.5 | 4185.5 | 0.25531 | 1.0643 | 0.37631 | 0 | 0 | 0 | 3992.5 | 5252.5 | 4185.5 | 0.25531 | 1.0643 | 0.37631 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.15684 | 0.0087149 | 0.17427 | Cap-Tons/1000 sf | 2264.5 | 3217.5 | 2396.5 | 0.32152 | 1.0855 | 0.42452 | 0 | 0 | 0 | 2264.5 | 3217.5 | 2396.5 | 0.32152 | 1.0855 | 0.42452 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.18544 | 0.010304 | 0.20605 | Cap-Tons/1000 sf | 4431.5 | 5252.5 | 4612.5 | 0.10041 | 0.64241 | 0.20141 | 0 | 0 | 0 | 4431.5 | 5252.5 | 4612.5 | 0.10041 | 0.64241 | 0.20141 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.1526 | 0.0084793 | 0.16956 | Cap-Tons/1000 sf | 2256.5 | 3217.5 | 2390.5 | 0.34156 | 1.1436 | 0.44956 | 0 | 0 | 0 | 2256.5 | 3217.5 | 2390.5 | 0.34156 | 1.1436 | 0.44956 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.1869 | 0.010385 | 0.20767 | Cap-Tons/1000 sf | 10346.5 | 10642.5 | 10642.5 | 0.0023202 | 0.08342 | 0.08342 | 0 | 0 | 0 | 10346.5 | 10642.5 | 10642.5 | 0.0023202 | 0.08342 | 0.08342 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFL | OFFICE - LARGE | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.13653 | 0.0075866 | 0.1517 | Cap-Tons/1000 sf | 9604.5 | 9817.5 | 9817.5 | 0.00275 | 0.12675 | 0.12675 | 0 | 0 | 0 | 9604.5 | 9817.5 | 9817.5 | 0.00275 | 0.12675 | 0.12675 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFS | OFFICE - SMALL | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.16578 | 0.0092117 | 0.1842 | Cap-Tons/1000 sf | 6980.5 | 7177.5 | 7177.5 | 0.003697 | 0.1347 | 0.1347 | 0 | 0 | 0 | 6980.5 | 7177.5 | 7177.5 | 0.003697 | 0.1347 | 0.1347 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.29153 | 0.0162 | 0.32393 | Cap-Tons/1000 sf | 15497 | 15840 | 15840 | 0.0026781 | 0.12368 | 0.12368 | 0 | 0 | 0 | 15497 | 15840 | 15840 | 0.0026781 | 0.12368 | 0.12368 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.19242 | 0.010692 | 0.2138 | Cap-Tons/1000 sf | 15589 | 15840 | 15840 | 0.0019321 | 0.12193 | 0.12193 | 0 | 0 | 0 | 15589 | 15840 | 15840 | 0.0019321 | 0.12193 | 0.12193 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.083367 | 0.0046324 | 0.092632 | Cap-Tons/1000 sf | 5792.5 | 6077.5 | 6077.5 | 0.0069374 | 0.14794 | 0.14794 | 0 | 0 | 0 | 5792.5 | 6077.5 | 6077.5 | 0.0069374 | 0.14794 | 0.14794 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.10107 | 0.0056162 | 0.1123 | Cap-Tons/1000 sf | 5815.5 | 6077.5 | 6077.5 | 0.0054062 | 0.12541 | 0.12541 | 0 | 0 | 0 | 5815.5 | 6077.5 | 6077.5 | 0.0054062 | 0.12541 | 0.12541 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTS | RETAIL - SMALL | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.10985 | 0.0061039 | 0.12206 | Cap-Tons/1000 sf | 5819.5 | 6077.5 | 6077.5 | 0.0058964 | 0.1389 | 0.1389 | 0 | 0 | 0 | 5819.5 | 6077.5 | 6077.5 | 0.0058964 | 0.1389 | 0.1389 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | SCN | STORAGE - CONDITIONED | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.060165 | 0.0033432 | 0.066851 | Cap-Tons/1000 sf | 1208.9 | 1307.5 | 1307.5 | 0.0060927 | 0.080793 | 0.080793 | 0 | 0 | 0 | 1208.9 | 1307.5 | 1307.5 | 0.0060927 | 0.080793 | 0.080793 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ASM | ASSEMBLY | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.22348 | 0.012418 | 0.24831 | Cap-Tons/1000 sf | 2379.3 | 3965.5 | 2681.3 | 0.63267 | 1.5817 | 0.78467 | 0 | 0 | 0 | 2379.3 | 3965.5 | 2681.3 | 0.63267 | 1.5817 | 0.78467 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.12949 | 0.0071952 | 0.14388 | Cap-Tons/1000 sf | 3992.5 | 5252.5 | 4186.5 | 0.26352 | 1.0985 | 0.38952 | 0 | 0 | 0 | 3992.5 | 5252.5 | 4186.5 | 0.26352 | 1.0985 | 0.38952 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.15684 | 0.0087149 | 0.17427 | Cap-Tons/1000 sf | 2177.5 | 3217.5 | 2321.5 | 0.128 | 0.396 | 0.1632 | 0 | 0 | 0 | 2177.5 | 3217.5 | 2321.5 | 0.128 | 0.396 | 0.1632 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.18544 | 0.010304 | 0.20605 | Cap-Tons/1000 sf | 4349.5 | 5252.5 | 4549.5 | 0.062075 | 0.36108 | 0.11768 | 0 | 0 | 0 | 4349.5 | 5252.5 | 4549.5 | 0.062075 | 0.36108 | 0.11768 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.1526 | 0.0084793 | 0.16956 | Cap-Tons/1000 sf | 2127.5 | 3217.5 | 2279.5 | 0.13731 | 0.40531 | 0.17271 | 0 | 0 | 0 | 2127.5 | 3217.5 | 2279.5 | 0.13731 | 0.40531 | 0.17271 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EUN | EDUCATION - UNIVERSITY | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.13025 | 0.0072376 | 0.14473 | Cap-Tons/1000 sf | 3842.5 | 5252.5 | 4057.5 | 0.28989 | 1.0799 | 0.40889 | 0 | 0 | 0 | 3842.5 | 5252.5 | 4057.5 | 0.28989 | 1.0799 | 0.40889 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.1526 | 0.0084793 | 0.16956 | Cap-Tons/1000 sf | 1930.5 | 3217.5 | 2135.5 | 0.20067 | 0.50167 | 0.24037 | 0 | 0 | 0 | 1930.5 | 3217.5 | 2135.5 | 0.20067 | 0.50167 | 0.24037 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EUN | EDUCATION - UNIVERSITY | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.13025 | 0.0072376 | 0.14473 | Cap-Tons/1000 sf | 3852.5 | 5252.5 | 4071.5 | 0.3078 | 1.1548 | 0.4358 | 0 | 0 | 0 | 3852.5 | 5252.5 | 4071.5 | 0.3078 | 1.1548 | 0.4358 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | GRO | GROCERY | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.23968 | 0.013318 | 0.26631 | Cap-Tons/1000 sf | 5900 | 7920 | 6283 | 0.21535 | 0.84435 | 0.31735 | 0 | 0 | 0 | 5900 | 7920 | 6283 | 0.21535 | 0.84435 | 0.31735 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.1869 | 0.010385 | 0.20767 | Cap-Tons/1000 sf | 8632.5 | 10642.5 | 8926.5 | 0.156 | 0.826 | 0.2512 | 0 | 0 | 0 | 8632.5 | 10642.5 | 8926.5 | 0.156 | 0.826 | 0.2512 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HTL | LODGING - HOTEL | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.10457 | 0.0058107 | 0.11619 | Cap-Tons/1000 sf | 4547.5 | 6627.5 | 4893.5 | 0.37186 | 1.1849 | 0.49986 | 0 | 0 | 0 | 4547.5 | 6627.5 | 4893.5 | 0.37186 | 1.1849 | 0.49986 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | MTL | LODGING - MOTEL | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.10457 | 0.0058107 | 0.11619 | Cap-Tons/1000 sf | 4547.5 | 6627.5 | 4893.5 | 0.37186 | 1.1849 | 0.49986 | 0 | 0 | 0 | 4547.5 | 6627.5 | 4893.5 | 0.37186 | 1.1849 | 0.49986 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.1869 | 0.010385 | 0.20767 | Cap-Tons/1000 sf | 8192.5 | 10642.5 | 8562.5 | 0.20934 | 0.90934 | 0.30824 | 0 | 0 | 0 | 8192.5 | 10642.5 | 8562.5 | 0.20934 | 0.90934 | 0.30824 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFL | OFFICE - LARGE | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.13653 | 0.0075866 | 0.1517 | Cap-Tons/1000 sf | 8677.5 | 9817.5 | 8866.5 | 0.095772 | 0.82477 | 0.21577 | 0 | 0 | 0 | 8677.5 | 9817.5 | 8866.5 | 0.095772 | 0.82477 | 0.21577 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFS | OFFICE - SMALL | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.16578 | 0.0092117 | 0.1842 | Cap-Tons/1000 sf | 5797.5 | 7177.5 | 5983.5 | 0.22732 | 1.1823 | 0.35532 | 0 | 0 | 0 | 5797.5 | 7177.5 | 5983.5 | 0.22732 | 1.1823 | 0.35532 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.29153 | 0.0162 | 0.32393 | Cap-Tons/1000 sf | 13120 | 15840 | 13509 | 0.20587 | 1.1989 | 0.33987 | 0 | 0 | 0 | 13120 | 15840 | 13509 | 0.20587 | 1.1989 | 0.33987 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.19242 | 0.010692 | 0.2138 | Cap-Tons/1000 sf | 13500 | 15840 | 13828 | 0.1976 | 1.3376 | 0.3506 | 0 | 0 | 0 | 13500 | 15840 | 13828 | 0.1976 | 1.3376 | 0.3506 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.083367 | 0.0046324 | 0.092632 | Cap-Tons/1000 sf | 4507.5 | 6077.5 | 4758.5 | 0.32811 | 1.2701 | 0.47211 | 0 | 0 | 0 | 4507.5 | 6077.5 | 4758.5 | 0.32811 | 1.2701 | 0.47211 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | GRO | GROCERY | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.23968 | 0.013318 | 0.26631 | Cap-Tons/1000 sf | 6260 | 7920 | 6572 | 0.15195 | 0.72495 | 0.24565 | 0 | 0 | 0 | 6260 | 7920 | 6572 | 0.15195 | 0.72495 | 0.24565 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.1869 | 0.010385 | 0.20767 | Cap-Tons/1000 sf | 8582.5 | 10642.5 | 8879.5 | 0.16226 | 0.83826 | 0.25806 | 0 | 0 | 0 | 8582.5 | 10642.5 | 8879.5 | 0.16226 | 0.83826 | 0.25806 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HTL | LODGING - HOTEL | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.10457 | 0.0058107 | 0.11619 | Cap-Tons/1000 sf | 4587.5 | 6627.5 | 4918.5 | 0.34597 | 1.124 | 0.46897 | 0 | 0 | 0 | 4587.5 | 6627.5 | 4918.5 | 0.34597 | 1.124 | 0.46897 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | MTL | LODGING - MOTEL | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.10457 | 0.0058107 | 0.11619 | Cap-Tons/1000 sf | 4587.5 | 6627.5 | 4918.5 | 0.34597 | 1.124 | 0.46897 | 0 | 0 | 0 | 4587.5 | 6627.5 | 4918.5 | 0.34597 | 1.124 | 0.46897 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.1869 | 0.010385 | 0.20767 | Cap-Tons/1000 sf | 8562.5 | 10642.5 | 8873.5 | 0.16203 | 0.82903 | 0.25633 | 0 | 0 | 0 | 8562.5 | 10642.5 | 8873.5 | 0.16203 | 0.82903 | 0.25633 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFL | OFFICE - LARGE | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.13653 | 0.0075866 | 0.1517 | Cap-Tons/1000 sf | 8577.5 | 9817.5 | 8780.5 | 0.10438 | 0.82638 | 0.22338 | 0 | 0 | 0 | 8577.5 | 9817.5 | 8780.5 | 0.10438 | 0.82638 | 0.22338 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFS | OFFICE - SMALL | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.16578 | 0.0092117 | 0.1842 | Cap-Tons/1000 sf | 5897.5 | 7177.5 | 6067.5 | 0.18904 | 1.06 | 0.30504 | 0 | 0 | 0 | 5897.5 | 7177.5 | 6067.5 | 0.18904 | 1.06 | 0.30504 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.29153 | 0.0162 | 0.32393 | Cap-Tons/1000 sf | 13390 | 15840 | 13735 | 0.18004 | 1.164 | 0.31304 | 0 | 0 | 0 | 13390 | 15840 | 13735 | 0.18004 | 1.164 | 0.31304 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.19242 | 0.010692 | 0.2138 | Cap-Tons/1000 sf | 13880 | 15840 | 14152 | 0.14968 | 1.2097 | 0.29268 | 0 | 0 | 0 | 13880 | 15840 | 14152 | 0.14968 | 1.2097 | 0.29268 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.083367 | 0.0046324 | 0.092632 | Cap-Tons/1000 sf | 4417.5 | 6077.5 | 4673.5 | 0.35586 | 1.3029 | 0.50086 | 0 | 0 | 0 | 4417.5 | 6077.5 | 4673.5 | 0.35586 | 1.3029 | 0.50086 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.10107 | 0.0056162 | 0.1123 | Cap-Tons/1000 sf | 4367.5 | 6077.5 | 4633.5 | 0.35903 | 1.276 | 0.49803 | 0 | 0 | 0 | 4367.5 | 6077.5 | 4633.5 | 0.35903 | 1.276 | 0.49803 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTS | RETAIL - SMALL | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.10985 | 0.0061039 | 0.12206 | Cap-Tons/1000 sf | 4507.5 | 6077.5 | 4751.5 | 0.32845 | 1.2715 | 0.47245 | 0 | 0 | 0 | 4507.5 | 6077.5 | 4751.5 | 0.32845 | 1.2715 | 0.47245 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EUN | EDUCATION - UNIVERSITY | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.13025 | 0.0072376 | 0.14473 | Cap-Tons/1000 sf | 5007.5 | 5252.5 | 5252.5 | 0.0069965 | 0.15 | 0.15 | 0 | 0 | 0 | 5007.5 | 5252.5 | 5252.5 | 0.0069965 | 0.15 | 0.15 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | GRO | GROCERY | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.23968 | 0.013318 | 0.26631 | Cap-Tons/1000 sf | 7615 | 7920 | 7920 | 0.0050066 | 0.13001 | 0.13001 | 0 | 0 | 0 | 7615 | 7920 | 7920 | 0.0050066 | 0.13001 | 0.13001 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.1869 | 0.010385 | 0.20767 | Cap-Tons/1000 sf | 10339.5 | 10642.5 | 10642.5 | 0.0029598 | 0.10396 | 0.10396 | 0 | 0 | 0 | 10339.5 | 10642.5 | 10642.5 | 0.0029598 | 0.10396 | 0.10396 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HTL | LODGING - HOTEL | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.10457 | 0.0058107 | 0.11619 | Cap-Tons/1000 sf | 6246.5 | 6627.5 | 6627.5 | 0.0087832 | 0.15278 | 0.15278 | 0 | 0 | 0 | 6246.5 | 6627.5 | 6627.5 | 0.0087832 | 0.15278 | 0.15278 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | MTL | LODGING - MOTEL | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.10457 | 0.0058107 | 0.11619 | Cap-Tons/1000 sf | 6246.5 | 6627.5 | 6627.5 | 0.0087832 | 0.15278 | 0.15278 | 0 | 0 | 0 | 6246.5 | 6627.5 | 6627.5 | 0.0087832 | 0.15278 | 0.15278 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.1869 | 0.010385 | 0.20767 | Cap-Tons/1000 sf | 10335.5 | 10642.5 | 10642.5 | 0.0028515 | 0.098852 | 0.098852 | 0 | 0 | 0 | 10335.5 | 10642.5 | 10642.5 | 0.0028515 | 0.098852 | 0.098852 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFL | OFFICE - LARGE | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.13653 | 0.0075866 | 0.1517 | Cap-Tons/1000 sf | 9563.5 | 9817.5 | 9817.5 | 0.0038777 | 0.14988 | 0.14988 | 0 | 0 | 0 | 9563.5 | 9817.5 | 9817.5 | 0.0038777 | 0.14988 | 0.14988 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFS | OFFICE - SMALL | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.16578 | 0.0092117 | 0.1842 | Cap-Tons/1000 sf | 6970.5 | 7177.5 | 7177.5 | 0.004306 | 0.14931 | 0.14931 | 0 | 0 | 0 | 6970.5 | 7177.5 | 7177.5 | 0.004306 | 0.14931 | 0.14931 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.29153 | 0.0162 | 0.32393 | Cap-Tons/1000 sf | 15434 | 15840 | 15840 | 0.0041037 | 0.1601 | 0.1601 | 0 | 0 | 0 | 15434 | 15840 | 15840 | 0.0041037 | 0.1601 | 0.1601 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.19242 | 0.010692 | 0.2138 | Cap-Tons/1000 sf | 15524 | 15840 | 15840 | 0.0032772 | 0.16428 | 0.16428 | 0 | 0 | 0 | 15524 | 15840 | 15840 | 0.0032772 | 0.16428 | 0.16428 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.083367 | 0.0046324 | 0.092632 | Cap-Tons/1000 sf | 5775.5 | 6077.5 | 6077.5 | 0.0085755 | 0.17258 | 0.17258 | 0 | 0 | 0 | 5775.5 | 6077.5 | 6077.5 | 0.0085755 | 0.17258 | 0.17258 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.10107 | 0.0056162 | 0.1123 | Cap-Tons/1000 sf | 5787.5 | 6077.5 | 6077.5 | 0.0077166 | 0.16172 | 0.16172 | 0 | 0 | 0 | 5787.5 | 6077.5 | 6077.5 | 0.0077166 | 0.16172 | 0.16172 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTS | RETAIL - SMALL | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.10985 | 0.0061039 | 0.12206 | Cap-Tons/1000 sf | 5793.5 | 6077.5 | 6077.5 | 0.0078923 | 0.16889 | 0.16889 | 0 | 0 | 0 | 5793.5 | 6077.5 | 6077.5 | 0.0078923 | 0.16889 | 0.16889 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | SCN | STORAGE - CONDITIONED | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.060165 | 0.0033432 | 0.066851 | Cap-Tons/1000 sf | 1193.5 | 1307.5 | 1307.5 | 0.010316 | 0.11832 | 0.11832 | 0 | 0 | 0 | 1193.5 | 1307.5 | 1307.5 | 0.010316 | 0.11832 | 0.11832 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ASM | ASSEMBLY | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.22348 | 0.012418 | 0.24831 | Cap-Tons/1000 sf | 2379.3 | 3965.5 | 2702.3 | 0.618 | 1.545 | 0.767 | 0 | 0 | 0 | 2379.3 | 3965.5 | 2702.3 | 0.618 | 1.545 | 0.767 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.10107 | 0.0056162 | 0.1123 | Cap-Tons/1000 sf | 4297.5 | 6077.5 | 4583.5 | 0.38479 | 1.3138 | 0.52579 | 0 | 0 | 0 | 4297.5 | 6077.5 | 4583.5 | 0.38479 | 1.3138 | 0.52579 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTS | RETAIL - SMALL | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.10985 | 0.0061039 | 0.12206 | Cap-Tons/1000 sf | 4437.5 | 6077.5 | 4699.5 | 0.36219 | 1.3422 | 0.51219 | 0 | 0 | 0 | 4437.5 | 6077.5 | 4699.5 | 0.36219 | 1.3422 | 0.51219 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | SCN | STORAGE - CONDITIONED | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.060165 | 0.0033432 | 0.066851 | Cap-Tons/1000 sf | 1076.5 | 1307.5 | 1307.5 | 0.026823 | 0.15182 | 0.15182 | 0 | 0 | 0 | 1076.5 | 1307.5 | 1307.5 | 0.026823 | 0.15182 | 0.15182 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ASM | ASSEMBLY | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.22348 | 0.012418 | 0.24831 | Cap-Tons/1000 sf | 3634.5 | 3965.5 | 3965.5 | 0.014025 | 0.16803 | 0.16803 | 0 | 0 | 0 | 3634.5 | 3965.5 | 3965.5 | 0.014025 | 0.16803 | 0.16803 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.12949 | 0.0071952 | 0.14388 | Cap-Tons/1000 sf | 4993.5 | 5252.5 | 5252.5 | 0.0080395 | 0.16304 | 0.16304 | 0 | 0 | 0 | 4993.5 | 5252.5 | 5252.5 | 0.0080395 | 0.16304 | 0.16304 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.15684 | 0.0087149 | 0.17427 | Cap-Tons/1000 sf | 3011.5 | 3217.5 | 3217.5 | 0.0026267 | 0.041027 | 0.041027 | 0 | 0 | 0 | 3011.5 | 3217.5 | 3217.5 | 0.0026267 | 0.041027 | 0.041027 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.18544 | 0.010304 | 0.20605 | Cap-Tons/1000 sf | 4976.5 | 5252.5 | 5252.5 | 0.0038101 | 0.07251 | 0.07251 | 0 | 0 | 0 | 4976.5 | 5252.5 | 5252.5 | 0.0038101 | 0.07251 | 0.07251 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.1526 | 0.0084793 | 0.16956 | Cap-Tons/1000 sf | 2971.5 | 3217.5 | 3217.5 | 0.0029969 | 0.039197 | 0.039197 | 0 | 0 | 0 | 2971.5 | 3217.5 | 3217.5 | 0.0029969 | 0.039197 | 0.039197 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EUN | EDUCATION - UNIVERSITY | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.13025 | 0.0072376 | 0.14473 | Cap-Tons/1000 sf | 5004.5 | 5252.5 | 5252.5 | 0.0073838 | 0.15638 | 0.15638 | 0 | 0 | 0 | 5004.5 | 5252.5 | 5252.5 | 0.0073838 | 0.15638 | 0.15638 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | GRO | GROCERY | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.23968 | 0.013318 | 0.26631 | Cap-Tons/1000 sf | 7535 | 7920 | 7920 | 0.0067445 | 0.13874 | 0.13874 | 0 | 0 | 0 | 7535 | 7920 | 7920 | 0.0067445 | 0.13874 | 0.13874 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.1869 | 0.010385 | 0.20767 | Cap-Tons/1000 sf | 10339.5 | 10642.5 | 10642.5 | 0.0029598 | 0.10396 | 0.10396 | 0 | 0 | 0 | 10339.5 | 10642.5 | 10642.5 | 0.0029598 | 0.10396 | 0.10396 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HTL | LODGING - HOTEL | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.10457 | 0.0058107 | 0.11619 | Cap-Tons/1000 sf | 6210.5 | 6627.5 | 6627.5 | 0.0098702 | 0.15687 | 0.15687 | 0 | 0 | 0 | 6210.5 | 6627.5 | 6627.5 | 0.0098702 | 0.15687 | 0.15687 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | MTL | LODGING - MOTEL | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.10457 | 0.0058107 | 0.11619 | Cap-Tons/1000 sf | 6210.5 | 6627.5 | 6627.5 | 0.0098702 | 0.15687 | 0.15687 | 0 | 0 | 0 | 6210.5 | 6627.5 | 6627.5 | 0.0098702 | 0.15687 | 0.15687 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.1869 | 0.010385 | 0.20767 | Cap-Tons/1000 sf | 10257.5 | 10642.5 | 10642.5 | 0.0037909 | 0.10479 | 0.10479 | 0 | 0 | 0 | 10257.5 | 10642.5 | 10642.5 | 0.0037909 | 0.10479 | 0.10479 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFL | OFFICE - LARGE | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.13653 | 0.0075866 | 0.1517 | Cap-Tons/1000 sf | 9601.5 | 9817.5 | 9817.5 | 0.0032845 | 0.14928 | 0.14928 | 0 | 0 | 0 | 9601.5 | 9817.5 | 9817.5 | 0.0032845 | 0.14928 | 0.14928 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFS | OFFICE - SMALL | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.16578 | 0.0092117 | 0.1842 | Cap-Tons/1000 sf | 6958.5 | 7177.5 | 7177.5 | 0.0049097 | 0.16091 | 0.16091 | 0 | 0 | 0 | 6958.5 | 7177.5 | 7177.5 | 0.0049097 | 0.16091 | 0.16091 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.29153 | 0.0162 | 0.32393 | Cap-Tons/1000 sf | 15358 | 15840 | 15840 | 0.0048646 | 0.15986 | 0.15986 | 0 | 0 | 0 | 15358 | 15840 | 15840 | 0.0048646 | 0.15986 | 0.15986 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.19242 | 0.010692 | 0.2138 | Cap-Tons/1000 sf | 15473 | 15840 | 15840 | 0.0038187 | 0.16482 | 0.16482 | 0 | 0 | 0 | 15473 | 15840 | 15840 | 0.0038187 | 0.16482 | 0.16482 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.083367 | 0.0046324 | 0.092632 | Cap-Tons/1000 sf | 5777.5 | 6077.5 | 6077.5 | 0.0084119 | 0.17041 | 0.17041 | 0 | 0 | 0 | 5777.5 | 6077.5 | 6077.5 | 0.0084119 | 0.17041 | 0.17041 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.10107 | 0.0056162 | 0.1123 | Cap-Tons/1000 sf | 5758.5 | 6077.5 | 6077.5 | 0.0085864 | 0.16359 | 0.16359 | 0 | 0 | 0 | 5758.5 | 6077.5 | 6077.5 | 0.0085864 | 0.16359 | 0.16359 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTS | RETAIL - SMALL | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.10985 | 0.0061039 | 0.12206 | Cap-Tons/1000 sf | 5778.5 | 6077.5 | 6077.5 | 0.0084342 | 0.17143 | 0.17143 | 0 | 0 | 0 | 5778.5 | 6077.5 | 6077.5 | 0.0084342 | 0.17143 | 0.17143 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | SCN | STORAGE - CONDITIONED | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.060165 | 0.0033432 | 0.066851 | Cap-Tons/1000 sf | 1076.5 | 1307.5 | 1307.5 | 0.026823 | 0.15182 | 0.15182 | 0 | 0 | 0 | 1076.5 | 1307.5 | 1307.5 | 0.026823 | 0.15182 | 0.15182 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ASM | ASSEMBLY | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.22348 | 0.012418 | 0.24831 | Cap-Tons/1000 sf | 2379.3 | 3965.5 | 2703.3 | 0.64533 | 1.6133 | 0.80233 | 0 | 0 | 0 | 2379.3 | 3965.5 | 2703.3 | 0.64533 | 1.6133 | 0.80233 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.12949 | 0.0071952 | 0.14388 | Cap-Tons/1000 sf | 4949.5 | 5252.5 | 5252.5 | 0.0090603 | 0.15706 | 0.15706 | 0 | 0 | 0 | 4949.5 | 5252.5 | 5252.5 | 0.0090603 | 0.15706 | 0.15706 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.15684 | 0.0087149 | 0.17427 | Cap-Tons/1000 sf | 1930.5 | 3217.5 | 2115.5 | 0.226 | 0.565 | 0.2707 | 0 | 0 | 0 | 1930.5 | 3217.5 | 2115.5 | 0.226 | 0.565 | 0.2707 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.18544 | 0.010304 | 0.20605 | Cap-Tons/1000 sf | 4062.5 | 5252.5 | 4300.5 | 0.10545 | 0.46545 | 0.17225 | 0 | 0 | 0 | 4062.5 | 5252.5 | 4300.5 | 0.10545 | 0.46545 | 0.17225 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.1526 | 0.0084793 | 0.16956 | Cap-Tons/1000 sf | 1930.5 | 3217.5 | 2141.5 | 0.21667 | 0.54167 | 0.25967 | 0 | 0 | 0 | 1930.5 | 3217.5 | 2141.5 | 0.21667 | 0.54167 | 0.25967 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EUN | EDUCATION - UNIVERSITY | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.13025 | 0.0072376 | 0.14473 | Cap-Tons/1000 sf | 4950.5 | 5252.5 | 5252.5 | 0.0087236 | 0.15172 | 0.15172 | 0 | 0 | 0 | 4950.5 | 5252.5 | 5252.5 | 0.0087236 | 0.15172 | 0.15172 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | GRO | GROCERY | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.23968 | 0.013318 | 0.26631 | Cap-Tons/1000 sf | 6230 | 7920 | 6526 | 0.1728 | 0.8098 | 0.2758 | 0 | 0 | 0 | 6230 | 7920 | 6526 | 0.1728 | 0.8098 | 0.2758 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.1869 | 0.010385 | 0.20767 | Cap-Tons/1000 sf | 10305.5 | 10642.5 | 10642.5 | 0.0036298 | 0.11463 | 0.11463 | 0 | 0 | 0 | 10305.5 | 10642.5 | 10642.5 | 0.0036298 | 0.11463 | 0.11463 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HTL | LODGING - HOTEL | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.10457 | 0.0058107 | 0.11619 | Cap-Tons/1000 sf | 4157.5 | 6627.5 | 4553.5 | 0.51687 | 1.3869 | 0.65387 | 0 | 0 | 0 | 4157.5 | 6627.5 | 4553.5 | 0.51687 | 1.3869 | 0.65387 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | MTL | LODGING - MOTEL | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.10457 | 0.0058107 | 0.11619 | Cap-Tons/1000 sf | 4157.5 | 6627.5 | 4553.5 | 0.51687 | 1.3869 | 0.65387 | 0 | 0 | 0 | 4157.5 | 6627.5 | 4553.5 | 0.51687 | 1.3869 | 0.65387 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.1869 | 0.010385 | 0.20767 | Cap-Tons/1000 sf | 10317.5 | 10642.5 | 10642.5 | 0.003528 | 0.11553 | 0.11553 | 0 | 0 | 0 | 10317.5 | 10642.5 | 10642.5 | 0.003528 | 0.11553 | 0.11553 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFL | OFFICE - LARGE | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.13653 | 0.0075866 | 0.1517 | Cap-Tons/1000 sf | 8397.5 | 9817.5 | 8632.5 | 0.12801 | 0.88501 | 0.25301 | 0 | 0 | 0 | 8397.5 | 9817.5 | 8632.5 | 0.12801 | 0.88501 | 0.25301 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFS | OFFICE - SMALL | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.16578 | 0.0092117 | 0.1842 | Cap-Tons/1000 sf | 5477.5 | 7177.5 | 5704.5 | 0.2995 | 1.2645 | 0.4285 | 0 | 0 | 0 | 5477.5 | 7177.5 | 5704.5 | 0.2995 | 1.2645 | 0.4285 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.29153 | 0.0162 | 0.32393 | Cap-Tons/1000 sf | 13110 | 15840 | 13484 | 0.22281 | 1.2928 | 0.36781 | 0 | 0 | 0 | 13110 | 15840 | 13484 | 0.22281 | 1.2928 | 0.36781 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.19242 | 0.010692 | 0.2138 | Cap-Tons/1000 sf | 13440 | 15840 | 13767 | 0.21429 | 1.4143 | 0.37529 | 0 | 0 | 0 | 13440 | 15840 | 13767 | 0.21429 | 1.4143 | 0.37529 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.083367 | 0.0046324 | 0.092632 | Cap-Tons/1000 sf | 4147.5 | 6077.5 | 4443.5 | 0.46115 | 1.4522 | 0.61315 | 0 | 0 | 0 | 4147.5 | 6077.5 | 4443.5 | 0.46115 | 1.4522 | 0.61315 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.10107 | 0.0056162 | 0.1123 | Cap-Tons/1000 sf | 3987.5 | 6077.5 | 4310.5 | 0.52938 | 1.5394 | 0.68338 | 0 | 0 | 0 | 3987.5 | 6077.5 | 4310.5 | 0.52938 | 1.5394 | 0.68338 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTS | RETAIL - SMALL | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.10985 | 0.0061039 | 0.12206 | Cap-Tons/1000 sf | 4207.5 | 6077.5 | 4494.5 | 0.44 | 1.43 | 0.591 | 0 | 0 | 0 | 4207.5 | 6077.5 | 4494.5 | 0.44 | 1.43 | 0.591 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | SCN | STORAGE - CONDITIONED | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.060165 | 0.0033432 | 0.066851 | Cap-Tons/1000 sf | 1111.5 | 1307.5 | 1307.5 | 0.02504 | 0.16704 | 0.16704 | 0 | 0 | 0 | 1111.5 | 1307.5 | 1307.5 | 0.02504 | 0.16704 | 0.16704 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ASM | ASSEMBLY | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.22348 | 0.012418 | 0.24831 | Cap-Tons/1000 sf | 3645.5 | 3965.5 | 3965.5 | 0.014396 | 0.1784 | 0.1784 | 0 | 0 | 0 | 3645.5 | 3965.5 | 3965.5 | 0.014396 | 0.1784 | 0.1784 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.12949 | 0.0071952 | 0.14388 | Cap-Tons/1000 sf | 4949.5 | 5252.5 | 5252.5 | 0.0090603 | 0.15706 | 0.15706 | 0 | 0 | 0 | 4949.5 | 5252.5 | 5252.5 | 0.0090603 | 0.15706 | 0.15706 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.15684 | 0.0087149 | 0.17427 | Cap-Tons/1000 sf | 3024.5 | 3217.5 | 3217.5 | 0.0027312 | 0.045531 | 0.045531 | 0 | 0 | 0 | 3024.5 | 3217.5 | 3217.5 | 0.0027312 | 0.045531 | 0.045531 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.18544 | 0.010304 | 0.20605 | Cap-Tons/1000 sf | 5004.5 | 5252.5 | 5252.5 | 0.0035581 | 0.075358 | 0.075358 | 0 | 0 | 0 | 5004.5 | 5252.5 | 5252.5 | 0.0035581 | 0.075358 | 0.075358 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.1526 | 0.0084793 | 0.16956 | Cap-Tons/1000 sf | 2994.5 | 3217.5 | 3217.5 | 0.0030831 | 0.044483 | 0.044483 | 0 | 0 | 0 | 2994.5 | 3217.5 | 3217.5 | 0.0030831 | 0.044483 | 0.044483 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EUN | EDUCATION - UNIVERSITY | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.13025 | 0.0072376 | 0.14473 | Cap-Tons/1000 sf | 4950.5 | 5252.5 | 5252.5 | 0.0087236 | 0.15172 | 0.15172 | 0 | 0 | 0 | 4950.5 | 5252.5 | 5252.5 | 0.0087236 | 0.15172 | 0.15172 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | GRO | GROCERY | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.23968 | 0.013318 | 0.26631 | Cap-Tons/1000 sf | 7590 | 7920 | 7920 | 0.0050435 | 0.12104 | 0.12104 | 0 | 0 | 0 | 7590 | 7920 | 7920 | 0.0050435 | 0.12104 | 0.12104 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.29153 | 0.0162 | 0.32393 | Cap-Tons/1000 sf | 15439 | 15840 | 15840 | 0.0042077 | 0.16621 | 0.16621 | 0 | 0 | 0 | 15439 | 15840 | 15840 | 0.0042077 | 0.16621 | 0.16621 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.19242 | 0.010692 | 0.2138 | Cap-Tons/1000 sf | 15498 | 15840 | 15840 | 0.0035087 | 0.16251 | 0.16251 | 0 | 0 | 0 | 15498 | 15840 | 15840 | 0.0035087 | 0.16251 | 0.16251 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.083367 | 0.0046324 | 0.092632 | Cap-Tons/1000 sf | 5747.5 | 6077.5 | 6077.5 | 0.0097608 | 0.17976 | 0.17976 | 0 | 0 | 0 | 5747.5 | 6077.5 | 6077.5 | 0.0097608 | 0.17976 | 0.17976 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.10107 | 0.0056162 | 0.1123 | Cap-Tons/1000 sf | 5720.5 | 6077.5 | 6077.5 | 0.010484 | 0.17848 | 0.17848 | 0 | 0 | 0 | 5720.5 | 6077.5 | 6077.5 | 0.010484 | 0.17848 | 0.17848 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTS | RETAIL - SMALL | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.10985 | 0.0061039 | 0.12206 | Cap-Tons/1000 sf | 5751.5 | 6077.5 | 6077.5 | 0.0096357 | 0.17964 | 0.17964 | 0 | 0 | 0 | 5751.5 | 6077.5 | 6077.5 | 0.0096357 | 0.17964 | 0.17964 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-047 | HVAC - SEER Rated Package Rooftop HP (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 14) | Packaged SEER-Rated Heat Pump - Average SEER = 14, Average COP = 3.51 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER14 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | SCN | STORAGE - CONDITIONED | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.060165 | 0.0033432 | 0.066851 | Cap-Tons/1000 sf | 1111.5 | 1307.5 | 1307.5 | 0.02504 | 0.16704 | 0.16704 | 0 | 0 | 0 | 1111.5 | 1307.5 | 1307.5 | 0.02504 | 0.16704 | 0.16704 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1680 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFS | OFFICE - SMALL | Existing | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.13983 | 0.010993 | 0.16182 | Cap-Tons/1000 sf | 6277.5 | 7177.5 | 6472.5 | 0.072115 | 0.57511 | 0.17811 | 0 | 0 | 0 | 6277.5 | 7177.5 | 6472.5 | 0.072115 | 0.57511 | 0.17811 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | Existing | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.24312 | 0.019113 | 0.28135 | Cap-Tons/1000 sf | 11400 | 15840 | 12280 | 0.16085 | 0.57385 | 0.23835 | 0 | 0 | 0 | 11400 | 15840 | 12280 | 0.16085 | 0.57385 | 0.23835 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | Existing | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.16098 | 0.012656 | 0.1863 | Cap-Tons/1000 sf | 11930 | 15840 | 12724 | 0.13929 | 0.56429 | 0.22119 | 0 | 0 | 0 | 11930 | 15840 | 12724 | 0.13929 | 0.56429 | 0.22119 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | Existing | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.076065 | 0.0059798 | 0.088025 | Cap-Tons/1000 sf | 4807.5 | 6077.5 | 5100.5 | 0.10567 | 0.50567 | 0.19027 | 0 | 0 | 0 | 4807.5 | 6077.5 | 5100.5 | 0.10567 | 0.50567 | 0.19027 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | Existing | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.082079 | 0.0064526 | 0.094984 | Cap-Tons/1000 sf | 4057.5 | 6077.5 | 4520.5 | 0.2086 | 0.6276 | 0.2981 | 0 | 0 | 0 | 4057.5 | 6077.5 | 4520.5 | 0.2086 | 0.6276 | 0.2981 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTS | RETAIL - SMALL | Existing | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.09448 | 0.0074275 | 0.10933 | Cap-Tons/1000 sf | 4497.5 | 6077.5 | 4863.5 | 0.16055 | 0.61755 | 0.25735 | 0 | 0 | 0 | 4497.5 | 6077.5 | 4863.5 | 0.16055 | 0.61755 | 0.25735 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.16837 | 0.013237 | 0.19485 | Cap-Tons/1000 sf | 8332.5 | 10642.5 | 8883.5 | 0.11117 | 0.51217 | 0.19667 | 0 | 0 | 0 | 8332.5 | 10642.5 | 8883.5 | 0.11117 | 0.51217 | 0.19667 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFL | OFFICE - LARGE | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.11956 | 0.0093995 | 0.13836 | Cap-Tons/1000 sf | 8677.5 | 9817.5 | 8941.5 | 0.081583 | 0.70258 | 0.22458 | 0 | 0 | 0 | 8677.5 | 9817.5 | 8941.5 | 0.081583 | 0.70258 | 0.22458 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFS | OFFICE - SMALL | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.13983 | 0.010993 | 0.16182 | Cap-Tons/1000 sf | 6180.5 | 7177.5 | 6403.5 | 0.10453 | 0.75253 | 0.24853 | 0 | 0 | 0 | 6180.5 | 7177.5 | 6403.5 | 0.10453 | 0.75253 | 0.24853 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | SCN | STORAGE - CONDITIONED | New | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.052413 | 0.0041205 | 0.060654 | Cap-Tons/1000 sf | 1722 | 2040 | 2040 | 0.027146 | 0.17415 | 0.17415 | 0 | 0 | 0 | 1722 | 2040 | 2040 | 0.027146 | 0.17415 | 0.17415 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ASM | ASSEMBLY | Existing | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.19798 | 0.015564 | 0.2291 | Cap-Tons/1000 sf | 3129 | 5215 | 3619 | 0.666 | 1.665 | 0.867 | 0 | 0 | 0 | 3129 | 5215 | 3619 | 0.666 | 1.665 | 0.867 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | Existing | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.11412 | 0.0089716 | 0.13206 | Cap-Tons/1000 sf | 4012.5 | 5252.5 | 4268.5 | 0.1984 | 0.8404 | 0.3244 | 0 | 0 | 0 | 4012.5 | 5252.5 | 4268.5 | 0.1984 | 0.8404 | 0.3244 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | Existing | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.12139 | 0.0095429 | 0.14047 | Cap-Tons/1000 sf | 2107.5 | 3217.5 | 2326.5 | 0.014063 | 0.040763 | 0.018853 | 0 | 0 | 0 | 2107.5 | 3217.5 | 2326.5 | 0.014063 | 0.040763 | 0.018853 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | Existing | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.14515 | 0.011411 | 0.16797 | Cap-Tons/1000 sf | 3902.5 | 5252.5 | 4177 | 0.23837 | 0.92087 | 0.37237 | 0 | 0 | 0 | 3902.5 | 5252.5 | 4177 | 0.23837 | 0.92087 | 0.37237 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | Existing | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.11708 | 0.0092041 | 0.13549 | Cap-Tons/1000 sf | 2246 | 3516 | 2501 | 0.0067854 | 0.018785 | 0.0089054 | 0 | 0 | 0 | 2246 | 3516 | 2501 | 0.0067854 | 0.018785 | 0.0089054 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ASM | ASSEMBLY | Existing | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.19798 | 0.015564 | 0.2291 | Cap-Tons/1000 sf | 3129 | 5215 | 3768 | 0.23667 | 0.59167 | 0.31407 | 0 | 0 | 0 | 3129 | 5215 | 3768 | 0.23667 | 0.59167 | 0.31407 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | Existing | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.11412 | 0.0089716 | 0.13206 | Cap-Tons/1000 sf | 3802.5 | 5252.5 | 4096.5 | 0.19257 | 0.69757 | 0.28857 | 0 | 0 | 0 | 3802.5 | 5252.5 | 4096.5 | 0.19257 | 0.69757 | 0.28857 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | Existing | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.12139 | 0.0095429 | 0.14047 | Cap-Tons/1000 sf | 1930.5 | 3217.5 | 2215.5 | 0.254 | 0.635 | 0.3313 | 0 | 0 | 0 | 1930.5 | 3217.5 | 2215.5 | 0.254 | 0.635 | 0.3313 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | Existing | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.14515 | 0.011411 | 0.16797 | Cap-Tons/1000 sf | 3792.5 | 5252.5 | 4084 | 0.23095 | 0.82995 | 0.34495 | 0 | 0 | 0 | 3792.5 | 5252.5 | 4084 | 0.23095 | 0.82995 | 0.34495 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | Existing | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.11708 | 0.0092041 | 0.13549 | Cap-Tons/1000 sf | 2109.6 | 3516 | 2443.6 | 0.21 | 0.525 | 0.273 | 0 | 0 | 0 | 2109.6 | 3516 | 2443.6 | 0.21 | 0.525 | 0.273 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EUN | EDUCATION - UNIVERSITY | Existing | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.11392 | 0.0089559 | 0.13183 | Cap-Tons/1000 sf | 3782.5 | 5252.5 | 4071.5 | 0.26932 | 0.96232 | 0.40132 | 0 | 0 | 0 | 3782.5 | 5252.5 | 4071.5 | 0.26932 | 0.96232 | 0.40132 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | GRO | GROCERY | Existing | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.19025 | 0.014956 | 0.22016 | Cap-Tons/1000 sf | 4752 | 7920 | 5802 | 0.184 | 0.46 | 0.2486 | 0 | 0 | 0 | 4752 | 7920 | 5802 | 0.184 | 0.46 | 0.2486 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | Existing | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.16837 | 0.013237 | 0.19485 | Cap-Tons/1000 sf | 8592.5 | 10642.5 | 9037.5 | 0.095671 | 0.49667 | 0.17847 | 0 | 0 | 0 | 8592.5 | 10642.5 | 9037.5 | 0.095671 | 0.49667 | 0.17847 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HTL | LODGING - HOTEL | Existing | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.089751 | 0.0070558 | 0.10386 | Cap-Tons/1000 sf | 4457.5 | 6627.5 | 4984.5 | 0.24974 | 0.76274 | 0.36474 | 0 | 0 | 0 | 4457.5 | 6627.5 | 4984.5 | 0.24974 | 0.76274 | 0.36474 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | MTL | LODGING - MOTEL | Existing | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.089751 | 0.0070558 | 0.10386 | Cap-Tons/1000 sf | 4457.5 | 6627.5 | 4984.5 | 0.24974 | 0.76274 | 0.36474 | 0 | 0 | 0 | 4457.5 | 6627.5 | 4984.5 | 0.24974 | 0.76274 | 0.36474 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | Existing | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.16837 | 0.013237 | 0.19485 | Cap-Tons/1000 sf | 7762.5 | 10642.5 | 8438.5 | 0.09498 | 0.35098 | 0.14788 | 0 | 0 | 0 | 7762.5 | 10642.5 | 8438.5 | 0.09498 | 0.35098 | 0.14788 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFL | OFFICE - LARGE | Existing | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.11956 | 0.0093995 | 0.13836 | Cap-Tons/1000 sf | 8757.5 | 9817.5 | 8981.5 | 0.068145 | 0.63115 | 0.18615 | 0 | 0 | 0 | 8757.5 | 9817.5 | 8981.5 | 0.068145 | 0.63115 | 0.18615 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | SCN | STORAGE - CONDITIONED | Existing | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.052413 | 0.0041205 | 0.060654 | Cap-Tons/1000 sf | 1224 | 2040 | 1657 | 0 | 0 | 0 | 0 | 0 | 0 | 1224 | 2040 | 1657 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ASM | ASSEMBLY | New | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.19798 | 0.015564 | 0.2291 | Cap-Tons/1000 sf | 4593 | 5215 | 5215 | 0.0097776 | 0.081978 | 0.081978 | 0 | 0 | 0 | 4593 | 5215 | 5215 | 0.0097776 | 0.081978 | 0.081978 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | New | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.11412 | 0.0089716 | 0.13206 | Cap-Tons/1000 sf | 4872.5 | 5252.5 | 5252.5 | 0.0071516 | 0.098852 | 0.098852 | 0 | 0 | 0 | 4872.5 | 5252.5 | 5252.5 | 0.0071516 | 0.098852 | 0.098852 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | New | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.12139 | 0.0095429 | 0.14047 | Cap-Tons/1000 sf | 2891.5 | 3217.5 | 3217.5 | 0.0087602 | 0.08646 | 0.08646 | 0 | 0 | 0 | 2891.5 | 3217.5 | 3217.5 | 0.0087602 | 0.08646 | 0.08646 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | New | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.14515 | 0.011411 | 0.16797 | Cap-Tons/1000 sf | 4897.5 | 5252.5 | 5252.5 | 0.0087043 | 0.13105 | 0.13105 | 0 | 0 | 0 | 4897.5 | 5252.5 | 5252.5 | 0.0087043 | 0.13105 | 0.13105 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | New | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.11708 | 0.0092041 | 0.13549 | Cap-Tons/1000 sf | 3099 | 3516 | 3516 | 0.0077103 | 0.06501 | 0.06501 | 0 | 0 | 0 | 3099 | 3516 | 3516 | 0.0077103 | 0.06501 | 0.06501 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EUN | EDUCATION - UNIVERSITY | New | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.11392 | 0.0089559 | 0.13183 | Cap-Tons/1000 sf | 4922.5 | 5252.5 | 5252.5 | 0.010257 | 0.16326 | 0.16326 | 0 | 0 | 0 | 4922.5 | 5252.5 | 5252.5 | 0.010257 | 0.16326 | 0.16326 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | GRO | GROCERY | New | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.19025 | 0.014956 | 0.22016 | Cap-Tons/1000 sf | 7082 | 7920 | 7920 | 0.0052538 | 0.049654 | 0.049654 | 0 | 0 | 0 | 7082 | 7920 | 7920 | 0.0052538 | 0.049654 | 0.049654 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | New | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.16837 | 0.013237 | 0.19485 | Cap-Tons/1000 sf | 10213.5 | 10642.5 | 10642.5 | 0.0033645 | 0.083464 | 0.083464 | 0 | 0 | 0 | 10213.5 | 10642.5 | 10642.5 | 0.0033645 | 0.083464 | 0.083464 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HTL | LODGING - HOTEL | New | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.089751 | 0.0070558 | 0.10386 | Cap-Tons/1000 sf | 6050.5 | 6627.5 | 6627.5 | 0.011539 | 0.13254 | 0.13254 | 0 | 0 | 0 | 6050.5 | 6627.5 | 6627.5 | 0.011539 | 0.13254 | 0.13254 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | MTL | LODGING - MOTEL | New | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.089751 | 0.0070558 | 0.10386 | Cap-Tons/1000 sf | 6050.5 | 6627.5 | 6627.5 | 0.011539 | 0.13254 | 0.13254 | 0 | 0 | 0 | 6050.5 | 6627.5 | 6627.5 | 0.011539 | 0.13254 | 0.13254 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | New | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.16837 | 0.013237 | 0.19485 | Cap-Tons/1000 sf | 9941.5 | 10642.5 | 10642.5 | 0.0032506 | 0.049351 | 0.049351 | 0 | 0 | 0 | 9941.5 | 10642.5 | 10642.5 | 0.0032506 | 0.049351 | 0.049351 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFL | OFFICE - LARGE | New | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.11956 | 0.0093995 | 0.13836 | Cap-Tons/1000 sf | 9563.5 | 9817.5 | 9817.5 | 0.0038511 | 0.14885 | 0.14885 | 0 | 0 | 0 | 9563.5 | 9817.5 | 9817.5 | 0.0038511 | 0.14885 | 0.14885 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFS | OFFICE - SMALL | New | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.13983 | 0.010993 | 0.16182 | Cap-Tons/1000 sf | 6959.5 | 7177.5 | 7177.5 | 0.0040408 | 0.13304 | 0.13304 | 0 | 0 | 0 | 6959.5 | 7177.5 | 7177.5 | 0.0040408 | 0.13304 | 0.13304 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | New | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.24312 | 0.019113 | 0.28135 | Cap-Tons/1000 sf | 14740 | 15840 | 15840 | 0.0055448 | 0.079845 | 0.079845 | 0 | 0 | 0 | 14740 | 15840 | 15840 | 0.0055448 | 0.079845 | 0.079845 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | New | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.16098 | 0.012656 | 0.1863 | Cap-Tons/1000 sf | 14905 | 15840 | 15840 | 0.0058089 | 0.098409 | 0.098409 | 0 | 0 | 0 | 14905 | 15840 | 15840 | 0.0058089 | 0.098409 | 0.098409 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | New | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.076065 | 0.0059798 | 0.088025 | Cap-Tons/1000 sf | 5723.5 | 6077.5 | 6077.5 | 0.0053191 | 0.091319 | 0.091319 | 0 | 0 | 0 | 5723.5 | 6077.5 | 6077.5 | 0.0053191 | 0.091319 | 0.091319 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | New | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.082079 | 0.0064526 | 0.094984 | Cap-Tons/1000 sf | 5560.5 | 6077.5 | 6077.5 | 0.0088049 | 0.1035 | 0.1035 | 0 | 0 | 0 | 5560.5 | 6077.5 | 6077.5 | 0.0088049 | 0.1035 | 0.1035 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTS | RETAIL - SMALL | New | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.09448 | 0.0074275 | 0.10933 | Cap-Tons/1000 sf | 5669.5 | 6077.5 | 6077.5 | 0.0077001 | 0.1147 | 0.1147 | 0 | 0 | 0 | 5669.5 | 6077.5 | 6077.5 | 0.0077001 | 0.1147 | 0.1147 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | SCN | STORAGE - CONDITIONED | New | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.052413 | 0.0041205 | 0.060654 | Cap-Tons/1000 sf | 1602 | 2040 | 2040 | 0 | 0 | 0 | 0 | 0 | 0 | 1602 | 2040 | 2040 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ASM | ASSEMBLY | Existing | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.19798 | 0.015564 | 0.2291 | Cap-Tons/1000 sf | 3129 | 5215 | 3672 | 0.76667 | 1.9167 | 1.0057 | 0 | 0 | 0 | 3129 | 5215 | 3672 | 0.76667 | 1.9167 | 1.0057 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | Existing | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.11412 | 0.0089716 | 0.13206 | Cap-Tons/1000 sf | 3852.5 | 5252.5 | 4148.5 | 0.33142 | 1.2434 | 0.51542 | 0 | 0 | 0 | 3852.5 | 5252.5 | 4148.5 | 0.33142 | 1.2434 | 0.51542 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | Existing | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.12139 | 0.0095429 | 0.14047 | Cap-Tons/1000 sf | 1930.5 | 3217.5 | 2204.5 | 0.138 | 0.345 | 0.1765 | 0 | 0 | 0 | 1930.5 | 3217.5 | 2204.5 | 0.138 | 0.345 | 0.1765 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | Existing | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.14515 | 0.011411 | 0.16797 | Cap-Tons/1000 sf | 3807.5 | 5252.5 | 4110.5 | 0.34015 | 1.2367 | 0.52115 | 0 | 0 | 0 | 3807.5 | 5252.5 | 4110.5 | 0.34015 | 1.2367 | 0.52115 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | Existing | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.11708 | 0.0092041 | 0.13549 | Cap-Tons/1000 sf | 2116 | 3516 | 2410 | 0.15217 | 0.38217 | 0.19537 | 0 | 0 | 0 | 2116 | 3516 | 2410 | 0.15217 | 0.38217 | 0.19537 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EUN | EDUCATION - UNIVERSITY | Existing | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.11392 | 0.0089559 | 0.13183 | Cap-Tons/1000 sf | 3762.5 | 5252.5 | 4072.5 | 0.34889 | 1.2299 | 0.52689 | 0 | 0 | 0 | 3762.5 | 5252.5 | 4072.5 | 0.34889 | 1.2299 | 0.52689 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | GRO | GROCERY | Existing | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.19025 | 0.014956 | 0.22016 | Cap-Tons/1000 sf | 4800 | 7920 | 5543 | 0.42965 | 1.0906 | 0.56865 | 0 | 0 | 0 | 4800 | 7920 | 5543 | 0.42965 | 1.0906 | 0.56865 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | Existing | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.16837 | 0.013237 | 0.19485 | Cap-Tons/1000 sf | 8632.5 | 10642.5 | 9077.5 | 0.15088 | 0.79888 | 0.28788 | 0 | 0 | 0 | 8632.5 | 10642.5 | 9077.5 | 0.15088 | 0.79888 | 0.28788 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HTL | LODGING - HOTEL | Existing | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.089751 | 0.0070558 | 0.10386 | Cap-Tons/1000 sf | 4347.5 | 6627.5 | 4887.5 | 0.47095 | 1.3689 | 0.67095 | 0 | 0 | 0 | 4347.5 | 6627.5 | 4887.5 | 0.47095 | 1.3689 | 0.67095 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | MTL | LODGING - MOTEL | Existing | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.089751 | 0.0070558 | 0.10386 | Cap-Tons/1000 sf | 4347.5 | 6627.5 | 4887.5 | 0.47095 | 1.3689 | 0.67095 | 0 | 0 | 0 | 4347.5 | 6627.5 | 4887.5 | 0.47095 | 1.3689 | 0.67095 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | Existing | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.16837 | 0.013237 | 0.19485 | Cap-Tons/1000 sf | 7922.5 | 10642.5 | 8564.5 | 0.23072 | 0.90272 | 0.37272 | 0 | 0 | 0 | 7922.5 | 10642.5 | 8564.5 | 0.23072 | 0.90272 | 0.37272 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFL | OFFICE - LARGE | Existing | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.11956 | 0.0093995 | 0.13836 | Cap-Tons/1000 sf | 8697.5 | 9817.5 | 8952.5 | 0.10173 | 0.89173 | 0.28073 | 0 | 0 | 0 | 8697.5 | 9817.5 | 8952.5 | 0.10173 | 0.89173 | 0.28073 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFS | OFFICE - SMALL | Existing | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.13983 | 0.010993 | 0.16182 | Cap-Tons/1000 sf | 6097.5 | 7177.5 | 6339.5 | 0.15144 | 1.0064 | 0.33944 | 0 | 0 | 0 | 6097.5 | 7177.5 | 6339.5 | 0.15144 | 1.0064 | 0.33944 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | Existing | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.24312 | 0.019113 | 0.28135 | Cap-Tons/1000 sf | 12640 | 15840 | 13317 | 0.2557 | 1.2657 | 0.4557 | 0 | 0 | 0 | 12640 | 15840 | 13317 | 0.2557 | 1.2657 | 0.4557 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | Existing | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.16098 | 0.012656 | 0.1863 | Cap-Tons/1000 sf | 13170 | 15840 | 13726 | 0.24531 | 1.4553 | 0.48231 | 0 | 0 | 0 | 13170 | 15840 | 13726 | 0.24531 | 1.4553 | 0.48231 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | Existing | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.076065 | 0.0059798 | 0.088025 | Cap-Tons/1000 sf | 4397.5 | 6077.5 | 4766.5 | 0.41642 | 1.5064 | 0.64642 | 0 | 0 | 0 | 4397.5 | 6077.5 | 4766.5 | 0.41642 | 1.5064 | 0.64642 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | Existing | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.082079 | 0.0064526 | 0.094984 | Cap-Tons/1000 sf | 3977.5 | 6077.5 | 4441.5 | 0.55965 | 1.6196 | 0.78365 | 0 | 0 | 0 | 3977.5 | 6077.5 | 4441.5 | 0.55965 | 1.6196 | 0.78365 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTS | RETAIL - SMALL | Existing | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.09448 | 0.0074275 | 0.10933 | Cap-Tons/1000 sf | 4237.5 | 6077.5 | 4646.5 | 0.47764 | 1.5776 | 0.71064 | 0 | 0 | 0 | 4237.5 | 6077.5 | 4646.5 | 0.47764 | 1.5776 | 0.71064 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | SCN | STORAGE - CONDITIONED | Existing | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.052413 | 0.0041205 | 0.060654 | Cap-Tons/1000 sf | 1224 | 2040 | 1538 | 0.44 | 1.1 | 0.59 | 0 | 0 | 0 | 1224 | 2040 | 1538 | 0.44 | 1.1 | 0.59 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ASM | ASSEMBLY | New | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.19798 | 0.015564 | 0.2291 | Cap-Tons/1000 sf | 4667 | 5215 | 5215 | 0.027711 | 0.26371 | 0.26371 | 0 | 0 | 0 | 4667 | 5215 | 5215 | 0.027711 | 0.26371 | 0.26371 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | New | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.11412 | 0.0089716 | 0.13206 | Cap-Tons/1000 sf | 4900.5 | 5252.5 | 5252.5 | 0.015802 | 0.2358 | 0.2358 | 0 | 0 | 0 | 4900.5 | 5252.5 | 5252.5 | 0.015802 | 0.2358 | 0.2358 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | New | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.12139 | 0.0095429 | 0.14047 | Cap-Tons/1000 sf | 2911.5 | 3217.5 | 3217.5 | 0.00099005 | 0.01041 | 0.01041 | 0 | 0 | 0 | 2911.5 | 3217.5 | 3217.5 | 0.00099005 | 0.01041 | 0.01041 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | New | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.14515 | 0.011411 | 0.16797 | Cap-Tons/1000 sf | 4902 | 5252.5 | 5252.5 | 0.015446 | 0.23145 | 0.23145 | 0 | 0 | 0 | 4902 | 5252.5 | 5252.5 | 0.015446 | 0.23145 | 0.23145 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | New | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.11708 | 0.0092041 | 0.13549 | Cap-Tons/1000 sf | 3151 | 3516 | 3516 | 0.0017839 | 0.017184 | 0.017184 | 0 | 0 | 0 | 3151 | 3516 | 3516 | 0.0017839 | 0.017184 | 0.017184 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EUN | EDUCATION - UNIVERSITY | New | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.11392 | 0.0089559 | 0.13183 | Cap-Tons/1000 sf | 4903.5 | 5252.5 | 5252.5 | 0.015089 | 0.22709 | 0.22709 | 0 | 0 | 0 | 4903.5 | 5252.5 | 5252.5 | 0.015089 | 0.22709 | 0.22709 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | GRO | GROCERY | New | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.19025 | 0.014956 | 0.22016 | Cap-Tons/1000 sf | 7224 | 7920 | 7920 | 0.018017 | 0.20502 | 0.20502 | 0 | 0 | 0 | 7224 | 7920 | 7920 | 0.018017 | 0.20502 | 0.20502 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | New | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.16837 | 0.013237 | 0.19485 | Cap-Tons/1000 sf | 10191.5 | 10642.5 | 10642.5 | 0.0063724 | 0.15037 | 0.15037 | 0 | 0 | 0 | 10191.5 | 10642.5 | 10642.5 | 0.0063724 | 0.15037 | 0.15037 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HTL | LODGING - HOTEL | New | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.089751 | 0.0070558 | 0.10386 | Cap-Tons/1000 sf | 5996.5 | 6627.5 | 6627.5 | 0.023676 | 0.24868 | 0.24868 | 0 | 0 | 0 | 5996.5 | 6627.5 | 6627.5 | 0.023676 | 0.24868 | 0.24868 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | MTL | LODGING - MOTEL | New | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.089751 | 0.0070558 | 0.10386 | Cap-Tons/1000 sf | 5996.5 | 6627.5 | 6627.5 | 0.023676 | 0.24868 | 0.24868 | 0 | 0 | 0 | 5996.5 | 6627.5 | 6627.5 | 0.023676 | 0.24868 | 0.24868 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | New | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.16837 | 0.013237 | 0.19485 | Cap-Tons/1000 sf | 9987.5 | 10642.5 | 10642.5 | 0.0093782 | 0.15238 | 0.15238 | 0 | 0 | 0 | 9987.5 | 10642.5 | 10642.5 | 0.0093782 | 0.15238 | 0.15238 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFL | OFFICE - LARGE | New | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.11956 | 0.0093995 | 0.13836 | Cap-Tons/1000 sf | 9518.5 | 9817.5 | 9817.5 | 0.0069422 | 0.22794 | 0.22794 | 0 | 0 | 0 | 9518.5 | 9817.5 | 9817.5 | 0.0069422 | 0.22794 | 0.22794 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFS | OFFICE - SMALL | New | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.13983 | 0.010993 | 0.16182 | Cap-Tons/1000 sf | 6888.5 | 7177.5 | 7177.5 | 0.010027 | 0.24903 | 0.24903 | 0 | 0 | 0 | 6888.5 | 7177.5 | 7177.5 | 0.010027 | 0.24903 | 0.24903 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | New | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.24312 | 0.019113 | 0.28135 | Cap-Tons/1000 sf | 14959 | 15840 | 15840 | 0.014311 | 0.25731 | 0.25731 | 0 | 0 | 0 | 14959 | 15840 | 15840 | 0.014311 | 0.25731 | 0.25731 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | New | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.16098 | 0.012656 | 0.1863 | Cap-Tons/1000 sf | 15244 | 15840 | 15840 | 0.0095007 | 0.2525 | 0.2525 | 0 | 0 | 0 | 15244 | 15840 | 15840 | 0.0095007 | 0.2525 | 0.2525 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | New | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.076065 | 0.0059798 | 0.088025 | Cap-Tons/1000 sf | 5649.5 | 6077.5 | 6077.5 | 0.019697 | 0.2797 | 0.2797 | 0 | 0 | 0 | 5649.5 | 6077.5 | 6077.5 | 0.019697 | 0.2797 | 0.2797 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | New | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.082079 | 0.0064526 | 0.094984 | Cap-Tons/1000 sf | 5570.5 | 6077.5 | 6077.5 | 0.02239 | 0.26839 | 0.26839 | 0 | 0 | 0 | 5570.5 | 6077.5 | 6077.5 | 0.02239 | 0.26839 | 0.26839 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTS | RETAIL - SMALL | New | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.09448 | 0.0074275 | 0.10933 | Cap-Tons/1000 sf | 5611.5 | 6077.5 | 6077.5 | 0.021508 | 0.28051 | 0.28051 | 0 | 0 | 0 | 5611.5 | 6077.5 | 6077.5 | 0.021508 | 0.28051 | 0.28051 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EUN | EDUCATION - UNIVERSITY | Existing | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.11392 | 0.0089559 | 0.13183 | Cap-Tons/1000 sf | 3792.5 | 5252.5 | 4085.5 | 0.27833 | 1.0013 | 0.42033 | 0 | 0 | 0 | 3792.5 | 5252.5 | 4085.5 | 0.27833 | 1.0013 | 0.42033 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | GRO | GROCERY | Existing | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.19025 | 0.014956 | 0.22016 | Cap-Tons/1000 sf | 4752 | 7920 | 5465 | 0.30667 | 0.76667 | 0.39897 | 0 | 0 | 0 | 4752 | 7920 | 5465 | 0.30667 | 0.76667 | 0.39897 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | Existing | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.16837 | 0.013237 | 0.19485 | Cap-Tons/1000 sf | 8572.5 | 10642.5 | 9008.5 | 0.14126 | 0.72626 | 0.26126 | 0 | 0 | 0 | 8572.5 | 10642.5 | 9008.5 | 0.14126 | 0.72626 | 0.26126 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.16837 | 0.013237 | 0.19485 | Cap-Tons/1000 sf | 8482.5 | 10642.5 | 8962.5 | 0.13267 | 0.65367 | 0.24367 | 0 | 0 | 0 | 8482.5 | 10642.5 | 8962.5 | 0.13267 | 0.65367 | 0.24367 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HTL | LODGING - HOTEL | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.089751 | 0.0070558 | 0.10386 | Cap-Tons/1000 sf | 4397.5 | 6627.5 | 4923.5 | 0.33875 | 1.0067 | 0.48775 | 0 | 0 | 0 | 4397.5 | 6627.5 | 4923.5 | 0.33875 | 1.0067 | 0.48775 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | MTL | LODGING - MOTEL | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.089751 | 0.0070558 | 0.10386 | Cap-Tons/1000 sf | 4397.5 | 6627.5 | 4923.5 | 0.33875 | 1.0067 | 0.48775 | 0 | 0 | 0 | 4397.5 | 6627.5 | 4923.5 | 0.33875 | 1.0067 | 0.48775 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.24312 | 0.019113 | 0.28135 | Cap-Tons/1000 sf | 13060 | 15840 | 13656 | 0.13176 | 0.75076 | 0.25476 | 0 | 0 | 0 | 13060 | 15840 | 13656 | 0.13176 | 0.75076 | 0.25476 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.16098 | 0.012656 | 0.1863 | Cap-Tons/1000 sf | 13820 | 15840 | 14247 | 0.095446 | 0.74845 | 0.22445 | 0 | 0 | 0 | 13820 | 15840 | 14247 | 0.095446 | 0.74845 | 0.22445 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.076065 | 0.0059798 | 0.088025 | Cap-Tons/1000 sf | 4637.5 | 6077.5 | 4948.5 | 0.25338 | 1.0694 | 0.42838 | 0 | 0 | 0 | 4637.5 | 6077.5 | 4948.5 | 0.25338 | 1.0694 | 0.42838 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | SCN | STORAGE - CONDITIONED | Existing | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.052413 | 0.0041205 | 0.060654 | Cap-Tons/1000 sf | 1471 | 2040 | 1792 | 0.15627 | 0.56027 | 0.30927 | 0 | 0 | 0 | 1471 | 2040 | 1792 | 0.15627 | 0.56027 | 0.30927 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ASM | ASSEMBLY | New | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.19798 | 0.015564 | 0.2291 | Cap-Tons/1000 sf | 4696 | 5215 | 5215 | 0.028514 | 0.28651 | 0.28651 | 0 | 0 | 0 | 4696 | 5215 | 5215 | 0.028514 | 0.28651 | 0.28651 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | New | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.11412 | 0.0089716 | 0.13206 | Cap-Tons/1000 sf | 4893.5 | 5252.5 | 5252.5 | 0.017167 | 0.25117 | 0.25117 | 0 | 0 | 0 | 4893.5 | 5252.5 | 5252.5 | 0.017167 | 0.25117 | 0.25117 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFL | OFFICE - LARGE | New | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.11956 | 0.0093995 | 0.13836 | Cap-Tons/1000 sf | 9507.5 | 9817.5 | 9817.5 | 0.0071407 | 0.22614 | 0.22614 | 0 | 0 | 0 | 9507.5 | 9817.5 | 9817.5 | 0.0071407 | 0.22614 | 0.22614 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFS | OFFICE - SMALL | New | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.13983 | 0.010993 | 0.16182 | Cap-Tons/1000 sf | 6881.5 | 7177.5 | 7177.5 | 0.0094631 | 0.22946 | 0.22946 | 0 | 0 | 0 | 6881.5 | 7177.5 | 7177.5 | 0.0094631 | 0.22946 | 0.22946 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | New | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.24312 | 0.019113 | 0.28135 | Cap-Tons/1000 sf | 15126 | 15840 | 15840 | 0.011187 | 0.24819 | 0.24819 | 0 | 0 | 0 | 15126 | 15840 | 15840 | 0.011187 | 0.24819 | 0.24819 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | New | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.11412 | 0.0089716 | 0.13206 | Cap-Tons/1000 sf | 4833.5 | 5252.5 | 5252.5 | 0.020198 | 0.2532 | 0.2532 | 0 | 0 | 0 | 4833.5 | 5252.5 | 5252.5 | 0.020198 | 0.2532 | 0.2532 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | New | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.12139 | 0.0095429 | 0.14047 | Cap-Tons/1000 sf | 2876.5 | 3217.5 | 3217.5 | 0.0054176 | 0.051118 | 0.051118 | 0 | 0 | 0 | 2876.5 | 3217.5 | 3217.5 | 0.0054176 | 0.051118 | 0.051118 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | New | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.14515 | 0.011411 | 0.16797 | Cap-Tons/1000 sf | 4843.5 | 5252.5 | 5252.5 | 0.019635 | 0.25214 | 0.25214 | 0 | 0 | 0 | 4843.5 | 5252.5 | 5252.5 | 0.019635 | 0.25214 | 0.25214 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | New | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.11708 | 0.0092041 | 0.13549 | Cap-Tons/1000 sf | 3097 | 3516 | 3516 | 0.0061423 | 0.051542 | 0.051542 | 0 | 0 | 0 | 3097 | 3516 | 3516 | 0.0061423 | 0.051542 | 0.051542 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EUN | EDUCATION - UNIVERSITY | New | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.11392 | 0.0089559 | 0.13183 | Cap-Tons/1000 sf | 4853.5 | 5252.5 | 5252.5 | 0.019072 | 0.25107 | 0.25107 | 0 | 0 | 0 | 4853.5 | 5252.5 | 5252.5 | 0.019072 | 0.25107 | 0.25107 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | GRO | GROCERY | New | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.19025 | 0.014956 | 0.22016 | Cap-Tons/1000 sf | 7296 | 7920 | 7920 | 0.015737 | 0.19974 | 0.19974 | 0 | 0 | 0 | 7296 | 7920 | 7920 | 0.015737 | 0.19974 | 0.19974 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | New | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.16837 | 0.013237 | 0.19485 | Cap-Tons/1000 sf | 10159.5 | 10642.5 | 10642.5 | 0.007369 | 0.16237 | 0.16237 | 0 | 0 | 0 | 10159.5 | 10642.5 | 10642.5 | 0.007369 | 0.16237 | 0.16237 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HTL | LODGING - HOTEL | New | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.089751 | 0.0070558 | 0.10386 | Cap-Tons/1000 sf | 5944.5 | 6627.5 | 6627.5 | 0.026656 | 0.25866 | 0.25866 | 0 | 0 | 0 | 5944.5 | 6627.5 | 6627.5 | 0.026656 | 0.25866 | 0.25866 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | MTL | LODGING - MOTEL | New | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.089751 | 0.0070558 | 0.10386 | Cap-Tons/1000 sf | 5944.5 | 6627.5 | 6627.5 | 0.026656 | 0.25866 | 0.25866 | 0 | 0 | 0 | 5944.5 | 6627.5 | 6627.5 | 0.026656 | 0.25866 | 0.25866 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | New | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.16837 | 0.013237 | 0.19485 | Cap-Tons/1000 sf | 10035.5 | 10642.5 | 10642.5 | 0.0088309 | 0.15483 | 0.15483 | 0 | 0 | 0 | 10035.5 | 10642.5 | 10642.5 | 0.0088309 | 0.15483 | 0.15483 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFL | OFFICE - LARGE | New | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.11956 | 0.0093995 | 0.13836 | Cap-Tons/1000 sf | 9477.5 | 9817.5 | 9817.5 | 0.0083229 | 0.24032 | 0.24032 | 0 | 0 | 0 | 9477.5 | 9817.5 | 9817.5 | 0.0083229 | 0.24032 | 0.24032 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFS | OFFICE - SMALL | New | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.13983 | 0.010993 | 0.16182 | Cap-Tons/1000 sf | 6819.5 | 7177.5 | 7177.5 | 0.012914 | 0.25891 | 0.25891 | 0 | 0 | 0 | 6819.5 | 7177.5 | 7177.5 | 0.012914 | 0.25891 | 0.25891 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.076065 | 0.0059798 | 0.088025 | Cap-Tons/1000 sf | 5535.5 | 6077.5 | 6077.5 | 0.028297 | 0.3173 | 0.3173 | 0 | 0 | 0 | 5535.5 | 6077.5 | 6077.5 | 0.028297 | 0.3173 | 0.3173 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.082079 | 0.0064526 | 0.094984 | Cap-Tons/1000 sf | 5522.5 | 6077.5 | 6077.5 | 0.027737 | 0.30374 | 0.30374 | 0 | 0 | 0 | 5522.5 | 6077.5 | 6077.5 | 0.027737 | 0.30374 | 0.30374 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTS | RETAIL - SMALL | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.09448 | 0.0074275 | 0.10933 | Cap-Tons/1000 sf | 5563.5 | 6077.5 | 6077.5 | 0.026423 | 0.31242 | 0.31242 | 0 | 0 | 0 | 5563.5 | 6077.5 | 6077.5 | 0.026423 | 0.31242 | 0.31242 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | New | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.12139 | 0.0095429 | 0.14047 | Cap-Tons/1000 sf | 2926.5 | 3217.5 | 3217.5 | 0.003709 | 0.041009 | 0.041009 | 0 | 0 | 0 | 2926.5 | 3217.5 | 3217.5 | 0.003709 | 0.041009 | 0.041009 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | New | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.14515 | 0.011411 | 0.16797 | Cap-Tons/1000 sf | 4895.5 | 5252.5 | 5252.5 | 0.016956 | 0.24946 | 0.24946 | 0 | 0 | 0 | 4895.5 | 5252.5 | 5252.5 | 0.016956 | 0.24946 | 0.24946 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | New | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.11708 | 0.0092041 | 0.13549 | Cap-Tons/1000 sf | 3168 | 3516 | 3516 | 0.003592 | 0.036292 | 0.036292 | 0 | 0 | 0 | 3168 | 3516 | 3516 | 0.003592 | 0.036292 | 0.036292 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.16837 | 0.013237 | 0.19485 | Cap-Tons/1000 sf | 10019.5 | 10642.5 | 10642.5 | 0.0089537 | 0.15295 | 0.15295 | 0 | 0 | 0 | 10019.5 | 10642.5 | 10642.5 | 0.0089537 | 0.15295 | 0.15295 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HTL | LODGING - HOTEL | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.089751 | 0.0070558 | 0.10386 | Cap-Tons/1000 sf | 5694.5 | 6627.5 | 6627.5 | 0.034407 | 0.24441 | 0.24441 | 0 | 0 | 0 | 5694.5 | 6627.5 | 6627.5 | 0.034407 | 0.24441 | 0.24441 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | MTL | LODGING - MOTEL | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.089751 | 0.0070558 | 0.10386 | Cap-Tons/1000 sf | 5694.5 | 6627.5 | 6627.5 | 0.034407 | 0.24441 | 0.24441 | 0 | 0 | 0 | 5694.5 | 6627.5 | 6627.5 | 0.034407 | 0.24441 | 0.24441 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.16837 | 0.013237 | 0.19485 | Cap-Tons/1000 sf | 9552.5 | 10642.5 | 10642.5 | 0.014606 | 0.14261 | 0.14261 | 0 | 0 | 0 | 9552.5 | 10642.5 | 10642.5 | 0.014606 | 0.14261 | 0.14261 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFL | OFFICE - LARGE | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.11956 | 0.0093995 | 0.13836 | Cap-Tons/1000 sf | 9491.5 | 9817.5 | 9817.5 | 0.0076249 | 0.22962 | 0.22962 | 0 | 0 | 0 | 9491.5 | 9817.5 | 9817.5 | 0.0076249 | 0.22962 | 0.22962 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFS | OFFICE - SMALL | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.13983 | 0.010993 | 0.16182 | Cap-Tons/1000 sf | 6787.5 | 7177.5 | 7177.5 | 0.013215 | 0.24322 | 0.24322 | 0 | 0 | 0 | 6787.5 | 7177.5 | 7177.5 | 0.013215 | 0.24322 | 0.24322 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HTL | LODGING - HOTEL | Existing | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.089751 | 0.0070558 | 0.10386 | Cap-Tons/1000 sf | 4297.5 | 6627.5 | 4816.5 | 0.42886 | 1.2199 | 0.59786 | 0 | 0 | 0 | 4297.5 | 6627.5 | 4816.5 | 0.42886 | 1.2199 | 0.59786 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | MTL | LODGING - MOTEL | Existing | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.089751 | 0.0070558 | 0.10386 | Cap-Tons/1000 sf | 4297.5 | 6627.5 | 4816.5 | 0.42886 | 1.2199 | 0.59786 | 0 | 0 | 0 | 4297.5 | 6627.5 | 4816.5 | 0.42886 | 1.2199 | 0.59786 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | Existing | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.16837 | 0.013237 | 0.19485 | Cap-Tons/1000 sf | 8202.5 | 10642.5 | 8750.5 | 0.1523 | 0.6643 | 0.2573 | 0 | 0 | 0 | 8202.5 | 10642.5 | 8750.5 | 0.1523 | 0.6643 | 0.2573 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFL | OFFICE - LARGE | Existing | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.11956 | 0.0093995 | 0.13836 | Cap-Tons/1000 sf | 8697.5 | 9817.5 | 8946.5 | 0.08602 | 0.75402 | 0.23402 | 0 | 0 | 0 | 8697.5 | 9817.5 | 8946.5 | 0.08602 | 0.75402 | 0.23402 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFS | OFFICE - SMALL | Existing | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.13983 | 0.010993 | 0.16182 | Cap-Tons/1000 sf | 6216.5 | 7177.5 | 6430.5 | 0.099555 | 0.74356 | 0.24056 | 0 | 0 | 0 | 6216.5 | 7177.5 | 6430.5 | 0.099555 | 0.74356 | 0.24056 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | Existing | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.24312 | 0.019113 | 0.28135 | Cap-Tons/1000 sf | 12870 | 15840 | 13502 | 0.17262 | 0.92062 | 0.31962 | 0 | 0 | 0 | 12870 | 15840 | 13502 | 0.17262 | 0.92062 | 0.31962 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | Existing | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.16098 | 0.012656 | 0.1863 | Cap-Tons/1000 sf | 13640 | 15840 | 14101 | 0.13419 | 0.96619 | 0.29719 | 0 | 0 | 0 | 13640 | 15840 | 14101 | 0.13419 | 0.96619 | 0.29719 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | Existing | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.076065 | 0.0059798 | 0.088025 | Cap-Tons/1000 sf | 4647.5 | 6077.5 | 4949.5 | 0.26646 | 1.1325 | 0.44346 | 0 | 0 | 0 | 4647.5 | 6077.5 | 4949.5 | 0.26646 | 1.1325 | 0.44346 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | Existing | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.082079 | 0.0064526 | 0.094984 | Cap-Tons/1000 sf | 4277.5 | 6077.5 | 4669.5 | 0.37031 | 1.2503 | 0.55231 | 0 | 0 | 0 | 4277.5 | 6077.5 | 4669.5 | 0.37031 | 1.2503 | 0.55231 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTS | RETAIL - SMALL | Existing | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.09448 | 0.0074275 | 0.10933 | Cap-Tons/1000 sf | 4537.5 | 6077.5 | 4865.5 | 0.29697 | 1.172 | 0.47597 | 0 | 0 | 0 | 4537.5 | 6077.5 | 4865.5 | 0.29697 | 1.172 | 0.47597 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | SCN | STORAGE - CONDITIONED | Existing | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.052413 | 0.0041205 | 0.060654 | Cap-Tons/1000 sf | 1224 | 2040 | 1460 | 0.202 | 0.505 | 0.2645 | 0 | 0 | 0 | 1224 | 2040 | 1460 | 0.202 | 0.505 | 0.2645 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ASM | ASSEMBLY | New | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.19798 | 0.015564 | 0.2291 | Cap-Tons/1000 sf | 4748 | 5215 | 5215 | 0.01918 | 0.21418 | 0.21418 | 0 | 0 | 0 | 4748 | 5215 | 5215 | 0.01918 | 0.21418 | 0.21418 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | New | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.11412 | 0.0089716 | 0.13206 | Cap-Tons/1000 sf | 4962.5 | 5252.5 | 5252.5 | 0.0081229 | 0.14712 | 0.14712 | 0 | 0 | 0 | 4962.5 | 5252.5 | 5252.5 | 0.0081229 | 0.14712 | 0.14712 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | New | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.12139 | 0.0095429 | 0.14047 | Cap-Tons/1000 sf | 2989.5 | 3217.5 | 3217.5 | 5.2319e-05 | 0.00073832 | 0.00073832 | 0 | 0 | 0 | 2989.5 | 3217.5 | 3217.5 | 5.2319e-05 | 0.00073832 | 0.00073832 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | New | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.14515 | 0.011411 | 0.16797 | Cap-Tons/1000 sf | 4950.5 | 5252.5 | 5252.5 | 0.0093706 | 0.16237 | 0.16237 | 0 | 0 | 0 | 4950.5 | 5252.5 | 5252.5 | 0.0093706 | 0.16237 | 0.16237 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | New | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.11708 | 0.0092041 | 0.13549 | Cap-Tons/1000 sf | 3219 | 3516 | 3516 | 0 | 0 | 0 | 0 | 0 | 0 | 3219 | 3516 | 3516 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EUN | EDUCATION - UNIVERSITY | New | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.11392 | 0.0089559 | 0.13183 | Cap-Tons/1000 sf | 4938.5 | 5252.5 | 5252.5 | 0.010618 | 0.17762 | 0.17762 | 0 | 0 | 0 | 4938.5 | 5252.5 | 5252.5 | 0.010618 | 0.17762 | 0.17762 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | GRO | GROCERY | New | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.19025 | 0.014956 | 0.22016 | Cap-Tons/1000 sf | 7406 | 7920 | 7920 | 0.0081202 | 0.12512 | 0.12512 | 0 | 0 | 0 | 7406 | 7920 | 7920 | 0.0081202 | 0.12512 | 0.12512 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | New | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.16837 | 0.013237 | 0.19485 | Cap-Tons/1000 sf | 10204.5 | 10642.5 | 10642.5 | 0.0053653 | 0.13037 | 0.13037 | 0 | 0 | 0 | 10204.5 | 10642.5 | 10642.5 | 0.0053653 | 0.13037 | 0.13037 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HTL | LODGING - HOTEL | New | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.089751 | 0.0070558 | 0.10386 | Cap-Tons/1000 sf | 6081.5 | 6627.5 | 6627.5 | 0.016609 | 0.20161 | 0.20161 | 0 | 0 | 0 | 6081.5 | 6627.5 | 6627.5 | 0.016609 | 0.20161 | 0.20161 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | MTL | LODGING - MOTEL | New | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.089751 | 0.0070558 | 0.10386 | Cap-Tons/1000 sf | 6081.5 | 6627.5 | 6627.5 | 0.016609 | 0.20161 | 0.20161 | 0 | 0 | 0 | 6081.5 | 6627.5 | 6627.5 | 0.016609 | 0.20161 | 0.20161 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | New | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.16837 | 0.013237 | 0.19485 | Cap-Tons/1000 sf | 10085.5 | 10642.5 | 10642.5 | 0.0056885 | 0.10869 | 0.10869 | 0 | 0 | 0 | 10085.5 | 10642.5 | 10642.5 | 0.0056885 | 0.10869 | 0.10869 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFL | OFFICE - LARGE | New | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.11956 | 0.0093995 | 0.13836 | Cap-Tons/1000 sf | 9537.5 | 9817.5 | 9817.5 | 0.0053138 | 0.18631 | 0.18631 | 0 | 0 | 0 | 9537.5 | 9817.5 | 9817.5 | 0.0053138 | 0.18631 | 0.18631 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFS | OFFICE - SMALL | New | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.13983 | 0.010993 | 0.16182 | Cap-Tons/1000 sf | 6933.5 | 7177.5 | 7177.5 | 0.0061233 | 0.18012 | 0.18012 | 0 | 0 | 0 | 6933.5 | 7177.5 | 7177.5 | 0.0061233 | 0.18012 | 0.18012 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | New | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.24312 | 0.019113 | 0.28135 | Cap-Tons/1000 sf | 15120 | 15840 | 15840 | 0.0079524 | 0.17495 | 0.17495 | 0 | 0 | 0 | 15120 | 15840 | 15840 | 0.0079524 | 0.17495 | 0.17495 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | New | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.16098 | 0.012656 | 0.1863 | Cap-Tons/1000 sf | 15389 | 15840 | 15840 | 0.0049528 | 0.17395 | 0.17395 | 0 | 0 | 0 | 15389 | 15840 | 15840 | 0.0049528 | 0.17395 | 0.17395 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | New | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.076065 | 0.0059798 | 0.088025 | Cap-Tons/1000 sf | 5739.5 | 6077.5 | 6077.5 | 0.011896 | 0.2139 | 0.2139 | 0 | 0 | 0 | 5739.5 | 6077.5 | 6077.5 | 0.011896 | 0.2139 | 0.2139 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | New | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.082079 | 0.0064526 | 0.094984 | Cap-Tons/1000 sf | 5618.5 | 6077.5 | 6077.5 | 0.017891 | 0.23689 | 0.23689 | 0 | 0 | 0 | 5618.5 | 6077.5 | 6077.5 | 0.017891 | 0.23689 | 0.23689 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTS | RETAIL - SMALL | New | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.09448 | 0.0074275 | 0.10933 | Cap-Tons/1000 sf | 5714.5 | 6077.5 | 6077.5 | 0.01334 | 0.22334 | 0.22334 | 0 | 0 | 0 | 5714.5 | 6077.5 | 6077.5 | 0.01334 | 0.22334 | 0.22334 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | SCN | STORAGE - CONDITIONED | New | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.052413 | 0.0041205 | 0.060654 | Cap-Tons/1000 sf | 1809 | 2040 | 2040 | 0.0043033 | 0.038003 | 0.038003 | 0 | 0 | 0 | 1809 | 2040 | 2040 | 0.0043033 | 0.038003 | 0.038003 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ASM | ASSEMBLY | Existing | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.19798 | 0.015564 | 0.2291 | Cap-Tons/1000 sf | 3129 | 5215 | 3621 | 0.79333 | 1.9833 | 1.0443 | 0 | 0 | 0 | 3129 | 5215 | 3621 | 0.79333 | 1.9833 | 1.0443 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | Existing | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.11412 | 0.0089716 | 0.13206 | Cap-Tons/1000 sf | 3782.5 | 5252.5 | 4093.5 | 0.36454 | 1.3025 | 0.55654 | 0 | 0 | 0 | 3782.5 | 5252.5 | 4093.5 | 0.36454 | 1.3025 | 0.55654 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | Existing | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.12139 | 0.0095429 | 0.14047 | Cap-Tons/1000 sf | 1967.5 | 3217.5 | 2228.5 | 0.080686 | 0.20769 | 0.10439 | 0 | 0 | 0 | 1967.5 | 3217.5 | 2228.5 | 0.080686 | 0.20769 | 0.10439 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | Existing | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.14515 | 0.011411 | 0.16797 | Cap-Tons/1000 sf | 3702.5 | 5252.5 | 4027 | 0.39578 | 1.3393 | 0.58828 | 0 | 0 | 0 | 3702.5 | 5252.5 | 4027 | 0.39578 | 1.3393 | 0.58828 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | Existing | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.11708 | 0.0092041 | 0.13549 | Cap-Tons/1000 sf | 2206 | 3516 | 2480 | 0.070073 | 0.18807 | 0.092173 | 0 | 0 | 0 | 2206 | 3516 | 2480 | 0.070073 | 0.18807 | 0.092173 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EUN | EDUCATION - UNIVERSITY | Existing | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.11392 | 0.0089559 | 0.13183 | Cap-Tons/1000 sf | 3622.5 | 5252.5 | 3960.5 | 0.42702 | 1.376 | 0.62002 | 0 | 0 | 0 | 3622.5 | 5252.5 | 3960.5 | 0.42702 | 1.376 | 0.62002 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | GRO | GROCERY | Existing | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.19025 | 0.014956 | 0.22016 | Cap-Tons/1000 sf | 5270 | 7920 | 5920 | 0.33087 | 0.98887 | 0.47187 | 0 | 0 | 0 | 5270 | 7920 | 5920 | 0.33087 | 0.98887 | 0.47187 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | Existing | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.16837 | 0.013237 | 0.19485 | Cap-Tons/1000 sf | 8522.5 | 10642.5 | 8992.5 | 0.17811 | 0.89411 | 0.33111 | 0 | 0 | 0 | 8522.5 | 10642.5 | 8992.5 | 0.17811 | 0.89411 | 0.33111 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HTL | LODGING - HOTEL | Existing | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.089751 | 0.0070558 | 0.10386 | Cap-Tons/1000 sf | 4367.5 | 6627.5 | 4897.5 | 0.45329 | 1.3293 | 0.64929 | 0 | 0 | 0 | 4367.5 | 6627.5 | 4897.5 | 0.45329 | 1.3293 | 0.64929 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | MTL | LODGING - MOTEL | Existing | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.089751 | 0.0070558 | 0.10386 | Cap-Tons/1000 sf | 4367.5 | 6627.5 | 4897.5 | 0.45329 | 1.3293 | 0.64929 | 0 | 0 | 0 | 4367.5 | 6627.5 | 4897.5 | 0.45329 | 1.3293 | 0.64929 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | Existing | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.16837 | 0.013237 | 0.19485 | Cap-Tons/1000 sf | 8242.5 | 10642.5 | 8808.5 | 0.19771 | 0.87671 | 0.34271 | 0 | 0 | 0 | 8242.5 | 10642.5 | 8808.5 | 0.19771 | 0.87671 | 0.34271 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFL | OFFICE - LARGE | Existing | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.11956 | 0.0093995 | 0.13836 | Cap-Tons/1000 sf | 8627.5 | 9817.5 | 8903.5 | 0.10883 | 0.89783 | 0.29083 | 0 | 0 | 0 | 8627.5 | 9817.5 | 8903.5 | 0.10883 | 0.89783 | 0.29083 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFS | OFFICE - SMALL | Existing | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.13983 | 0.010993 | 0.16182 | Cap-Tons/1000 sf | 6037.5 | 7177.5 | 6293.5 | 0.1537 | 0.9677 | 0.3347 | 0 | 0 | 0 | 6037.5 | 7177.5 | 6293.5 | 0.1537 | 0.9677 | 0.3347 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | Existing | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.24312 | 0.019113 | 0.28135 | Cap-Tons/1000 sf | 12910 | 15840 | 13531 | 0.23603 | 1.276 | 0.44203 | 0 | 0 | 0 | 12910 | 15840 | 13531 | 0.23603 | 1.276 | 0.44203 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | Existing | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.16098 | 0.012656 | 0.1863 | Cap-Tons/1000 sf | 13570 | 15840 | 14048 | 0.19906 | 1.3891 | 0.43706 | 0 | 0 | 0 | 13570 | 15840 | 14048 | 0.19906 | 1.3891 | 0.43706 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | Existing | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.076065 | 0.0059798 | 0.088025 | Cap-Tons/1000 sf | 4357.5 | 6077.5 | 4733.5 | 0.43419 | 1.5342 | 0.66919 | 0 | 0 | 0 | 4357.5 | 6077.5 | 4733.5 | 0.43419 | 1.5342 | 0.66919 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | Existing | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.082079 | 0.0064526 | 0.094984 | Cap-Tons/1000 sf | 4207.5 | 6077.5 | 4627.5 | 0.47111 | 1.5311 | 0.69811 | 0 | 0 | 0 | 4207.5 | 6077.5 | 4627.5 | 0.47111 | 1.5311 | 0.69811 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTS | RETAIL - SMALL | Existing | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.09448 | 0.0074275 | 0.10933 | Cap-Tons/1000 sf | 4447.5 | 6077.5 | 4807.5 | 0.37383 | 1.3938 | 0.59183 | 0 | 0 | 0 | 4447.5 | 6077.5 | 4807.5 | 0.37383 | 1.3938 | 0.59183 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | SCN | STORAGE - CONDITIONED | Existing | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.052413 | 0.0041205 | 0.060654 | Cap-Tons/1000 sf | 1224 | 2040 | 1472 | 0.388 | 0.97 | 0.521 | 0 | 0 | 0 | 1224 | 2040 | 1472 | 0.388 | 0.97 | 0.521 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ASM | ASSEMBLY | New | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.19798 | 0.015564 | 0.2291 | Cap-Tons/1000 sf | 4744 | 5215 | 5215 | 0.024722 | 0.27372 | 0.27372 | 0 | 0 | 0 | 4744 | 5215 | 5215 | 0.024722 | 0.27372 | 0.27372 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | New | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.11412 | 0.0089716 | 0.13206 | Cap-Tons/1000 sf | 4876.5 | 5252.5 | 5252.5 | 0.01812 | 0.25312 | 0.25312 | 0 | 0 | 0 | 4876.5 | 5252.5 | 5252.5 | 0.01812 | 0.25312 | 0.25312 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | New | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.12139 | 0.0095429 | 0.14047 | Cap-Tons/1000 sf | 2919.5 | 3217.5 | 3217.5 | 0.0011636 | 0.012564 | 0.012564 | 0 | 0 | 0 | 2919.5 | 3217.5 | 3217.5 | 0.0011636 | 0.012564 | 0.012564 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | New | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.14515 | 0.011411 | 0.16797 | Cap-Tons/1000 sf | 4875.5 | 5252.5 | 5252.5 | 0.017939 | 0.24994 | 0.24994 | 0 | 0 | 0 | 4875.5 | 5252.5 | 5252.5 | 0.017939 | 0.24994 | 0.24994 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | New | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.11708 | 0.0092041 | 0.13549 | Cap-Tons/1000 sf | 3198 | 3516 | 3516 | 0.0011236 | 0.012424 | 0.012424 | 0 | 0 | 0 | 3198 | 3516 | 3516 | 0.0011236 | 0.012424 | 0.012424 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EUN | EDUCATION - UNIVERSITY | New | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.11392 | 0.0089559 | 0.13183 | Cap-Tons/1000 sf | 4874.5 | 5252.5 | 5252.5 | 0.017758 | 0.24676 | 0.24676 | 0 | 0 | 0 | 4874.5 | 5252.5 | 5252.5 | 0.017758 | 0.24676 | 0.24676 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | GRO | GROCERY | New | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.19025 | 0.014956 | 0.22016 | Cap-Tons/1000 sf | 7288 | 7920 | 7920 | 0.018558 | 0.23256 | 0.23256 | 0 | 0 | 0 | 7288 | 7920 | 7920 | 0.018558 | 0.23256 | 0.23256 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | New | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.16837 | 0.013237 | 0.19485 | Cap-Tons/1000 sf | 10161.5 | 10642.5 | 10642.5 | 0.007763 | 0.17176 | 0.17176 | 0 | 0 | 0 | 10161.5 | 10642.5 | 10642.5 | 0.007763 | 0.17176 | 0.17176 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HTL | LODGING - HOTEL | New | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.089751 | 0.0070558 | 0.10386 | Cap-Tons/1000 sf | 6044.5 | 6627.5 | 6627.5 | 0.021412 | 0.24341 | 0.24341 | 0 | 0 | 0 | 6044.5 | 6627.5 | 6627.5 | 0.021412 | 0.24341 | 0.24341 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | MTL | LODGING - MOTEL | New | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.089751 | 0.0070558 | 0.10386 | Cap-Tons/1000 sf | 6044.5 | 6627.5 | 6627.5 | 0.021412 | 0.24341 | 0.24341 | 0 | 0 | 0 | 6044.5 | 6627.5 | 6627.5 | 0.021412 | 0.24341 | 0.24341 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | New | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.16837 | 0.013237 | 0.19485 | Cap-Tons/1000 sf | 10074.5 | 10642.5 | 10642.5 | 0.0083442 | 0.15634 | 0.15634 | 0 | 0 | 0 | 10074.5 | 10642.5 | 10642.5 | 0.0083442 | 0.15634 | 0.15634 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | New | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.16098 | 0.012656 | 0.1863 | Cap-Tons/1000 sf | 15198 | 15840 | 15840 | 0.011828 | 0.29183 | 0.29183 | 0 | 0 | 0 | 15198 | 15840 | 15840 | 0.011828 | 0.29183 | 0.29183 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | New | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.076065 | 0.0059798 | 0.088025 | Cap-Tons/1000 sf | 5654.5 | 6077.5 | 6077.5 | 0.019824 | 0.28482 | 0.28482 | 0 | 0 | 0 | 5654.5 | 6077.5 | 6077.5 | 0.019824 | 0.28482 | 0.28482 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | New | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.082079 | 0.0064526 | 0.094984 | Cap-Tons/1000 sf | 5608.5 | 6077.5 | 6077.5 | 0.021491 | 0.27849 | 0.27849 | 0 | 0 | 0 | 5608.5 | 6077.5 | 6077.5 | 0.021491 | 0.27849 | 0.27849 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTS | RETAIL - SMALL | New | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.09448 | 0.0074275 | 0.10933 | Cap-Tons/1000 sf | 5681.5 | 6077.5 | 6077.5 | 0.017425 | 0.26742 | 0.26742 | 0 | 0 | 0 | 5681.5 | 6077.5 | 6077.5 | 0.017425 | 0.26742 | 0.26742 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | SCN | STORAGE - CONDITIONED | New | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.052413 | 0.0041205 | 0.060654 | Cap-Tons/1000 sf | 1812 | 2040 | 2040 | 0.01598 | 0.14298 | 0.14298 | 0 | 0 | 0 | 1812 | 2040 | 2040 | 0.01598 | 0.14298 | 0.14298 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ASM | ASSEMBLY | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.19798 | 0.015564 | 0.2291 | Cap-Tons/1000 sf | 3129 | 5215 | 3648 | 0.56933 | 1.4233 | 0.74933 | 0 | 0 | 0 | 3129 | 5215 | 3648 | 0.56933 | 1.4233 | 0.74933 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.11412 | 0.0089716 | 0.13206 | Cap-Tons/1000 sf | 4062.5 | 5252.5 | 4314.5 | 0.20651 | 0.91151 | 0.34951 | 0 | 0 | 0 | 4062.5 | 5252.5 | 4314.5 | 0.20651 | 0.91151 | 0.34951 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.12139 | 0.0095429 | 0.14047 | Cap-Tons/1000 sf | 2117.5 | 3217.5 | 2344.5 | 0.33403 | 0.97703 | 0.46003 | 0 | 0 | 0 | 2117.5 | 3217.5 | 2344.5 | 0.33403 | 0.97703 | 0.46003 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.14515 | 0.011411 | 0.16797 | Cap-Tons/1000 sf | 3857.5 | 5252.5 | 4149 | 0.29315 | 1.0792 | 0.45315 | 0 | 0 | 0 | 3857.5 | 5252.5 | 4149 | 0.29315 | 1.0792 | 0.45315 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.11708 | 0.0092041 | 0.13549 | Cap-Tons/1000 sf | 2436 | 3516 | 2663 | 0.28197 | 0.91797 | 0.40697 | 0 | 0 | 0 | 2436 | 3516 | 2663 | 0.28197 | 0.91797 | 0.40697 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EUN | EDUCATION - UNIVERSITY | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.11392 | 0.0089559 | 0.13183 | Cap-Tons/1000 sf | 3652.5 | 5252.5 | 3983.5 | 0.37979 | 1.2468 | 0.55679 | 0 | 0 | 0 | 3652.5 | 5252.5 | 3983.5 | 0.37979 | 1.2468 | 0.55679 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | GRO | GROCERY | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.19025 | 0.014956 | 0.22016 | Cap-Tons/1000 sf | 5240 | 7920 | 5900 | 0.17594 | 0.51994 | 0.24934 | 0 | 0 | 0 | 5240 | 7920 | 5900 | 0.17594 | 0.51994 | 0.24934 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.082079 | 0.0064526 | 0.094984 | Cap-Tons/1000 sf | 4527.5 | 6077.5 | 4882.5 | 0.22082 | 0.86582 | 0.36182 | 0 | 0 | 0 | 4527.5 | 6077.5 | 4882.5 | 0.22082 | 0.86582 | 0.36182 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTS | RETAIL - SMALL | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.09448 | 0.0074275 | 0.10933 | Cap-Tons/1000 sf | 4537.5 | 6077.5 | 4879.5 | 0.27796 | 1.097 | 0.45296 | 0 | 0 | 0 | 4537.5 | 6077.5 | 4879.5 | 0.27796 | 1.097 | 0.45296 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | SCN | STORAGE - CONDITIONED | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.052413 | 0.0041205 | 0.060654 | Cap-Tons/1000 sf | 1454 | 2040 | 1612 | 0.096726 | 0.33673 | 0.15183 | 0 | 0 | 0 | 1454 | 2040 | 1612 | 0.096726 | 0.33673 | 0.15183 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ASM | ASSEMBLY | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.19798 | 0.015564 | 0.2291 | Cap-Tons/1000 sf | 4719 | 5215 | 5215 | 0.018394 | 0.19339 | 0.19339 | 0 | 0 | 0 | 4719 | 5215 | 5215 | 0.018394 | 0.19339 | 0.19339 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.11412 | 0.0089716 | 0.13206 | Cap-Tons/1000 sf | 4967.5 | 5252.5 | 5252.5 | 0.0091223 | 0.16812 | 0.16812 | 0 | 0 | 0 | 4967.5 | 5252.5 | 5252.5 | 0.0091223 | 0.16812 | 0.16812 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.12139 | 0.0095429 | 0.14047 | Cap-Tons/1000 sf | 2970.5 | 3217.5 | 3217.5 | 0.011558 | 0.15056 | 0.15056 | 0 | 0 | 0 | 2970.5 | 3217.5 | 3217.5 | 0.011558 | 0.15056 | 0.15056 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.14515 | 0.011411 | 0.16797 | Cap-Tons/1000 sf | 4923.5 | 5252.5 | 5252.5 | 0.012511 | 0.19601 | 0.19601 | 0 | 0 | 0 | 4923.5 | 5252.5 | 5252.5 | 0.012511 | 0.19601 | 0.19601 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.11708 | 0.0092041 | 0.13549 | Cap-Tons/1000 sf | 3260 | 3516 | 3516 | 0.010444 | 0.14344 | 0.14344 | 0 | 0 | 0 | 3260 | 3516 | 3516 | 0.010444 | 0.14344 | 0.14344 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EUN | EDUCATION - UNIVERSITY | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.11392 | 0.0089559 | 0.13183 | Cap-Tons/1000 sf | 4879.5 | 5252.5 | 5252.5 | 0.0159 | 0.2239 | 0.2239 | 0 | 0 | 0 | 4879.5 | 5252.5 | 5252.5 | 0.0159 | 0.2239 | 0.2239 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | GRO | GROCERY | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.19025 | 0.014956 | 0.22016 | Cap-Tons/1000 sf | 7380 | 7920 | 7920 | 0.0068415 | 0.10034 | 0.10034 | 0 | 0 | 0 | 7380 | 7920 | 7920 | 0.0068415 | 0.10034 | 0.10034 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.16837 | 0.013237 | 0.19485 | Cap-Tons/1000 sf | 10147.5 | 10642.5 | 10642.5 | 0.0058049 | 0.1248 | 0.1248 | 0 | 0 | 0 | 10147.5 | 10642.5 | 10642.5 | 0.0058049 | 0.1248 | 0.1248 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HTL | LODGING - HOTEL | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.089751 | 0.0070558 | 0.10386 | Cap-Tons/1000 sf | 6056.5 | 6627.5 | 6627.5 | 0.015556 | 0.18056 | 0.18056 | 0 | 0 | 0 | 6056.5 | 6627.5 | 6627.5 | 0.015556 | 0.18056 | 0.18056 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | MTL | LODGING - MOTEL | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.089751 | 0.0070558 | 0.10386 | Cap-Tons/1000 sf | 6056.5 | 6627.5 | 6627.5 | 0.015556 | 0.18056 | 0.18056 | 0 | 0 | 0 | 6056.5 | 6627.5 | 6627.5 | 0.015556 | 0.18056 | 0.18056 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.16837 | 0.013237 | 0.19485 | Cap-Tons/1000 sf | 10080.5 | 10642.5 | 10642.5 | 0.004672 | 0.088472 | 0.088472 | 0 | 0 | 0 | 10080.5 | 10642.5 | 10642.5 | 0.004672 | 0.088472 | 0.088472 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFL | OFFICE - LARGE | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.11956 | 0.0093995 | 0.13836 | Cap-Tons/1000 sf | 9514.5 | 9817.5 | 9817.5 | 0.0055412 | 0.17954 | 0.17954 | 0 | 0 | 0 | 9514.5 | 9817.5 | 9817.5 | 0.0055412 | 0.17954 | 0.17954 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFS | OFFICE - SMALL | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.13983 | 0.010993 | 0.16182 | Cap-Tons/1000 sf | 6922.5 | 7177.5 | 7177.5 | 0.0064832 | 0.18248 | 0.18248 | 0 | 0 | 0 | 6922.5 | 7177.5 | 7177.5 | 0.0064832 | 0.18248 | 0.18248 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.24312 | 0.019113 | 0.28135 | Cap-Tons/1000 sf | 15161 | 15840 | 15840 | 0.0060461 | 0.14105 | 0.14105 | 0 | 0 | 0 | 15161 | 15840 | 15840 | 0.0060461 | 0.14105 | 0.14105 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.16098 | 0.012656 | 0.1863 | Cap-Tons/1000 sf | 15424 | 15840 | 15840 | 0.0033444 | 0.12734 | 0.12734 | 0 | 0 | 0 | 15424 | 15840 | 15840 | 0.0033444 | 0.12734 | 0.12734 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.076065 | 0.0059798 | 0.088025 | Cap-Tons/1000 sf | 5742.5 | 6077.5 | 6077.5 | 0.011726 | 0.21273 | 0.21273 | 0 | 0 | 0 | 5742.5 | 6077.5 | 6077.5 | 0.011726 | 0.21273 | 0.21273 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.082079 | 0.0064526 | 0.094984 | Cap-Tons/1000 sf | 5676.5 | 6077.5 | 6077.5 | 0.01215 | 0.18415 | 0.18415 | 0 | 0 | 0 | 5676.5 | 6077.5 | 6077.5 | 0.01215 | 0.18415 | 0.18415 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTS | RETAIL - SMALL | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.09448 | 0.0074275 | 0.10933 | Cap-Tons/1000 sf | 5700.5 | 6077.5 | 6077.5 | 0.013491 | 0.21749 | 0.21749 | 0 | 0 | 0 | 5700.5 | 6077.5 | 6077.5 | 0.013491 | 0.21749 | 0.21749 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | SCN | STORAGE - CONDITIONED | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.052413 | 0.0041205 | 0.060654 | Cap-Tons/1000 sf | 1894 | 2040 | 2040 | 0.0034688 | 0.048469 | 0.048469 | 0 | 0 | 0 | 1894 | 2040 | 2040 | 0.0034688 | 0.048469 | 0.048469 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ASM | ASSEMBLY | Existing | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.19798 | 0.015564 | 0.2291 | Cap-Tons/1000 sf | 3129 | 5215 | 3699 | 0.70667 | 1.7667 | 0.94067 | 0 | 0 | 0 | 3129 | 5215 | 3699 | 0.70667 | 1.7667 | 0.94067 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | Existing | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.11412 | 0.0089716 | 0.13206 | Cap-Tons/1000 sf | 3562.5 | 5252.5 | 3922.5 | 0.45683 | 1.4198 | 0.65283 | 0 | 0 | 0 | 3562.5 | 5252.5 | 3922.5 | 0.45683 | 1.4198 | 0.65283 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | Existing | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.12139 | 0.0095429 | 0.14047 | Cap-Tons/1000 sf | 1930.5 | 3217.5 | 2241.5 | 0.18067 | 0.45167 | 0.23557 | 0 | 0 | 0 | 1930.5 | 3217.5 | 2241.5 | 0.18067 | 0.45167 | 0.23557 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | Existing | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.14515 | 0.011411 | 0.16797 | Cap-Tons/1000 sf | 3562.5 | 5252.5 | 3919.5 | 0.45565 | 1.4161 | 0.65115 | 0 | 0 | 0 | 3562.5 | 5252.5 | 3919.5 | 0.45565 | 1.4161 | 0.65115 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | Existing | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.11708 | 0.0092041 | 0.13549 | Cap-Tons/1000 sf | 2109.6 | 3516 | 2462.6 | 0.18067 | 0.45167 | 0.23567 | 0 | 0 | 0 | 2109.6 | 3516 | 2462.6 | 0.18067 | 0.45167 | 0.23567 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EUN | EDUCATION - UNIVERSITY | Existing | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.11392 | 0.0089559 | 0.13183 | Cap-Tons/1000 sf | 3562.5 | 5252.5 | 3916.5 | 0.45446 | 1.4125 | 0.64946 | 0 | 0 | 0 | 3562.5 | 5252.5 | 3916.5 | 0.45446 | 1.4125 | 0.64946 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | GRO | GROCERY | Existing | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.19025 | 0.014956 | 0.22016 | Cap-Tons/1000 sf | 5350 | 7920 | 6012 | 0.30456 | 0.93856 | 0.44656 | 0 | 0 | 0 | 5350 | 7920 | 6012 | 0.30456 | 0.93856 | 0.44656 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | Existing | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.16837 | 0.013237 | 0.19485 | Cap-Tons/1000 sf | 8592.5 | 10642.5 | 9060.5 | 0.15961 | 0.82861 | 0.30561 | 0 | 0 | 0 | 8592.5 | 10642.5 | 9060.5 | 0.15961 | 0.82861 | 0.30561 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HTL | LODGING - HOTEL | Existing | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.089751 | 0.0070558 | 0.10386 | Cap-Tons/1000 sf | 4157.5 | 6627.5 | 4715.5 | 0.56321 | 1.5112 | 0.76821 | 0 | 0 | 0 | 4157.5 | 6627.5 | 4715.5 | 0.56321 | 1.5112 | 0.76821 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | MTL | LODGING - MOTEL | Existing | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.089751 | 0.0070558 | 0.10386 | Cap-Tons/1000 sf | 4157.5 | 6627.5 | 4715.5 | 0.56321 | 1.5112 | 0.76821 | 0 | 0 | 0 | 4157.5 | 6627.5 | 4715.5 | 0.56321 | 1.5112 | 0.76821 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | Existing | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.16837 | 0.013237 | 0.19485 | Cap-Tons/1000 sf | 8132.5 | 10642.5 | 8742.5 | 0.20555 | 0.87155 | 0.35055 | 0 | 0 | 0 | 8132.5 | 10642.5 | 8742.5 | 0.20555 | 0.87155 | 0.35055 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFL | OFFICE - LARGE | Existing | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.11956 | 0.0093995 | 0.13836 | Cap-Tons/1000 sf | 8537.5 | 9817.5 | 8826.5 | 0.12759 | 0.97859 | 0.31759 | 0 | 0 | 0 | 8537.5 | 9817.5 | 8826.5 | 0.12759 | 0.97859 | 0.31759 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFS | OFFICE - SMALL | Existing | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.13983 | 0.010993 | 0.16182 | Cap-Tons/1000 sf | 5847.5 | 7177.5 | 6144.5 | 0.20584 | 1.1108 | 0.40284 | 0 | 0 | 0 | 5847.5 | 7177.5 | 6144.5 | 0.20584 | 1.1108 | 0.40284 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | Existing | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.24312 | 0.019113 | 0.28135 | Cap-Tons/1000 sf | 12600 | 15840 | 13295 | 0.26486 | 1.2949 | 0.47086 | 0 | 0 | 0 | 12600 | 15840 | 13295 | 0.26486 | 1.2949 | 0.47086 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | Existing | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.16098 | 0.012656 | 0.1863 | Cap-Tons/1000 sf | 13090 | 15840 | 13669 | 0.2479 | 1.4279 | 0.4829 | 0 | 0 | 0 | 13090 | 15840 | 13669 | 0.2479 | 1.4279 | 0.4829 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | Existing | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.076065 | 0.0059798 | 0.088025 | Cap-Tons/1000 sf | 4127.5 | 6077.5 | 4588.5 | 0.48189 | 1.5019 | 0.70889 | 0 | 0 | 0 | 4127.5 | 6077.5 | 4588.5 | 0.48189 | 1.5019 | 0.70889 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | Existing | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.082079 | 0.0064526 | 0.094984 | Cap-Tons/1000 sf | 3987.5 | 6077.5 | 4484.5 | 0.5147 | 1.4967 | 0.7337 | 0 | 0 | 0 | 3987.5 | 6077.5 | 4484.5 | 0.5147 | 1.4967 | 0.7337 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTS | RETAIL - SMALL | Existing | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.09448 | 0.0074275 | 0.10933 | Cap-Tons/1000 sf | 4157.5 | 6077.5 | 4612.5 | 0.47105 | 1.4911 | 0.69905 | 0 | 0 | 0 | 4157.5 | 6077.5 | 4612.5 | 0.47105 | 1.4911 | 0.69905 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | SCN | STORAGE - CONDITIONED | Existing | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.052413 | 0.0041205 | 0.060654 | Cap-Tons/1000 sf | 1224 | 2040 | 1577 | 0.41333 | 1.0333 | 0.56433 | 0 | 0 | 0 | 1224 | 2040 | 1577 | 0.41333 | 1.0333 | 0.56433 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ASM | ASSEMBLY | New | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.19798 | 0.015564 | 0.2291 | Cap-Tons/1000 sf | 4632 | 5215 | 5215 | 0.02983 | 0.26683 | 0.26683 | 0 | 0 | 0 | 4632 | 5215 | 5215 | 0.02983 | 0.26683 | 0.26683 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | New | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.24312 | 0.019113 | 0.28135 | Cap-Tons/1000 sf | 14996 | 15840 | 15840 | 0.013226 | 0.24823 | 0.24823 | 0 | 0 | 0 | 14996 | 15840 | 15840 | 0.013226 | 0.24823 | 0.24823 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | New | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.16098 | 0.012656 | 0.1863 | Cap-Tons/1000 sf | 15220 | 15840 | 15840 | 0.0092878 | 0.23729 | 0.23729 | 0 | 0 | 0 | 15220 | 15840 | 15840 | 0.0092878 | 0.23729 | 0.23729 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | New | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.076065 | 0.0059798 | 0.088025 | Cap-Tons/1000 sf | 5544.5 | 6077.5 | 6077.5 | 0.023937 | 0.27294 | 0.27294 | 0 | 0 | 0 | 5544.5 | 6077.5 | 6077.5 | 0.023937 | 0.27294 | 0.27294 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | New | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.082079 | 0.0064526 | 0.094984 | Cap-Tons/1000 sf | 5522.5 | 6077.5 | 6077.5 | 0.023919 | 0.26192 | 0.26192 | 0 | 0 | 0 | 5522.5 | 6077.5 | 6077.5 | 0.023919 | 0.26192 | 0.26192 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTS | RETAIL - SMALL | New | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.09448 | 0.0074275 | 0.10933 | Cap-Tons/1000 sf | 5557.5 | 6077.5 | 6077.5 | 0.023392 | 0.27339 | 0.27339 | 0 | 0 | 0 | 5557.5 | 6077.5 | 6077.5 | 0.023392 | 0.27339 | 0.27339 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | SCN | STORAGE - CONDITIONED | New | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.052413 | 0.0041205 | 0.060654 | Cap-Tons/1000 sf | 1672 | 2040 | 2040 | 0.034335 | 0.19033 | 0.19033 | 0 | 0 | 0 | 1672 | 2040 | 2040 | 0.034335 | 0.19033 | 0.19033 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ASM | ASSEMBLY | Existing | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.19798 | 0.015564 | 0.2291 | Cap-Tons/1000 sf | 3129 | 5215 | 3643 | 0.78 | 1.95 | 1.033 | 0 | 0 | 0 | 3129 | 5215 | 3643 | 0.78 | 1.95 | 1.033 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | Existing | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.11412 | 0.0089716 | 0.13206 | Cap-Tons/1000 sf | 3762.5 | 5252.5 | 4080.5 | 0.38017 | 1.3402 | 0.57617 | 0 | 0 | 0 | 3762.5 | 5252.5 | 4080.5 | 0.38017 | 1.3402 | 0.57617 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | Existing | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.12139 | 0.0095429 | 0.14047 | Cap-Tons/1000 sf | 1957.5 | 3217.5 | 2233.5 | 0.16671 | 0.42571 | 0.21791 | 0 | 0 | 0 | 1957.5 | 3217.5 | 2233.5 | 0.16671 | 0.42571 | 0.21791 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | Existing | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.14515 | 0.011411 | 0.16797 | Cap-Tons/1000 sf | 3737.5 | 5252.5 | 4057.5 | 0.38754 | 1.3435 | 0.58254 | 0 | 0 | 0 | 3737.5 | 5252.5 | 4057.5 | 0.38754 | 1.3435 | 0.58254 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | Existing | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.11708 | 0.0092041 | 0.13549 | Cap-Tons/1000 sf | 2146 | 3516 | 2450 | 0.16151 | 0.41451 | 0.21111 | 0 | 0 | 0 | 2146 | 3516 | 2450 | 0.16151 | 0.41451 | 0.21111 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EUN | EDUCATION - UNIVERSITY | Existing | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.11392 | 0.0089559 | 0.13183 | Cap-Tons/1000 sf | 3712.5 | 5252.5 | 4034.5 | 0.3949 | 1.3469 | 0.5889 | 0 | 0 | 0 | 3712.5 | 5252.5 | 4034.5 | 0.3949 | 1.3469 | 0.5889 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | GRO | GROCERY | Existing | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.19025 | 0.014956 | 0.22016 | Cap-Tons/1000 sf | 5460 | 7920 | 6091 | 0.30007 | 0.96607 | 0.44807 | 0 | 0 | 0 | 5460 | 7920 | 6091 | 0.30007 | 0.96607 | 0.44807 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | Existing | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.16837 | 0.013237 | 0.19485 | Cap-Tons/1000 sf | 8642.5 | 10642.5 | 9096.5 | 0.1613 | 0.8583 | 0.3123 | 0 | 0 | 0 | 8642.5 | 10642.5 | 9096.5 | 0.1613 | 0.8583 | 0.3123 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HTL | LODGING - HOTEL | Existing | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.089751 | 0.0070558 | 0.10386 | Cap-Tons/1000 sf | 4387.5 | 6627.5 | 4917.5 | 0.47378 | 1.4018 | 0.68078 | 0 | 0 | 0 | 4387.5 | 6627.5 | 4917.5 | 0.47378 | 1.4018 | 0.68078 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | MTL | LODGING - MOTEL | Existing | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.089751 | 0.0070558 | 0.10386 | Cap-Tons/1000 sf | 4387.5 | 6627.5 | 4917.5 | 0.47378 | 1.4018 | 0.68078 | 0 | 0 | 0 | 4387.5 | 6627.5 | 4917.5 | 0.47378 | 1.4018 | 0.68078 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | Existing | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.16837 | 0.013237 | 0.19485 | Cap-Tons/1000 sf | 8182.5 | 10642.5 | 8778.5 | 0.21436 | 0.92736 | 0.36836 | 0 | 0 | 0 | 8182.5 | 10642.5 | 8778.5 | 0.21436 | 0.92736 | 0.36836 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFL | OFFICE - LARGE | Existing | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.11956 | 0.0093995 | 0.13836 | Cap-Tons/1000 sf | 8677.5 | 9817.5 | 8946.5 | 0.10983 | 0.94583 | 0.30583 | 0 | 0 | 0 | 8677.5 | 9817.5 | 8946.5 | 0.10983 | 0.94583 | 0.30583 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFS | OFFICE - SMALL | Existing | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.13983 | 0.010993 | 0.16182 | Cap-Tons/1000 sf | 5977.5 | 7177.5 | 6246.5 | 0.18811 | 1.1251 | 0.39311 | 0 | 0 | 0 | 5977.5 | 7177.5 | 6246.5 | 0.18811 | 1.1251 | 0.39311 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | Existing | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.24312 | 0.019113 | 0.28135 | Cap-Tons/1000 sf | 12920 | 15840 | 13552 | 0.23731 | 1.2873 | 0.44931 | 0 | 0 | 0 | 12920 | 15840 | 13552 | 0.23731 | 1.2873 | 0.44931 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | Existing | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.16098 | 0.012656 | 0.1863 | Cap-Tons/1000 sf | 13180 | 15840 | 13744 | 0.26237 | 1.5624 | 0.52237 | 0 | 0 | 0 | 13180 | 15840 | 13744 | 0.26237 | 1.5624 | 0.52237 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | Existing | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.076065 | 0.0059798 | 0.088025 | Cap-Tons/1000 sf | 4307.5 | 6077.5 | 4719.5 | 0.43557 | 1.4956 | 0.67057 | 0 | 0 | 0 | 4307.5 | 6077.5 | 4719.5 | 0.43557 | 1.4956 | 0.67057 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | Existing | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.082079 | 0.0064526 | 0.094984 | Cap-Tons/1000 sf | 4157.5 | 6077.5 | 4607.5 | 0.47567 | 1.5057 | 0.70267 | 0 | 0 | 0 | 4157.5 | 6077.5 | 4607.5 | 0.47567 | 1.5057 | 0.70267 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTS | RETAIL - SMALL | Existing | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.09448 | 0.0074275 | 0.10933 | Cap-Tons/1000 sf | 4257.5 | 6077.5 | 4685.5 | 0.4574 | 1.5274 | 0.6944 | 0 | 0 | 0 | 4257.5 | 6077.5 | 4685.5 | 0.4574 | 1.5274 | 0.6944 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EUN | EDUCATION - UNIVERSITY | New | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.11392 | 0.0089559 | 0.13183 | Cap-Tons/1000 sf | 4897.5 | 5252.5 | 5252.5 | 0.016744 | 0.24774 | 0.24774 | 0 | 0 | 0 | 4897.5 | 5252.5 | 5252.5 | 0.016744 | 0.24774 | 0.24774 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | GRO | GROCERY | New | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.19025 | 0.014956 | 0.22016 | Cap-Tons/1000 sf | 7353 | 7920 | 7920 | 0.015345 | 0.21435 | 0.21435 | 0 | 0 | 0 | 7353 | 7920 | 7920 | 0.015345 | 0.21435 | 0.21435 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | New | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.16837 | 0.013237 | 0.19485 | Cap-Tons/1000 sf | 10175.5 | 10642.5 | 10642.5 | 0.0074349 | 0.16943 | 0.16943 | 0 | 0 | 0 | 10175.5 | 10642.5 | 10642.5 | 0.0074349 | 0.16943 | 0.16943 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HTL | LODGING - HOTEL | New | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.089751 | 0.0070558 | 0.10386 | Cap-Tons/1000 sf | 6015.5 | 6627.5 | 6627.5 | 0.024213 | 0.26221 | 0.26221 | 0 | 0 | 0 | 6015.5 | 6627.5 | 6627.5 | 0.024213 | 0.26221 | 0.26221 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | MTL | LODGING - MOTEL | New | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.089751 | 0.0070558 | 0.10386 | Cap-Tons/1000 sf | 6015.5 | 6627.5 | 6627.5 | 0.024213 | 0.26221 | 0.26221 | 0 | 0 | 0 | 6015.5 | 6627.5 | 6627.5 | 0.024213 | 0.26221 | 0.26221 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | New | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.16837 | 0.013237 | 0.19485 | Cap-Tons/1000 sf | 10057.5 | 10642.5 | 10642.5 | 0.0091902 | 0.16719 | 0.16719 | 0 | 0 | 0 | 10057.5 | 10642.5 | 10642.5 | 0.0091902 | 0.16719 | 0.16719 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFL | OFFICE - LARGE | New | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.11956 | 0.0093995 | 0.13836 | Cap-Tons/1000 sf | 9505.5 | 9817.5 | 9817.5 | 0.0079104 | 0.24891 | 0.24891 | 0 | 0 | 0 | 9505.5 | 9817.5 | 9817.5 | 0.0079104 | 0.24891 | 0.24891 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFS | OFFICE - SMALL | New | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.13983 | 0.010993 | 0.16182 | Cap-Tons/1000 sf | 6864.5 | 7177.5 | 7177.5 | 0.01149 | 0.26349 | 0.26349 | 0 | 0 | 0 | 6864.5 | 7177.5 | 7177.5 | 0.01149 | 0.26349 | 0.26349 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | New | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.24312 | 0.019113 | 0.28135 | Cap-Tons/1000 sf | 15082 | 15840 | 15840 | 0.012665 | 0.26467 | 0.26467 | 0 | 0 | 0 | 15082 | 15840 | 15840 | 0.012665 | 0.26467 | 0.26467 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | New | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.16098 | 0.012656 | 0.1863 | Cap-Tons/1000 sf | 15250 | 15840 | 15840 | 0.010252 | 0.27525 | 0.27525 | 0 | 0 | 0 | 15250 | 15840 | 15840 | 0.010252 | 0.27525 | 0.27525 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | New | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.076065 | 0.0059798 | 0.088025 | Cap-Tons/1000 sf | 5613.5 | 6077.5 | 6077.5 | 0.022152 | 0.29015 | 0.29015 | 0 | 0 | 0 | 5613.5 | 6077.5 | 6077.5 | 0.022152 | 0.29015 | 0.29015 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | New | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.082079 | 0.0064526 | 0.094984 | Cap-Tons/1000 sf | 5599.5 | 6077.5 | 6077.5 | 0.021512 | 0.27351 | 0.27351 | 0 | 0 | 0 | 5599.5 | 6077.5 | 6077.5 | 0.021512 | 0.27351 | 0.27351 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTS | RETAIL - SMALL | New | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.09448 | 0.0074275 | 0.10933 | Cap-Tons/1000 sf | 5581.5 | 6077.5 | 6077.5 | 0.02426 | 0.29726 | 0.29726 | 0 | 0 | 0 | 5581.5 | 6077.5 | 6077.5 | 0.02426 | 0.29726 | 0.29726 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | SCN | STORAGE - CONDITIONED | New | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.052413 | 0.0041205 | 0.060654 | Cap-Tons/1000 sf | 1713 | 2040 | 2040 | 0.032452 | 0.20245 | 0.20245 | 0 | 0 | 0 | 1713 | 2040 | 2040 | 0.032452 | 0.20245 | 0.20245 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ASM | ASSEMBLY | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.19798 | 0.015564 | 0.2291 | Cap-Tons/1000 sf | 3129 | 5215 | 3669 | 0.82 | 2.05 | 1.09 | 0 | 0 | 0 | 3129 | 5215 | 3669 | 0.82 | 2.05 | 1.09 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.11412 | 0.0089716 | 0.13206 | Cap-Tons/1000 sf | 3342.5 | 5252.5 | 3744.5 | 0.18971 | 0.52171 | 0.25611 | 0 | 0 | 0 | 3342.5 | 5252.5 | 3744.5 | 0.18971 | 0.52171 | 0.25611 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.12139 | 0.0095429 | 0.14047 | Cap-Tons/1000 sf | 1930.5 | 3217.5 | 2238.5 | 0.242 | 0.605 | 0.3157 | 0 | 0 | 0 | 1930.5 | 3217.5 | 2238.5 | 0.242 | 0.605 | 0.3157 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.14515 | 0.011411 | 0.16797 | Cap-Tons/1000 sf | 3327.5 | 5252.5 | 3728.5 | 0.18768 | 0.51218 | 0.25253 | 0 | 0 | 0 | 3327.5 | 5252.5 | 3728.5 | 0.18768 | 0.51218 | 0.25253 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.11708 | 0.0092041 | 0.13549 | Cap-Tons/1000 sf | 2109.6 | 3516 | 2461.6 | 0.236 | 0.59 | 0.3084 | 0 | 0 | 0 | 2109.6 | 3516 | 2461.6 | 0.236 | 0.59 | 0.3084 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EUN | EDUCATION - UNIVERSITY | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.11392 | 0.0089559 | 0.13183 | Cap-Tons/1000 sf | 3312.5 | 5252.5 | 3712.5 | 0.18565 | 0.50265 | 0.24895 | 0 | 0 | 0 | 3312.5 | 5252.5 | 3712.5 | 0.18565 | 0.50265 | 0.24895 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | GRO | GROCERY | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.19025 | 0.014956 | 0.22016 | Cap-Tons/1000 sf | 5440 | 7920 | 6059 | 0.37565 | 1.1996 | 0.56065 | 0 | 0 | 0 | 5440 | 7920 | 6059 | 0.37565 | 1.1996 | 0.56065 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.16837 | 0.013237 | 0.19485 | Cap-Tons/1000 sf | 8542.5 | 10642.5 | 9019.5 | 0.18241 | 0.92441 | 0.34541 | 0 | 0 | 0 | 8542.5 | 10642.5 | 9019.5 | 0.18241 | 0.92441 | 0.34541 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HTL | LODGING - HOTEL | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.089751 | 0.0070558 | 0.10386 | Cap-Tons/1000 sf | 4077.5 | 6627.5 | 4639.5 | 0.6504 | 1.6904 | 0.8724 | 0 | 0 | 0 | 4077.5 | 6627.5 | 4639.5 | 0.6504 | 1.6904 | 0.8724 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | MTL | LODGING - MOTEL | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.089751 | 0.0070558 | 0.10386 | Cap-Tons/1000 sf | 4077.5 | 6627.5 | 4639.5 | 0.6504 | 1.6904 | 0.8724 | 0 | 0 | 0 | 4077.5 | 6627.5 | 4639.5 | 0.6504 | 1.6904 | 0.8724 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.16837 | 0.013237 | 0.19485 | Cap-Tons/1000 sf | 8302.5 | 10642.5 | 8864.5 | 0.21589 | 0.98189 | 0.38389 | 0 | 0 | 0 | 8302.5 | 10642.5 | 8864.5 | 0.21589 | 0.98189 | 0.38389 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFL | OFFICE - LARGE | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.11956 | 0.0093995 | 0.13836 | Cap-Tons/1000 sf | 8507.5 | 9817.5 | 8800.5 | 0.13889 | 1.0409 | 0.33989 | 0 | 0 | 0 | 8507.5 | 9817.5 | 8800.5 | 0.13889 | 1.0409 | 0.33989 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFS | OFFICE - SMALL | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.13983 | 0.010993 | 0.16182 | Cap-Tons/1000 sf | 5847.5 | 7177.5 | 6143.5 | 0.21835 | 1.1783 | 0.43035 | 0 | 0 | 0 | 5847.5 | 7177.5 | 6143.5 | 0.21835 | 1.1783 | 0.43035 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.24312 | 0.019113 | 0.28135 | Cap-Tons/1000 sf | 12640 | 15840 | 13325 | 0.30633 | 1.5163 | 0.55233 | 0 | 0 | 0 | 12640 | 15840 | 13325 | 0.30633 | 1.5163 | 0.55233 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.16098 | 0.012656 | 0.1863 | Cap-Tons/1000 sf | 13060 | 15840 | 13647 | 0.29162 | 1.6616 | 0.56762 | 0 | 0 | 0 | 13060 | 15840 | 13647 | 0.29162 | 1.6616 | 0.56762 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.076065 | 0.0059798 | 0.088025 | Cap-Tons/1000 sf | 3967.5 | 6077.5 | 4452.5 | 0.62223 | 1.7922 | 0.88423 | 0 | 0 | 0 | 3967.5 | 6077.5 | 4452.5 | 0.62223 | 1.7922 | 0.88423 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.082079 | 0.0064526 | 0.094984 | Cap-Tons/1000 sf | 3987.5 | 6077.5 | 4477.5 | 0.58703 | 1.707 | 0.83803 | 0 | 0 | 0 | 3987.5 | 6077.5 | 4477.5 | 0.58703 | 1.707 | 0.83803 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTS | RETAIL - SMALL | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.09448 | 0.0074275 | 0.10933 | Cap-Tons/1000 sf | 4227.5 | 6077.5 | 4658.5 | 0.48575 | 1.5957 | 0.73575 | 0 | 0 | 0 | 4227.5 | 6077.5 | 4658.5 | 0.48575 | 1.5957 | 0.73575 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | SCN | STORAGE - CONDITIONED | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.052413 | 0.0041205 | 0.060654 | Cap-Tons/1000 sf | 1663 | 2040 | 2040 | 0.053048 | 0.28705 | 0.28705 | 0 | 0 | 0 | 1663 | 2040 | 2040 | 0.053048 | 0.28705 | 0.28705 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ASM | ASSEMBLY | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.19798 | 0.015564 | 0.2291 | Cap-Tons/1000 sf | 4681 | 5215 | 5215 | 0.031029 | 0.30303 | 0.30303 | 0 | 0 | 0 | 4681 | 5215 | 5215 | 0.031029 | 0.30303 | 0.30303 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.11412 | 0.0089716 | 0.13206 | Cap-Tons/1000 sf | 4776.5 | 5252.5 | 5252.5 | 0.0061587 | 0.067959 | 0.067959 | 0 | 0 | 0 | 4776.5 | 5252.5 | 5252.5 | 0.0061587 | 0.067959 | 0.067959 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.12139 | 0.0095429 | 0.14047 | Cap-Tons/1000 sf | 2914.5 | 3217.5 | 3217.5 | 0.0067264 | 0.071426 | 0.071426 | 0 | 0 | 0 | 2914.5 | 3217.5 | 3217.5 | 0.0067264 | 0.071426 | 0.071426 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.14515 | 0.011411 | 0.16797 | Cap-Tons/1000 sf | 4783.5 | 5252.5 | 5252.5 | 0.0059581 | 0.066708 | 0.066708 | 0 | 0 | 0 | 4783.5 | 5252.5 | 5252.5 | 0.0059581 | 0.066708 | 0.066708 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.11708 | 0.0092041 | 0.13549 | Cap-Tons/1000 sf | 3104 | 3516 | 3516 | 0.0093045 | 0.079405 | 0.079405 | 0 | 0 | 0 | 3104 | 3516 | 3516 | 0.0093045 | 0.079405 | 0.079405 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EUN | EDUCATION - UNIVERSITY | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.11392 | 0.0089559 | 0.13183 | Cap-Tons/1000 sf | 4790.5 | 5252.5 | 5252.5 | 0.0057575 | 0.065458 | 0.065458 | 0 | 0 | 0 | 4790.5 | 5252.5 | 5252.5 | 0.0057575 | 0.065458 | 0.065458 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | GRO | GROCERY | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.19025 | 0.014956 | 0.22016 | Cap-Tons/1000 sf | 7298 | 7920 | 7920 | 0.02037 | 0.25937 | 0.25937 | 0 | 0 | 0 | 7298 | 7920 | 7920 | 0.02037 | 0.25937 | 0.25937 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.16837 | 0.013237 | 0.19485 | Cap-Tons/1000 sf | 10154.5 | 10642.5 | 10642.5 | 0.008362 | 0.18236 | 0.18236 | 0 | 0 | 0 | 10154.5 | 10642.5 | 10642.5 | 0.008362 | 0.18236 | 0.18236 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HTL | LODGING - HOTEL | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.089751 | 0.0070558 | 0.10386 | Cap-Tons/1000 sf | 5991.5 | 6627.5 | 6627.5 | 0.02675 | 0.27875 | 0.27875 | 0 | 0 | 0 | 5991.5 | 6627.5 | 6627.5 | 0.02675 | 0.27875 | 0.27875 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | MTL | LODGING - MOTEL | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.089751 | 0.0070558 | 0.10386 | Cap-Tons/1000 sf | 5991.5 | 6627.5 | 6627.5 | 0.02675 | 0.27875 | 0.27875 | 0 | 0 | 0 | 5991.5 | 6627.5 | 6627.5 | 0.02675 | 0.27875 | 0.27875 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.16837 | 0.013237 | 0.19485 | Cap-Tons/1000 sf | 10091.5 | 10642.5 | 10642.5 | 0.0094459 | 0.18245 | 0.18245 | 0 | 0 | 0 | 10091.5 | 10642.5 | 10642.5 | 0.0094459 | 0.18245 | 0.18245 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFL | OFFICE - LARGE | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.11956 | 0.0093995 | 0.13836 | Cap-Tons/1000 sf | 9431.5 | 9817.5 | 9817.5 | 0.010641 | 0.27064 | 0.27064 | 0 | 0 | 0 | 9431.5 | 9817.5 | 9817.5 | 0.010641 | 0.27064 | 0.27064 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFS | OFFICE - SMALL | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.13983 | 0.010993 | 0.16182 | Cap-Tons/1000 sf | 6832.5 | 7177.5 | 7177.5 | 0.013027 | 0.27103 | 0.27103 | 0 | 0 | 0 | 6832.5 | 7177.5 | 7177.5 | 0.013027 | 0.27103 | 0.27103 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.24312 | 0.019113 | 0.28135 | Cap-Tons/1000 sf | 15062 | 15840 | 15840 | 0.014101 | 0.2871 | 0.2871 | 0 | 0 | 0 | 15062 | 15840 | 15840 | 0.014101 | 0.2871 | 0.2871 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.16098 | 0.012656 | 0.1863 | Cap-Tons/1000 sf | 15225 | 15840 | 15840 | 0.010381 | 0.26738 | 0.26738 | 0 | 0 | 0 | 15225 | 15840 | 15840 | 0.010381 | 0.26738 | 0.26738 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | SCN | STORAGE - CONDITIONED | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.052413 | 0.0041205 | 0.060654 | Cap-Tons/1000 sf | 1663 | 2040 | 2040 | 0.053048 | 0.28705 | 0.28705 | 0 | 0 | 0 | 1663 | 2040 | 2040 | 0.053048 | 0.28705 | 0.28705 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ASM | ASSEMBLY | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.19798 | 0.015564 | 0.2291 | Cap-Tons/1000 sf | 3129 | 5215 | 4066 | 0.75333 | 1.8833 | 0.99633 | 0 | 0 | 0 | 3129 | 5215 | 4066 | 0.75333 | 1.8833 | 0.99633 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.11412 | 0.0089716 | 0.13206 | Cap-Tons/1000 sf | 3151.5 | 5252.5 | 3661.5 | 0.62067 | 1.5517 | 0.80367 | 0 | 0 | 0 | 3151.5 | 5252.5 | 3661.5 | 0.62067 | 1.5517 | 0.80367 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.12139 | 0.0095429 | 0.14047 | Cap-Tons/1000 sf | 1930.5 | 3217.5 | 2407.5 | 0.12933 | 0.32333 | 0.16693 | 0 | 0 | 0 | 1930.5 | 3217.5 | 2407.5 | 0.12933 | 0.32333 | 0.16693 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.14515 | 0.011411 | 0.16797 | Cap-Tons/1000 sf | 3157 | 5252.5 | 3630.5 | 0.3047 | 1.5415 | 0.4867 | 0 | 0 | 0 | 3157 | 5252.5 | 3630.5 | 0.3047 | 1.5415 | 0.4867 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.11708 | 0.0092041 | 0.13549 | Cap-Tons/1000 sf | 2109.6 | 3516 | 2674.6 | 0.11 | 0.275 | 0.1422 | 0 | 0 | 0 | 2109.6 | 3516 | 2674.6 | 0.11 | 0.275 | 0.1422 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EUN | EDUCATION - UNIVERSITY | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.11392 | 0.0089559 | 0.13183 | Cap-Tons/1000 sf | 3162.5 | 5252.5 | 3599.5 | 0.60932 | 1.5313 | 0.79032 | 0 | 0 | 0 | 3162.5 | 5252.5 | 3599.5 | 0.60932 | 1.5313 | 0.79032 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | GRO | GROCERY | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.19025 | 0.014956 | 0.22016 | Cap-Tons/1000 sf | 4752 | 7920 | 5852 | 0.42267 | 1.0567 | 0.56167 | 0 | 0 | 0 | 4752 | 7920 | 5852 | 0.42267 | 1.0567 | 0.56167 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.16837 | 0.013237 | 0.19485 | Cap-Tons/1000 sf | 8212.5 | 10642.5 | 8773.5 | 0.19055 | 0.83455 | 0.32755 | 0 | 0 | 0 | 8212.5 | 10642.5 | 8773.5 | 0.19055 | 0.83455 | 0.32755 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HTL | LODGING - HOTEL | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.089751 | 0.0070558 | 0.10386 | Cap-Tons/1000 sf | 3976.5 | 6627.5 | 4638.5 | 0.56867 | 1.4217 | 0.75667 | 0 | 0 | 0 | 3976.5 | 6627.5 | 4638.5 | 0.56867 | 1.4217 | 0.75667 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | MTL | LODGING - MOTEL | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.089751 | 0.0070558 | 0.10386 | Cap-Tons/1000 sf | 3976.5 | 6627.5 | 4638.5 | 5.1486e-05 | 1.4217 | 0.18805 | 0 | 0 | 0 | 3976.5 | 6627.5 | 4638.5 | 5.1486e-05 | 1.4217 | 0.18805 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.16837 | 0.013237 | 0.19485 | Cap-Tons/1000 sf | 6592.5 | 10642.5 | 7566.5 | 0.38703 | 1.017 | 0.51903 | 0 | 0 | 0 | 6592.5 | 10642.5 | 7566.5 | 0.38703 | 1.017 | 0.51903 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFL | OFFICE - LARGE | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.11956 | 0.0093995 | 0.13836 | Cap-Tons/1000 sf | 8527.5 | 9817.5 | 8811.5 | 0.12692 | 0.96592 | 0.30692 | 0 | 0 | 0 | 8527.5 | 9817.5 | 8811.5 | 0.12692 | 0.96592 | 0.30692 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFS | OFFICE - SMALL | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.13983 | 0.010993 | 0.16182 | Cap-Tons/1000 sf | 5757.5 | 7177.5 | 6075.5 | 0.21778 | 1.1008 | 0.40578 | 0 | 0 | 0 | 5757.5 | 7177.5 | 6075.5 | 0.21778 | 1.1008 | 0.40578 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.24312 | 0.019113 | 0.28135 | Cap-Tons/1000 sf | 11140 | 15840 | 12140 | 0.37634 | 1.2683 | 0.55134 | 0 | 0 | 0 | 11140 | 15840 | 12140 | 0.37634 | 1.2683 | 0.55134 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.16098 | 0.012656 | 0.1863 | Cap-Tons/1000 sf | 11400 | 15840 | 12338 | 0.49463 | 1.7646 | 0.74263 | 0 | 0 | 0 | 11400 | 15840 | 12338 | 0.49463 | 1.7646 | 0.74263 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.076065 | 0.0059798 | 0.088025 | Cap-Tons/1000 sf | 3646.5 | 6077.5 | 4384.5 | 0.74 | 1.85 | 0.98 | 0 | 0 | 0 | 3646.5 | 6077.5 | 4384.5 | 0.74 | 1.85 | 0.98 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.082079 | 0.0064526 | 0.094984 | Cap-Tons/1000 sf | 3646.5 | 6077.5 | 4407.5 | 0.65667 | 1.6417 | 0.87467 | 0 | 0 | 0 | 3646.5 | 6077.5 | 4407.5 | 0.65667 | 1.6417 | 0.87467 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EUN | EDUCATION - UNIVERSITY | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.12971 | 0.0088131 | 0.14734 | Cap-Tons/1000 sf | 4879.5 | 5252.5 | 5252.5 | 0.0159 | 0.2239 | 0.2239 | 0 | 0 | 0 | 4879.5 | 5252.5 | 5252.5 | 0.0159 | 0.2239 | 0.2239 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | GRO | GROCERY | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.2306 | 0.015668 | 0.26194 | Cap-Tons/1000 sf | 7380 | 7920 | 7920 | 0.0068415 | 0.10034 | 0.10034 | 0 | 0 | 0 | 7380 | 7920 | 7920 | 0.0068415 | 0.10034 | 0.10034 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.18386 | 0.012492 | 0.20884 | Cap-Tons/1000 sf | 10147.5 | 10642.5 | 10642.5 | 0.0058049 | 0.1248 | 0.1248 | 0 | 0 | 0 | 10147.5 | 10642.5 | 10642.5 | 0.0058049 | 0.1248 | 0.1248 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HTL | LODGING - HOTEL | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.10324 | 0.0070147 | 0.11727 | Cap-Tons/1000 sf | 6056.5 | 6627.5 | 6627.5 | 0.015556 | 0.18056 | 0.18056 | 0 | 0 | 0 | 6056.5 | 6627.5 | 6627.5 | 0.015556 | 0.18056 | 0.18056 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | MTL | LODGING - MOTEL | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.10324 | 0.0070147 | 0.11727 | Cap-Tons/1000 sf | 6056.5 | 6627.5 | 6627.5 | 0.015556 | 0.18056 | 0.18056 | 0 | 0 | 0 | 6056.5 | 6627.5 | 6627.5 | 0.015556 | 0.18056 | 0.18056 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.18386 | 0.012492 | 0.20884 | Cap-Tons/1000 sf | 10080.5 | 10642.5 | 10642.5 | 0.004672 | 0.088472 | 0.088472 | 0 | 0 | 0 | 10080.5 | 10642.5 | 10642.5 | 0.004672 | 0.088472 | 0.088472 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTS | RETAIL - SMALL | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.09448 | 0.0074275 | 0.10933 | Cap-Tons/1000 sf | 3646.5 | 6077.5 | 4281.5 | 0.66667 | 1.6667 | 0.88567 | 0 | 0 | 0 | 3646.5 | 6077.5 | 4281.5 | 0.66667 | 1.6667 | 0.88567 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | SCN | STORAGE - CONDITIONED | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.052413 | 0.0041205 | 0.060654 | Cap-Tons/1000 sf | 1224 | 2040 | 2040 | 0.088667 | 0.22167 | 0.22167 | 0 | 0 | 0 | 1224 | 2040 | 2040 | 0.088667 | 0.22167 | 0.22167 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ASM | ASSEMBLY | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.19798 | 0.015564 | 0.2291 | Cap-Tons/1000 sf | 4035 | 5215 | 5215 | 0.073403 | 0.3244 | 0.3244 | 0 | 0 | 0 | 4035 | 5215 | 5215 | 0.073403 | 0.3244 | 0.3244 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.11412 | 0.0089716 | 0.13206 | Cap-Tons/1000 sf | 4531.5 | 5252.5 | 5252.5 | 0.034049 | 0.24805 | 0.24805 | 0 | 0 | 0 | 4531.5 | 5252.5 | 5252.5 | 0.034049 | 0.24805 | 0.24805 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.12139 | 0.0095429 | 0.14047 | Cap-Tons/1000 sf | 2583.5 | 3217.5 | 3217.5 | 0.0041228 | 0.020923 | 0.020923 | 0 | 0 | 0 | 2583.5 | 3217.5 | 3217.5 | 0.0041228 | 0.020923 | 0.020923 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.14515 | 0.011411 | 0.16797 | Cap-Tons/1000 sf | 4608 | 5252.5 | 5252.5 | 0.029938 | 0.24344 | 0.24344 | 0 | 0 | 0 | 4608 | 5252.5 | 5252.5 | 0.029938 | 0.24344 | 0.24344 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.11708 | 0.0092041 | 0.13549 | Cap-Tons/1000 sf | 2712 | 3516 | 3516 | 0.0048916 | 0.021392 | 0.021392 | 0 | 0 | 0 | 2712 | 3516 | 3516 | 0.0048916 | 0.021392 | 0.021392 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EUN | EDUCATION - UNIVERSITY | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.11392 | 0.0089559 | 0.13183 | Cap-Tons/1000 sf | 4684.5 | 5252.5 | 5252.5 | 0.025826 | 0.23883 | 0.23883 | 0 | 0 | 0 | 4684.5 | 5252.5 | 5252.5 | 0.025826 | 0.23883 | 0.23883 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | GRO | GROCERY | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.19025 | 0.014956 | 0.22016 | Cap-Tons/1000 sf | 6610 | 7920 | 7920 | 0.036466 | 0.22047 | 0.22047 | 0 | 0 | 0 | 6610 | 7920 | 7920 | 0.036466 | 0.22047 | 0.22047 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.24312 | 0.019113 | 0.28135 | Cap-Tons/1000 sf | 14410 | 15840 | 15840 | 0.019748 | 0.21875 | 0.21875 | 0 | 0 | 0 | 14410 | 15840 | 15840 | 0.019748 | 0.21875 | 0.21875 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.16098 | 0.012656 | 0.1863 | Cap-Tons/1000 sf | 14630 | 15840 | 15840 | 0.020842 | 0.27284 | 0.27284 | 0 | 0 | 0 | 14630 | 15840 | 15840 | 0.020842 | 0.27284 | 0.27284 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.076065 | 0.0059798 | 0.088025 | Cap-Tons/1000 sf | 4967.5 | 6077.5 | 6077.5 | 0.057874 | 0.31687 | 0.31687 | 0 | 0 | 0 | 4967.5 | 6077.5 | 6077.5 | 0.057874 | 0.31687 | 0.31687 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.082079 | 0.0064526 | 0.094984 | Cap-Tons/1000 sf | 4957.5 | 6077.5 | 6077.5 | 0.056254 | 0.30525 | 0.30525 | 0 | 0 | 0 | 4957.5 | 6077.5 | 6077.5 | 0.056254 | 0.30525 | 0.30525 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTS | RETAIL - SMALL | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.09448 | 0.0074275 | 0.10933 | Cap-Tons/1000 sf | 5243.5 | 6077.5 | 6077.5 | 0.038968 | 0.28397 | 0.28397 | 0 | 0 | 0 | 5243.5 | 6077.5 | 6077.5 | 0.038968 | 0.28397 | 0.28397 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | SCN | STORAGE - CONDITIONED | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.052413 | 0.0041205 | 0.060654 | Cap-Tons/1000 sf | 1224 | 2040 | 2040 | 0.088667 | 0.22167 | 0.22167 | 0 | 0 | 0 | 1224 | 2040 | 2040 | 0.088667 | 0.22167 | 0.22167 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ASM | ASSEMBLY | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.22241 | 0.015111 | 0.25263 | Cap-Tons/1000 sf | 3129 | 5215 | 3643 | 0.56 | 1.4 | 0.738 | 0 | 0 | 0 | 3129 | 5215 | 3643 | 0.56 | 1.4 | 0.738 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.12957 | 0.0088032 | 0.14717 | Cap-Tons/1000 sf | 4072.5 | 5252.5 | 4325.5 | 0.20224 | 0.90024 | 0.34624 | 0 | 0 | 0 | 4072.5 | 5252.5 | 4325.5 | 0.20224 | 0.90024 | 0.34624 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.14709 | 0.0099939 | 0.16708 | Cap-Tons/1000 sf | 2067.5 | 3217.5 | 2294.5 | 0.371 | 1.038 | 0.498 | 0 | 0 | 0 | 2067.5 | 3217.5 | 2294.5 | 0.371 | 1.038 | 0.498 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.17624 | 0.011975 | 0.20019 | Cap-Tons/1000 sf | 3872.5 | 5252.5 | 4165.5 | 0.28612 | 1.0651 | 0.44662 | 0 | 0 | 0 | 3872.5 | 5252.5 | 4165.5 | 0.28612 | 1.0651 | 0.44662 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.14499 | 0.0098513 | 0.16469 | Cap-Tons/1000 sf | 2386 | 3516 | 2612 | 0.3121 | 0.9711 | 0.4371 | 0 | 0 | 0 | 2386 | 3516 | 2612 | 0.3121 | 0.9711 | 0.4371 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EUN | EDUCATION - UNIVERSITY | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.12971 | 0.0088131 | 0.14734 | Cap-Tons/1000 sf | 3672.5 | 5252.5 | 4005.5 | 0.36999 | 1.23 | 0.54699 | 0 | 0 | 0 | 3672.5 | 5252.5 | 4005.5 | 0.36999 | 1.23 | 0.54699 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | GRO | GROCERY | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.2306 | 0.015668 | 0.26194 | Cap-Tons/1000 sf | 5300 | 7920 | 5956 | 0.16659 | 0.50359 | 0.23949 | 0 | 0 | 0 | 5300 | 7920 | 5956 | 0.16659 | 0.50359 | 0.23949 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.18386 | 0.012492 | 0.20884 | Cap-Tons/1000 sf | 8412.5 | 10642.5 | 8897.5 | 0.14208 | 0.67808 | 0.25508 | 0 | 0 | 0 | 8412.5 | 10642.5 | 8897.5 | 0.14208 | 0.67808 | 0.25508 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HTL | LODGING - HOTEL | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.10324 | 0.0070147 | 0.11727 | Cap-Tons/1000 sf | 4317.5 | 6627.5 | 4854.5 | 0.36757 | 1.0546 | 0.52057 | 0 | 0 | 0 | 4317.5 | 6627.5 | 4854.5 | 0.36757 | 1.0546 | 0.52057 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFL | OFFICE - LARGE | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.13686 | 0.009299 | 0.15546 | Cap-Tons/1000 sf | 9514.5 | 9817.5 | 9817.5 | 0.0055412 | 0.17954 | 0.17954 | 0 | 0 | 0 | 9514.5 | 9817.5 | 9817.5 | 0.0055412 | 0.17954 | 0.17954 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFS | OFFICE - SMALL | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.15528 | 0.01055 | 0.17638 | Cap-Tons/1000 sf | 6922.5 | 7177.5 | 7177.5 | 0.0064832 | 0.18248 | 0.18248 | 0 | 0 | 0 | 6922.5 | 7177.5 | 7177.5 | 0.0064832 | 0.18248 | 0.18248 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.27074 | 0.018395 | 0.30753 | Cap-Tons/1000 sf | 15161 | 15840 | 15840 | 0.0060461 | 0.14105 | 0.14105 | 0 | 0 | 0 | 15161 | 15840 | 15840 | 0.0060461 | 0.14105 | 0.14105 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.18244 | 0.012395 | 0.20723 | Cap-Tons/1000 sf | 15424 | 15840 | 15840 | 0.0033444 | 0.12734 | 0.12734 | 0 | 0 | 0 | 15424 | 15840 | 15840 | 0.0033444 | 0.12734 | 0.12734 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.083286 | 0.0056587 | 0.094603 | Cap-Tons/1000 sf | 5742.5 | 6077.5 | 6077.5 | 0.011726 | 0.21273 | 0.21273 | 0 | 0 | 0 | 5742.5 | 6077.5 | 6077.5 | 0.011726 | 0.21273 | 0.21273 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.096963 | 0.006588 | 0.11014 | Cap-Tons/1000 sf | 5676.5 | 6077.5 | 6077.5 | 0.01215 | 0.18415 | 0.18415 | 0 | 0 | 0 | 5676.5 | 6077.5 | 6077.5 | 0.01215 | 0.18415 | 0.18415 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | MTL | LODGING - MOTEL | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.10324 | 0.0070147 | 0.11727 | Cap-Tons/1000 sf | 4317.5 | 6627.5 | 4854.5 | 0.36757 | 1.0546 | 0.52057 | 0 | 0 | 0 | 4317.5 | 6627.5 | 4854.5 | 0.36757 | 1.0546 | 0.52057 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.18386 | 0.012492 | 0.20884 | Cap-Tons/1000 sf | 8252.5 | 10642.5 | 8807.5 | 0.11961 | 0.53261 | 0.20641 | 0 | 0 | 0 | 8252.5 | 10642.5 | 8807.5 | 0.11961 | 0.53261 | 0.20641 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFL | OFFICE - LARGE | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.13686 | 0.009299 | 0.15546 | Cap-Tons/1000 sf | 8587.5 | 9817.5 | 8858.5 | 0.095392 | 0.76139 | 0.24039 | 0 | 0 | 0 | 8587.5 | 9817.5 | 8858.5 | 0.095392 | 0.76139 | 0.24039 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFS | OFFICE - SMALL | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.15528 | 0.01055 | 0.17638 | Cap-Tons/1000 sf | 6117.5 | 7177.5 | 6340.5 | 0.11835 | 0.80135 | 0.26135 | 0 | 0 | 0 | 6117.5 | 7177.5 | 6340.5 | 0.11835 | 0.80135 | 0.26135 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.27074 | 0.018395 | 0.30753 | Cap-Tons/1000 sf | 13470 | 15840 | 14061 | 0.094659 | 0.63266 | 0.21466 | 0 | 0 | 0 | 13470 | 15840 | 14061 | 0.094659 | 0.63266 | 0.21466 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.18244 | 0.012395 | 0.20723 | Cap-Tons/1000 sf | 14140 | 15840 | 14558 | 0.067447 | 0.62845 | 0.19145 | 0 | 0 | 0 | 14140 | 15840 | 14558 | 0.067447 | 0.62845 | 0.19145 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.083286 | 0.0056587 | 0.094603 | Cap-Tons/1000 sf | 4707.5 | 6077.5 | 5016.5 | 0.22787 | 1.0109 | 0.40087 | 0 | 0 | 0 | 4707.5 | 6077.5 | 5016.5 | 0.22787 | 1.0109 | 0.40087 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.096963 | 0.006588 | 0.11014 | Cap-Tons/1000 sf | 4577.5 | 6077.5 | 4933.5 | 0.20579 | 0.83379 | 0.34779 | 0 | 0 | 0 | 4577.5 | 6077.5 | 4933.5 | 0.20579 | 0.83379 | 0.34779 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTS | RETAIL - SMALL | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.10735 | 0.0072936 | 0.12193 | Cap-Tons/1000 sf | 4597.5 | 6077.5 | 4936.5 | 0.25302 | 1.039 | 0.42702 | 0 | 0 | 0 | 4597.5 | 6077.5 | 4936.5 | 0.25302 | 1.039 | 0.42702 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | SCN | STORAGE - CONDITIONED | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.058722 | 0.0039897 | 0.066701 | Cap-Tons/1000 sf | 1345 | 2040 | 1510 | 0.13642 | 0.40042 | 0.19252 | 0 | 0 | 0 | 1345 | 2040 | 1510 | 0.13642 | 0.40042 | 0.19252 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ASM | ASSEMBLY | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.22241 | 0.015111 | 0.25263 | Cap-Tons/1000 sf | 4719 | 5215 | 5215 | 0.018394 | 0.19339 | 0.19339 | 0 | 0 | 0 | 4719 | 5215 | 5215 | 0.018394 | 0.19339 | 0.19339 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.12957 | 0.0088032 | 0.14717 | Cap-Tons/1000 sf | 4967.5 | 5252.5 | 5252.5 | 0.0091223 | 0.16812 | 0.16812 | 0 | 0 | 0 | 4967.5 | 5252.5 | 5252.5 | 0.0091223 | 0.16812 | 0.16812 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.14709 | 0.0099939 | 0.16708 | Cap-Tons/1000 sf | 2970.5 | 3217.5 | 3217.5 | 0.011558 | 0.15056 | 0.15056 | 0 | 0 | 0 | 2970.5 | 3217.5 | 3217.5 | 0.011558 | 0.15056 | 0.15056 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.17624 | 0.011975 | 0.20019 | Cap-Tons/1000 sf | 4923.5 | 5252.5 | 5252.5 | 0.012511 | 0.19601 | 0.19601 | 0 | 0 | 0 | 4923.5 | 5252.5 | 5252.5 | 0.012511 | 0.19601 | 0.19601 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.14499 | 0.0098513 | 0.16469 | Cap-Tons/1000 sf | 3260 | 3516 | 3516 | 0.010444 | 0.14344 | 0.14344 | 0 | 0 | 0 | 3260 | 3516 | 3516 | 0.010444 | 0.14344 | 0.14344 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.27074 | 0.018395 | 0.30753 | Cap-Tons/1000 sf | 13760 | 15840 | 14256 | 0.08843 | 0.67343 | 0.21843 | 0 | 0 | 0 | 13760 | 15840 | 14256 | 0.08843 | 0.67343 | 0.21843 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.18244 | 0.012395 | 0.20723 | Cap-Tons/1000 sf | 14160 | 15840 | 14558 | 0.083881 | 0.79088 | 0.24088 | 0 | 0 | 0 | 14160 | 15840 | 14558 | 0.083881 | 0.79088 | 0.24088 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.083286 | 0.0056587 | 0.094603 | Cap-Tons/1000 sf | 4677.5 | 6077.5 | 4988.5 | 0.20862 | 0.90562 | 0.36262 | 0 | 0 | 0 | 4677.5 | 6077.5 | 4988.5 | 0.20862 | 0.90562 | 0.36262 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.096963 | 0.006588 | 0.11014 | Cap-Tons/1000 sf | 4357.5 | 6077.5 | 4750.5 | 0.30275 | 1.0698 | 0.47275 | 0 | 0 | 0 | 4357.5 | 6077.5 | 4750.5 | 0.30275 | 1.0698 | 0.47275 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTS | RETAIL - SMALL | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.10735 | 0.0072936 | 0.12193 | Cap-Tons/1000 sf | 4507.5 | 6077.5 | 4859.5 | 0.27482 | 1.0638 | 0.44982 | 0 | 0 | 0 | 4507.5 | 6077.5 | 4859.5 | 0.27482 | 1.0638 | 0.44982 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | SCN | STORAGE - CONDITIONED | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.058722 | 0.0039897 | 0.066701 | Cap-Tons/1000 sf | 1493 | 2040 | 1623 | 0.12274 | 0.45774 | 0.19444 | 0 | 0 | 0 | 1493 | 2040 | 1623 | 0.12274 | 0.45774 | 0.19444 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ASM | ASSEMBLY | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.22241 | 0.015111 | 0.25263 | Cap-Tons/1000 sf | 4843 | 5215 | 5215 | 0.012904 | 0.1809 | 0.1809 | 0 | 0 | 0 | 4843 | 5215 | 5215 | 0.012904 | 0.1809 | 0.1809 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.12957 | 0.0088032 | 0.14717 | Cap-Tons/1000 sf | 5015.5 | 5252.5 | 5252.5 | 0.0052451 | 0.11625 | 0.11625 | 0 | 0 | 0 | 5015.5 | 5252.5 | 5252.5 | 0.0052451 | 0.11625 | 0.11625 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.14709 | 0.0099939 | 0.16708 | Cap-Tons/1000 sf | 3030.5 | 3217.5 | 3217.5 | 0.00028385 | 0.0048838 | 0.0048838 | 0 | 0 | 0 | 3030.5 | 3217.5 | 3217.5 | 0.00028385 | 0.0048838 | 0.0048838 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.17624 | 0.011975 | 0.20019 | Cap-Tons/1000 sf | 4959.5 | 5252.5 | 5252.5 | 0.0080318 | 0.13953 | 0.13953 | 0 | 0 | 0 | 4959.5 | 5252.5 | 5252.5 | 0.0080318 | 0.13953 | 0.13953 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.14499 | 0.0098513 | 0.16469 | Cap-Tons/1000 sf | 3306 | 3516 | 3516 | 0.00014737 | 0.0024674 | 0.0024674 | 0 | 0 | 0 | 3306 | 3516 | 3516 | 0.00014737 | 0.0024674 | 0.0024674 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EUN | EDUCATION - UNIVERSITY | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.12971 | 0.0088131 | 0.14734 | Cap-Tons/1000 sf | 4903.5 | 5252.5 | 5252.5 | 0.010818 | 0.16282 | 0.16282 | 0 | 0 | 0 | 4903.5 | 5252.5 | 5252.5 | 0.010818 | 0.16282 | 0.16282 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | GRO | GROCERY | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.2306 | 0.015668 | 0.26194 | Cap-Tons/1000 sf | 7453 | 7920 | 7920 | 0.0083964 | 0.1424 | 0.1424 | 0 | 0 | 0 | 7453 | 7920 | 7920 | 0.0083964 | 0.1424 | 0.1424 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.18386 | 0.012492 | 0.20884 | Cap-Tons/1000 sf | 10176.5 | 10642.5 | 10642.5 | 0.005495 | 0.1255 | 0.1255 | 0 | 0 | 0 | 10176.5 | 10642.5 | 10642.5 | 0.005495 | 0.1255 | 0.1255 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HTL | LODGING - HOTEL | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.10324 | 0.0070147 | 0.11727 | Cap-Tons/1000 sf | 6122.5 | 6627.5 | 6627.5 | 0.012785 | 0.16778 | 0.16778 | 0 | 0 | 0 | 6122.5 | 6627.5 | 6627.5 | 0.012785 | 0.16778 | 0.16778 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTS | RETAIL - SMALL | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.10735 | 0.0072936 | 0.12193 | Cap-Tons/1000 sf | 5700.5 | 6077.5 | 6077.5 | 0.013491 | 0.21749 | 0.21749 | 0 | 0 | 0 | 5700.5 | 6077.5 | 6077.5 | 0.013491 | 0.21749 | 0.21749 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | SCN | STORAGE - CONDITIONED | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.058722 | 0.0039897 | 0.066701 | Cap-Tons/1000 sf | 1894 | 2040 | 2040 | 0.0034688 | 0.048469 | 0.048469 | 0 | 0 | 0 | 1894 | 2040 | 2040 | 0.0034688 | 0.048469 | 0.048469 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ASM | ASSEMBLY | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.22241 | 0.015111 | 0.25263 | Cap-Tons/1000 sf | 3465 | 5215 | 3856 | 0.40253 | 1.1995 | 0.57153 | 0 | 0 | 0 | 3465 | 5215 | 3856 | 0.40253 | 1.1995 | 0.57153 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.12957 | 0.0088032 | 0.14717 | Cap-Tons/1000 sf | 3822.5 | 5252.5 | 4117.5 | 0.24354 | 0.89454 | 0.37554 | 0 | 0 | 0 | 3822.5 | 5252.5 | 4117.5 | 0.24354 | 0.89454 | 0.37554 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.14709 | 0.0099939 | 0.16708 | Cap-Tons/1000 sf | 2283.5 | 3217.5 | 2466.5 | 0.015543 | 0.053543 | 0.022603 | 0 | 0 | 0 | 2283.5 | 3217.5 | 2466.5 | 0.015543 | 0.053543 | 0.022603 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.17624 | 0.011975 | 0.20019 | Cap-Tons/1000 sf | 3767.5 | 5252.5 | 4076 | 0.25098 | 0.88798 | 0.38148 | 0 | 0 | 0 | 3767.5 | 5252.5 | 4076 | 0.25098 | 0.88798 | 0.38148 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.14499 | 0.0098513 | 0.16469 | Cap-Tons/1000 sf | 2506 | 3516 | 2704 | 0.0093101 | 0.03241 | 0.01353 | 0 | 0 | 0 | 2506 | 3516 | 2704 | 0.0093101 | 0.03241 | 0.01353 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EUN | EDUCATION - UNIVERSITY | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.12971 | 0.0088131 | 0.14734 | Cap-Tons/1000 sf | 3712.5 | 5252.5 | 4034.5 | 0.25843 | 0.88143 | 0.38743 | 0 | 0 | 0 | 3712.5 | 5252.5 | 4034.5 | 0.25843 | 0.88143 | 0.38743 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | GRO | GROCERY | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.2306 | 0.015668 | 0.26194 | Cap-Tons/1000 sf | 5530 | 7920 | 6121 | 0.17936 | 0.59436 | 0.26886 | 0 | 0 | 0 | 5530 | 7920 | 6121 | 0.17936 | 0.59436 | 0.26886 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.18386 | 0.012492 | 0.20884 | Cap-Tons/1000 sf | 8482.5 | 10642.5 | 8946.5 | 0.13725 | 0.67625 | 0.25125 | 0 | 0 | 0 | 8482.5 | 10642.5 | 8946.5 | 0.13725 | 0.67625 | 0.25125 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HTL | LODGING - HOTEL | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.10324 | 0.0070147 | 0.11727 | Cap-Tons/1000 sf | 4217.5 | 6627.5 | 4766.5 | 0.40514 | 1.1141 | 0.56314 | 0 | 0 | 0 | 4217.5 | 6627.5 | 4766.5 | 0.40514 | 1.1141 | 0.56314 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | MTL | LODGING - MOTEL | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.10324 | 0.0070147 | 0.11727 | Cap-Tons/1000 sf | 4217.5 | 6627.5 | 4766.5 | 0.40514 | 1.1141 | 0.56314 | 0 | 0 | 0 | 4217.5 | 6627.5 | 4766.5 | 0.40514 | 1.1141 | 0.56314 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.18386 | 0.012492 | 0.20884 | Cap-Tons/1000 sf | 8592.5 | 10642.5 | 9052.5 | 0.11285 | 0.58585 | 0.21145 | 0 | 0 | 0 | 8592.5 | 10642.5 | 9052.5 | 0.11285 | 0.58585 | 0.21145 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFL | OFFICE - LARGE | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.13686 | 0.009299 | 0.15546 | Cap-Tons/1000 sf | 8427.5 | 9817.5 | 8735.5 | 0.10902 | 0.77002 | 0.25502 | 0 | 0 | 0 | 8427.5 | 9817.5 | 8735.5 | 0.10902 | 0.77002 | 0.25502 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFS | OFFICE - SMALL | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.15528 | 0.01055 | 0.17638 | Cap-Tons/1000 sf | 5987.5 | 7177.5 | 6237.5 | 0.12521 | 0.75521 | 0.25721 | 0 | 0 | 0 | 5987.5 | 7177.5 | 6237.5 | 0.12521 | 0.75521 | 0.25721 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | MTL | LODGING - MOTEL | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.10324 | 0.0070147 | 0.11727 | Cap-Tons/1000 sf | 6122.5 | 6627.5 | 6627.5 | 0.012785 | 0.16778 | 0.16778 | 0 | 0 | 0 | 6122.5 | 6627.5 | 6627.5 | 0.012785 | 0.16778 | 0.16778 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.18386 | 0.012492 | 0.20884 | Cap-Tons/1000 sf | 10253.5 | 10642.5 | 10642.5 | 0.0032323 | 0.088432 | 0.088432 | 0 | 0 | 0 | 10253.5 | 10642.5 | 10642.5 | 0.0032323 | 0.088432 | 0.088432 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFL | OFFICE - LARGE | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.13686 | 0.009299 | 0.15546 | Cap-Tons/1000 sf | 9441.5 | 9817.5 | 9817.5 | 0.007248 | 0.18925 | 0.18925 | 0 | 0 | 0 | 9441.5 | 9817.5 | 9817.5 | 0.007248 | 0.18925 | 0.18925 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFS | OFFICE - SMALL | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.15528 | 0.01055 | 0.17638 | Cap-Tons/1000 sf | 6892.5 | 7177.5 | 7177.5 | 0.0066986 | 0.1687 | 0.1687 | 0 | 0 | 0 | 6892.5 | 7177.5 | 7177.5 | 0.0066986 | 0.1687 | 0.1687 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.27074 | 0.018395 | 0.30753 | Cap-Tons/1000 sf | 15339 | 15840 | 15840 | 0.004638 | 0.14664 | 0.14664 | 0 | 0 | 0 | 15339 | 15840 | 15840 | 0.004638 | 0.14664 | 0.14664 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.18244 | 0.012395 | 0.20723 | Cap-Tons/1000 sf | 15435 | 15840 | 15840 | 0.0044606 | 0.17446 | 0.17446 | 0 | 0 | 0 | 15435 | 15840 | 15840 | 0.0044606 | 0.17446 | 0.17446 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.083286 | 0.0056587 | 0.094603 | Cap-Tons/1000 sf | 5747.5 | 6077.5 | 6077.5 | 0.010335 | 0.19033 | 0.19033 | 0 | 0 | 0 | 5747.5 | 6077.5 | 6077.5 | 0.010335 | 0.19033 | 0.19033 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.096963 | 0.006588 | 0.11014 | Cap-Tons/1000 sf | 5649.5 | 6077.5 | 6077.5 | 0.015 | 0.213 | 0.213 | 0 | 0 | 0 | 5649.5 | 6077.5 | 6077.5 | 0.015 | 0.213 | 0.213 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTS | RETAIL - SMALL | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.10735 | 0.0072936 | 0.12193 | Cap-Tons/1000 sf | 5669.5 | 6077.5 | 6077.5 | 0.0154 | 0.2294 | 0.2294 | 0 | 0 | 0 | 5669.5 | 6077.5 | 6077.5 | 0.0154 | 0.2294 | 0.2294 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFL | OFFICE - LARGE | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.13686 | 0.009299 | 0.15546 | Cap-Tons/1000 sf | 8517.5 | 9817.5 | 8809.5 | 0.13645 | 1.0304 | 0.33645 | 0 | 0 | 0 | 8517.5 | 9817.5 | 8809.5 | 0.13645 | 1.0304 | 0.33645 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFS | OFFICE - SMALL | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.15528 | 0.01055 | 0.17638 | Cap-Tons/1000 sf | 5827.5 | 7177.5 | 6123.5 | 0.2261 | 1.2021 | 0.4371 | 0 | 0 | 0 | 5827.5 | 7177.5 | 6123.5 | 0.2261 | 1.2021 | 0.4371 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.27074 | 0.018395 | 0.30753 | Cap-Tons/1000 sf | 13260 | 15840 | 13945 | 0.19652 | 1.2065 | 0.43752 | 0 | 0 | 0 | 13260 | 15840 | 13945 | 0.19652 | 1.2065 | 0.43752 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.18244 | 0.012395 | 0.20723 | Cap-Tons/1000 sf | 13600 | 15840 | 14176 | 0.18612 | 1.3161 | 0.45212 | 0 | 0 | 0 | 13600 | 15840 | 14176 | 0.18612 | 1.3161 | 0.45212 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.083286 | 0.0056587 | 0.094603 | Cap-Tons/1000 sf | 4117.5 | 6077.5 | 4591.5 | 0.52362 | 1.6236 | 0.77962 | 0 | 0 | 0 | 4117.5 | 6077.5 | 4591.5 | 0.52362 | 1.6236 | 0.77962 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.096963 | 0.006588 | 0.11014 | Cap-Tons/1000 sf | 4127.5 | 6077.5 | 4608.5 | 0.49606 | 1.5461 | 0.74106 | 0 | 0 | 0 | 4127.5 | 6077.5 | 4608.5 | 0.49606 | 1.5461 | 0.74106 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HTL | LODGING - HOTEL | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.10324 | 0.0070147 | 0.11727 | Cap-Tons/1000 sf | 5897.5 | 6627.5 | 6627.5 | 0.030945 | 0.28095 | 0.28095 | 0 | 0 | 0 | 5897.5 | 6627.5 | 6627.5 | 0.030945 | 0.28095 | 0.28095 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | MTL | LODGING - MOTEL | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.10324 | 0.0070147 | 0.11727 | Cap-Tons/1000 sf | 5897.5 | 6627.5 | 6627.5 | 0.030945 | 0.28095 | 0.28095 | 0 | 0 | 0 | 5897.5 | 6627.5 | 6627.5 | 0.030945 | 0.28095 | 0.28095 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.18386 | 0.012492 | 0.20884 | Cap-Tons/1000 sf | 9967.5 | 10642.5 | 10642.5 | 0.01158 | 0.18258 | 0.18258 | 0 | 0 | 0 | 9967.5 | 10642.5 | 10642.5 | 0.01158 | 0.18258 | 0.18258 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFL | OFFICE - LARGE | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.13686 | 0.009299 | 0.15546 | Cap-Tons/1000 sf | 9449.5 | 9817.5 | 9817.5 | 0.0096581 | 0.25766 | 0.25766 | 0 | 0 | 0 | 9449.5 | 9817.5 | 9817.5 | 0.0096581 | 0.25766 | 0.25766 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFS | OFFICE - SMALL | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.15528 | 0.01055 | 0.17638 | Cap-Tons/1000 sf | 6802.5 | 7177.5 | 7177.5 | 0.014553 | 0.27855 | 0.27855 | 0 | 0 | 0 | 6802.5 | 7177.5 | 7177.5 | 0.014553 | 0.27855 | 0.27855 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.27074 | 0.018395 | 0.30753 | Cap-Tons/1000 sf | 14985 | 15840 | 15840 | 0.014949 | 0.27695 | 0.27695 | 0 | 0 | 0 | 14985 | 15840 | 15840 | 0.014949 | 0.27695 | 0.27695 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | SCN | STORAGE - CONDITIONED | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.058722 | 0.0039897 | 0.066701 | Cap-Tons/1000 sf | 1917 | 2040 | 2040 | 0.0041321 | 0.068532 | 0.068532 | 0 | 0 | 0 | 1917 | 2040 | 2040 | 0.0041321 | 0.068532 | 0.068532 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ASM | ASSEMBLY | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.22241 | 0.015111 | 0.25263 | Cap-Tons/1000 sf | 3365 | 5215 | 3773 | 0.45412 | 1.2801 | 0.62912 | 0 | 0 | 0 | 3365 | 5215 | 3773 | 0.45412 | 1.2801 | 0.62912 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.12957 | 0.0088032 | 0.14717 | Cap-Tons/1000 sf | 3672.5 | 5252.5 | 4002.5 | 0.43022 | 1.4302 | 0.63722 | 0 | 0 | 0 | 3672.5 | 5252.5 | 4002.5 | 0.43022 | 1.4302 | 0.63722 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.12957 | 0.0088032 | 0.14717 | Cap-Tons/1000 sf | 3882.5 | 5252.5 | 4207.5 | 0.31899 | 1.223 | 0.52899 | 0 | 0 | 0 | 3882.5 | 5252.5 | 4207.5 | 0.31899 | 1.223 | 0.52899 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.14709 | 0.0099939 | 0.16708 | Cap-Tons/1000 sf | 2177.5 | 3217.5 | 2423.5 | 0.12513 | 0.38713 | 0.18243 | 0 | 0 | 0 | 2177.5 | 3217.5 | 2423.5 | 0.12513 | 0.38713 | 0.18243 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.17624 | 0.011975 | 0.20019 | Cap-Tons/1000 sf | 3802.5 | 5252.5 | 4144 | 0.335 | 1.214 | 0.5385 | 0 | 0 | 0 | 3802.5 | 5252.5 | 4144 | 0.335 | 1.214 | 0.5385 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.14499 | 0.0098513 | 0.16469 | Cap-Tons/1000 sf | 2426 | 3516 | 2685 | 0.11862 | 0.38262 | 0.17642 | 0 | 0 | 0 | 2426 | 3516 | 2685 | 0.11862 | 0.38262 | 0.17642 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EUN | EDUCATION - UNIVERSITY | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.12971 | 0.0088131 | 0.14734 | Cap-Tons/1000 sf | 3722.5 | 5252.5 | 4080.5 | 0.35101 | 1.205 | 0.54801 | 0 | 0 | 0 | 3722.5 | 5252.5 | 4080.5 | 0.35101 | 1.205 | 0.54801 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | GRO | GROCERY | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.2306 | 0.015668 | 0.26194 | Cap-Tons/1000 sf | 6040 | 7920 | 6577 | 0.19672 | 0.82872 | 0.35272 | 0 | 0 | 0 | 6040 | 7920 | 6577 | 0.19672 | 0.82872 | 0.35272 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.18386 | 0.012492 | 0.20884 | Cap-Tons/1000 sf | 8572.5 | 10642.5 | 9065.5 | 0.16348 | 0.84048 | 0.31948 | 0 | 0 | 0 | 8572.5 | 10642.5 | 9065.5 | 0.16348 | 0.84048 | 0.31948 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HTL | LODGING - HOTEL | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.10324 | 0.0070147 | 0.11727 | Cap-Tons/1000 sf | 4397.5 | 6627.5 | 4966.5 | 0.43053 | 1.2795 | 0.63953 | 0 | 0 | 0 | 4397.5 | 6627.5 | 4966.5 | 0.43053 | 1.2795 | 0.63953 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | MTL | LODGING - MOTEL | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.10324 | 0.0070147 | 0.11727 | Cap-Tons/1000 sf | 4397.5 | 6627.5 | 4966.5 | 0.43053 | 1.2795 | 0.63953 | 0 | 0 | 0 | 4397.5 | 6627.5 | 4966.5 | 0.43053 | 1.2795 | 0.63953 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | MTL | LODGING - MOTEL | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.10324 | 0.0070147 | 0.11727 | Cap-Tons/1000 sf | 4237.5 | 6627.5 | 4837.5 | 0.51889 | 1.4389 | 0.73789 | 0 | 0 | 0 | 4237.5 | 6627.5 | 4837.5 | 0.51889 | 1.4389 | 0.73789 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.18386 | 0.012492 | 0.20884 | Cap-Tons/1000 sf | 8052.5 | 10642.5 | 8693.5 | 0.23673 | 0.97273 | 0.40073 | 0 | 0 | 0 | 8052.5 | 10642.5 | 8693.5 | 0.23673 | 0.97273 | 0.40073 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFL | OFFICE - LARGE | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.13686 | 0.009299 | 0.15546 | Cap-Tons/1000 sf | 8437.5 | 9817.5 | 8753.5 | 0.14295 | 1.0169 | 0.34295 | 0 | 0 | 0 | 8437.5 | 9817.5 | 8753.5 | 0.14295 | 1.0169 | 0.34295 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFS | OFFICE - SMALL | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.15528 | 0.01055 | 0.17638 | Cap-Tons/1000 sf | 5827.5 | 7177.5 | 6140.5 | 0.21776 | 1.1578 | 0.43176 | 0 | 0 | 0 | 5827.5 | 7177.5 | 6140.5 | 0.21776 | 1.1578 | 0.43176 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.27074 | 0.018395 | 0.30753 | Cap-Tons/1000 sf | 13390 | 15840 | 14077 | 0.16852 | 1.0895 | 0.39352 | 0 | 0 | 0 | 13390 | 15840 | 14077 | 0.16852 | 1.0895 | 0.39352 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.18244 | 0.012395 | 0.20723 | Cap-Tons/1000 sf | 13760 | 15840 | 14328 | 0.15721 | 1.1972 | 0.41021 | 0 | 0 | 0 | 13760 | 15840 | 14328 | 0.15721 | 1.1972 | 0.41021 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.14709 | 0.0099939 | 0.16708 | Cap-Tons/1000 sf | 2057.5 | 3217.5 | 2284.5 | 0.51305 | 1.423 | 0.68705 | 0 | 0 | 0 | 2057.5 | 3217.5 | 2284.5 | 0.51305 | 1.423 | 0.68705 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.17624 | 0.011975 | 0.20019 | Cap-Tons/1000 sf | 3562.5 | 5252.5 | 3915 | 0.48101 | 1.491 | 0.69001 | 0 | 0 | 0 | 3562.5 | 5252.5 | 3915 | 0.48101 | 1.491 | 0.69001 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.14499 | 0.0098513 | 0.16469 | Cap-Tons/1000 sf | 2346 | 3516 | 2575 | 0.47678 | 1.4328 | 0.65978 | 0 | 0 | 0 | 2346 | 3516 | 2575 | 0.47678 | 1.4328 | 0.65978 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EUN | EDUCATION - UNIVERSITY | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.12971 | 0.0088131 | 0.14734 | Cap-Tons/1000 sf | 3452.5 | 5252.5 | 3827.5 | 0.53179 | 1.5518 | 0.74279 | 0 | 0 | 0 | 3452.5 | 5252.5 | 3827.5 | 0.53179 | 1.5518 | 0.74279 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | GRO | GROCERY | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.2306 | 0.015668 | 0.26194 | Cap-Tons/1000 sf | 5660 | 7920 | 6209 | 0.21961 | 0.76961 | 0.33761 | 0 | 0 | 0 | 5660 | 7920 | 6209 | 0.21961 | 0.76961 | 0.33761 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.18386 | 0.012492 | 0.20884 | Cap-Tons/1000 sf | 8302.5 | 10642.5 | 8805.5 | 0.18348 | 0.83448 | 0.32048 | 0 | 0 | 0 | 8302.5 | 10642.5 | 8805.5 | 0.18348 | 0.83448 | 0.32048 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HTL | LODGING - HOTEL | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.10324 | 0.0070147 | 0.11727 | Cap-Tons/1000 sf | 4007.5 | 6627.5 | 4604.5 | 0.5714 | 1.4454 | 0.7664 | 0 | 0 | 0 | 4007.5 | 6627.5 | 4604.5 | 0.5714 | 1.4454 | 0.7664 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | MTL | LODGING - MOTEL | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.10324 | 0.0070147 | 0.11727 | Cap-Tons/1000 sf | 4007.5 | 6627.5 | 4604.5 | 0.5714 | 1.4454 | 0.7664 | 0 | 0 | 0 | 4007.5 | 6627.5 | 4604.5 | 0.5714 | 1.4454 | 0.7664 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.18386 | 0.012492 | 0.20884 | Cap-Tons/1000 sf | 8362.5 | 10642.5 | 8874.5 | 0.17586 | 0.82086 | 0.31086 | 0 | 0 | 0 | 8362.5 | 10642.5 | 8874.5 | 0.17586 | 0.82086 | 0.31086 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFL | OFFICE - LARGE | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.13686 | 0.009299 | 0.15546 | Cap-Tons/1000 sf | 8357.5 | 9817.5 | 8675.5 | 0.1415 | 0.9515 | 0.3185 | 0 | 0 | 0 | 8357.5 | 9817.5 | 8675.5 | 0.1415 | 0.9515 | 0.3185 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFS | OFFICE - SMALL | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.15528 | 0.01055 | 0.17638 | Cap-Tons/1000 sf | 5827.5 | 7177.5 | 6110.5 | 0.19969 | 1.0617 | 0.38069 | 0 | 0 | 0 | 5827.5 | 7177.5 | 6110.5 | 0.19969 | 1.0617 | 0.38069 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.27074 | 0.018395 | 0.30753 | Cap-Tons/1000 sf | 13610 | 15840 | 14141 | 0.13026 | 0.92526 | 0.30726 | 0 | 0 | 0 | 13610 | 15840 | 14141 | 0.13026 | 0.92526 | 0.30726 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.18244 | 0.012395 | 0.20723 | Cap-Tons/1000 sf | 14010 | 15840 | 14437 | 0.11403 | 0.98703 | 0.30803 | 0 | 0 | 0 | 14010 | 15840 | 14437 | 0.11403 | 0.98703 | 0.30803 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.083286 | 0.0056587 | 0.094603 | Cap-Tons/1000 sf | 4197.5 | 6077.5 | 4616.5 | 0.40175 | 1.2988 | 0.60075 | 0 | 0 | 0 | 4197.5 | 6077.5 | 4616.5 | 0.40175 | 1.2988 | 0.60075 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.096963 | 0.006588 | 0.11014 | Cap-Tons/1000 sf | 4167.5 | 6077.5 | 4600.5 | 0.39415 | 1.2541 | 0.58415 | 0 | 0 | 0 | 4167.5 | 6077.5 | 4600.5 | 0.39415 | 1.2541 | 0.58415 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTS | RETAIL - SMALL | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.10735 | 0.0072936 | 0.12193 | Cap-Tons/1000 sf | 4377.5 | 6077.5 | 4759.5 | 0.33437 | 1.1954 | 0.52537 | 0 | 0 | 0 | 4377.5 | 6077.5 | 4759.5 | 0.33437 | 1.1954 | 0.52537 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | SCN | STORAGE - CONDITIONED | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.058722 | 0.0039897 | 0.066701 | Cap-Tons/1000 sf | 1247 | 2040 | 1426 | 0.38664 | 0.99464 | 0.51564 | 0 | 0 | 0 | 1247 | 2040 | 1426 | 0.38664 | 0.99464 | 0.51564 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ASM | ASSEMBLY | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.22241 | 0.015111 | 0.25263 | Cap-Tons/1000 sf | 4823 | 5215 | 5215 | 0.014224 | 0.18922 | 0.18922 | 0 | 0 | 0 | 4823 | 5215 | 5215 | 0.014224 | 0.18922 | 0.18922 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.12957 | 0.0088032 | 0.14717 | Cap-Tons/1000 sf | 4894.5 | 5252.5 | 5252.5 | 0.016896 | 0.2479 | 0.2479 | 0 | 0 | 0 | 4894.5 | 5252.5 | 5252.5 | 0.016896 | 0.2479 | 0.2479 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.14709 | 0.0099939 | 0.16708 | Cap-Tons/1000 sf | 2978.5 | 3217.5 | 3217.5 | 0.015567 | 0.20957 | 0.20957 | 0 | 0 | 0 | 2978.5 | 3217.5 | 3217.5 | 0.015567 | 0.20957 | 0.20957 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.17624 | 0.011975 | 0.20019 | Cap-Tons/1000 sf | 4863.5 | 5252.5 | 5252.5 | 0.019008 | 0.25601 | 0.25601 | 0 | 0 | 0 | 4863.5 | 5252.5 | 5252.5 | 0.019008 | 0.25601 | 0.25601 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.14499 | 0.0098513 | 0.16469 | Cap-Tons/1000 sf | 3272 | 3516 | 3516 | 0.015287 | 0.22029 | 0.22029 | 0 | 0 | 0 | 3272 | 3516 | 3516 | 0.015287 | 0.22029 | 0.22029 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EUN | EDUCATION - UNIVERSITY | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.12971 | 0.0088131 | 0.14734 | Cap-Tons/1000 sf | 4832.5 | 5252.5 | 5252.5 | 0.02112 | 0.26412 | 0.26412 | 0 | 0 | 0 | 4832.5 | 5252.5 | 5252.5 | 0.02112 | 0.26412 | 0.26412 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | GRO | GROCERY | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.2306 | 0.015668 | 0.26194 | Cap-Tons/1000 sf | 7430 | 7920 | 7920 | 0.010354 | 0.16735 | 0.16735 | 0 | 0 | 0 | 7430 | 7920 | 7920 | 0.010354 | 0.16735 | 0.16735 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.18386 | 0.012492 | 0.20884 | Cap-Tons/1000 sf | 10128.5 | 10642.5 | 10642.5 | 0.0074092 | 0.15341 | 0.15341 | 0 | 0 | 0 | 10128.5 | 10642.5 | 10642.5 | 0.0074092 | 0.15341 | 0.15341 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HTL | LODGING - HOTEL | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.10324 | 0.0070147 | 0.11727 | Cap-Tons/1000 sf | 5985.5 | 6627.5 | 6627.5 | 0.023168 | 0.23917 | 0.23917 | 0 | 0 | 0 | 5985.5 | 6627.5 | 6627.5 | 0.023168 | 0.23917 | 0.23917 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | MTL | LODGING - MOTEL | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.10324 | 0.0070147 | 0.11727 | Cap-Tons/1000 sf | 5985.5 | 6627.5 | 6627.5 | 0.023168 | 0.23917 | 0.23917 | 0 | 0 | 0 | 5985.5 | 6627.5 | 6627.5 | 0.023168 | 0.23917 | 0.23917 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.18386 | 0.012492 | 0.20884 | Cap-Tons/1000 sf | 10129.5 | 10642.5 | 10642.5 | 0.0069889 | 0.14499 | 0.14499 | 0 | 0 | 0 | 10129.5 | 10642.5 | 10642.5 | 0.0069889 | 0.14499 | 0.14499 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFL | OFFICE - LARGE | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.13686 | 0.009299 | 0.15546 | Cap-Tons/1000 sf | 9455.5 | 9817.5 | 9817.5 | 0.008078 | 0.21908 | 0.21908 | 0 | 0 | 0 | 9455.5 | 9817.5 | 9817.5 | 0.008078 | 0.21908 | 0.21908 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFS | OFFICE - SMALL | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.15528 | 0.01055 | 0.17638 | Cap-Tons/1000 sf | 6843.5 | 7177.5 | 7177.5 | 0.010786 | 0.23179 | 0.23179 | 0 | 0 | 0 | 6843.5 | 7177.5 | 7177.5 | 0.010786 | 0.23179 | 0.23179 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.27074 | 0.018395 | 0.30753 | Cap-Tons/1000 sf | 15247 | 15840 | 15840 | 0.007973 | 0.21297 | 0.21297 | 0 | 0 | 0 | 15247 | 15840 | 15840 | 0.007973 | 0.21297 | 0.21297 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.18244 | 0.012395 | 0.20723 | Cap-Tons/1000 sf | 15407 | 15840 | 15840 | 0.0057332 | 0.20973 | 0.20973 | 0 | 0 | 0 | 15407 | 15840 | 15840 | 0.0057332 | 0.20973 | 0.20973 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.083286 | 0.0056587 | 0.094603 | Cap-Tons/1000 sf | 5592.5 | 6077.5 | 6077.5 | 0.020727 | 0.25973 | 0.25973 | 0 | 0 | 0 | 5592.5 | 6077.5 | 6077.5 | 0.020727 | 0.25973 | 0.25973 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.096963 | 0.006588 | 0.11014 | Cap-Tons/1000 sf | 5629.5 | 6077.5 | 6077.5 | 0.016155 | 0.21915 | 0.21915 | 0 | 0 | 0 | 5629.5 | 6077.5 | 6077.5 | 0.016155 | 0.21915 | 0.21915 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTS | RETAIL - SMALL | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.10735 | 0.0072936 | 0.12193 | Cap-Tons/1000 sf | 5638.5 | 6077.5 | 6077.5 | 0.017596 | 0.2436 | 0.2436 | 0 | 0 | 0 | 5638.5 | 6077.5 | 6077.5 | 0.017596 | 0.2436 | 0.2436 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | SCN | STORAGE - CONDITIONED | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.058722 | 0.0039897 | 0.066701 | Cap-Tons/1000 sf | 1869 | 2040 | 2040 | 0.01162 | 0.13862 | 0.13862 | 0 | 0 | 0 | 1869 | 2040 | 2040 | 0.01162 | 0.13862 | 0.13862 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ASM | ASSEMBLY | Existing | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 0.22241 | 0.015111 | 0.25263 | Cap-Tons/1000 sf | 3315 | 5215 | 3731 | 0.66486 | 1.8249 | 0.91086 | 0 | 0 | 0 | 3315 | 5215 | 3731 | 0.66486 | 1.8249 | 0.91086 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | Existing | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 0.12957 | 0.0088032 | 0.14717 | Cap-Tons/1000 sf | 3992.5 | 5252.5 | 4262.5 | 0.26794 | 1.1169 | 0.44794 | 0 | 0 | 0 | 3992.5 | 5252.5 | 4262.5 | 0.26794 | 1.1169 | 0.44794 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | Existing | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 0.14709 | 0.0099939 | 0.16708 | Cap-Tons/1000 sf | 2207.5 | 3217.5 | 2407.5 | 0.095624 | 0.30462 | 0.13562 | 0 | 0 | 0 | 2207.5 | 3217.5 | 2407.5 | 0.095624 | 0.30462 | 0.13562 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | Existing | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 0.17624 | 0.011975 | 0.20019 | Cap-Tons/1000 sf | 3882.5 | 5252.5 | 4175.5 | 0.3009 | 1.1509 | 0.4809 | 0 | 0 | 0 | 3882.5 | 5252.5 | 4175.5 | 0.3009 | 1.1509 | 0.4809 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | Existing | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 0.14499 | 0.0098513 | 0.16469 | Cap-Tons/1000 sf | 2476 | 3516 | 2680 | 0.087367 | 0.29537 | 0.12667 | 0 | 0 | 0 | 2476 | 3516 | 2680 | 0.087367 | 0.29537 | 0.12667 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EUN | EDUCATION - UNIVERSITY | Existing | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 0.12971 | 0.0088131 | 0.14734 | Cap-Tons/1000 sf | 3772.5 | 5252.5 | 4088.5 | 0.33386 | 1.1849 | 0.51386 | 0 | 0 | 0 | 3772.5 | 5252.5 | 4088.5 | 0.33386 | 1.1849 | 0.51386 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | GRO | GROCERY | Existing | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 0.2306 | 0.015668 | 0.26194 | Cap-Tons/1000 sf | 5830 | 7920 | 6338 | 0.25274 | 0.95774 | 0.40674 | 0 | 0 | 0 | 5830 | 7920 | 6338 | 0.25274 | 0.95774 | 0.40674 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | Existing | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 0.18386 | 0.012492 | 0.20884 | Cap-Tons/1000 sf | 8522.5 | 10642.5 | 8973.5 | 0.17562 | 0.88162 | 0.32362 | 0 | 0 | 0 | 8522.5 | 10642.5 | 8973.5 | 0.17562 | 0.88162 | 0.32362 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HTL | LODGING - HOTEL | Existing | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 0.10324 | 0.0070147 | 0.11727 | Cap-Tons/1000 sf | 4357.5 | 6627.5 | 4877.5 | 0.46207 | 1.3491 | 0.66107 | 0 | 0 | 0 | 4357.5 | 6627.5 | 4877.5 | 0.46207 | 1.3491 | 0.66107 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | MTL | LODGING - MOTEL | Existing | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 0.10324 | 0.0070147 | 0.11727 | Cap-Tons/1000 sf | 4357.5 | 6627.5 | 4877.5 | 0.46207 | 1.3491 | 0.66107 | 0 | 0 | 0 | 4357.5 | 6627.5 | 4877.5 | 0.46207 | 1.3491 | 0.66107 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | Existing | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 0.18386 | 0.012492 | 0.20884 | Cap-Tons/1000 sf | 8592.5 | 10642.5 | 9049.5 | 0.16653 | 0.86453 | 0.31253 | 0 | 0 | 0 | 8592.5 | 10642.5 | 9049.5 | 0.16653 | 0.86453 | 0.31253 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFL | OFFICE - LARGE | Existing | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 0.13686 | 0.009299 | 0.15546 | Cap-Tons/1000 sf | 8537.5 | 9817.5 | 8818.5 | 0.11919 | 0.91419 | 0.29319 | 0 | 0 | 0 | 8537.5 | 9817.5 | 8818.5 | 0.11919 | 0.91419 | 0.29319 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFS | OFFICE - SMALL | Existing | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 0.15528 | 0.01055 | 0.17638 | Cap-Tons/1000 sf | 5947.5 | 7177.5 | 6207.5 | 0.17207 | 1.0041 | 0.34807 | 0 | 0 | 0 | 5947.5 | 7177.5 | 6207.5 | 0.17207 | 1.0041 | 0.34807 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | Existing | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 0.27074 | 0.018395 | 0.30753 | Cap-Tons/1000 sf | 13820 | 15840 | 14298 | 0.12614 | 0.98914 | 0.31814 | 0 | 0 | 0 | 13820 | 15840 | 14298 | 0.12614 | 0.98914 | 0.31814 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | Existing | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 0.18244 | 0.012395 | 0.20723 | Cap-Tons/1000 sf | 14220 | 15840 | 14595 | 0.11506 | 1.1251 | 0.33806 | 0 | 0 | 0 | 14220 | 15840 | 14595 | 0.11506 | 1.1251 | 0.33806 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | Existing | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 0.083286 | 0.0056587 | 0.094603 | Cap-Tons/1000 sf | 4417.5 | 6077.5 | 4789.5 | 0.37954 | 1.3895 | 0.60554 | 0 | 0 | 0 | 4417.5 | 6077.5 | 4789.5 | 0.37954 | 1.3895 | 0.60554 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | Existing | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 0.096963 | 0.006588 | 0.11014 | Cap-Tons/1000 sf | 4347.5 | 6077.5 | 4741.5 | 0.39793 | 1.3979 | 0.62093 | 0 | 0 | 0 | 4347.5 | 6077.5 | 4741.5 | 0.39793 | 1.3979 | 0.62093 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTS | RETAIL - SMALL | Existing | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 0.10735 | 0.0072936 | 0.12193 | Cap-Tons/1000 sf | 4537.5 | 6077.5 | 4885.5 | 0.32955 | 1.3006 | 0.54555 | 0 | 0 | 0 | 4537.5 | 6077.5 | 4885.5 | 0.32955 | 1.3006 | 0.54555 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | SCN | STORAGE - CONDITIONED | Existing | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 0.058722 | 0.0039897 | 0.066701 | Cap-Tons/1000 sf | 1263 | 2040 | 1441 | 0.46325 | 1.2162 | 0.62725 | 0 | 0 | 0 | 1263 | 2040 | 1441 | 0.46325 | 1.2162 | 0.62725 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ASM | ASSEMBLY | New | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 0.22241 | 0.015111 | 0.25263 | Cap-Tons/1000 sf | 4815 | 5215 | 5215 | 0.020436 | 0.26644 | 0.26644 | 0 | 0 | 0 | 4815 | 5215 | 5215 | 0.020436 | 0.26644 | 0.26644 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | New | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 0.12957 | 0.0088032 | 0.14717 | Cap-Tons/1000 sf | 4960.5 | 5252.5 | 5252.5 | 0.012774 | 0.22977 | 0.22977 | 0 | 0 | 0 | 4960.5 | 5252.5 | 5252.5 | 0.012774 | 0.22977 | 0.22977 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | New | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 0.14709 | 0.0099939 | 0.16708 | Cap-Tons/1000 sf | 2996.5 | 3217.5 | 3217.5 | 0.002751 | 0.040051 | 0.040051 | 0 | 0 | 0 | 2996.5 | 3217.5 | 3217.5 | 0.002751 | 0.040051 | 0.040051 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | New | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 0.17624 | 0.011975 | 0.20019 | Cap-Tons/1000 sf | 4936.5 | 5252.5 | 5252.5 | 0.013689 | 0.22769 | 0.22769 | 0 | 0 | 0 | 4936.5 | 5252.5 | 5252.5 | 0.013689 | 0.22769 | 0.22769 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | New | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 0.14499 | 0.0098513 | 0.16469 | Cap-Tons/1000 sf | 3306 | 3516 | 3516 | 0.0019882 | 0.033288 | 0.033288 | 0 | 0 | 0 | 3306 | 3516 | 3516 | 0.0019882 | 0.033288 | 0.033288 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EUN | EDUCATION - UNIVERSITY | New | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 0.12971 | 0.0088131 | 0.14734 | Cap-Tons/1000 sf | 4912.5 | 5252.5 | 5252.5 | 0.014604 | 0.2256 | 0.2256 | 0 | 0 | 0 | 4912.5 | 5252.5 | 5252.5 | 0.014604 | 0.2256 | 0.2256 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | GRO | GROCERY | New | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 0.2306 | 0.015668 | 0.26194 | Cap-Tons/1000 sf | 7454 | 7920 | 7920 | 0.013191 | 0.22419 | 0.22419 | 0 | 0 | 0 | 7454 | 7920 | 7920 | 0.013191 | 0.22419 | 0.22419 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | New | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 0.18386 | 0.012492 | 0.20884 | Cap-Tons/1000 sf | 10187.5 | 10642.5 | 10642.5 | 0.007012 | 0.16401 | 0.16401 | 0 | 0 | 0 | 10187.5 | 10642.5 | 10642.5 | 0.007012 | 0.16401 | 0.16401 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HTL | LODGING - HOTEL | New | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 0.10324 | 0.0070147 | 0.11727 | Cap-Tons/1000 sf | 6081.5 | 6627.5 | 6627.5 | 0.020111 | 0.24411 | 0.24411 | 0 | 0 | 0 | 6081.5 | 6627.5 | 6627.5 | 0.020111 | 0.24411 | 0.24411 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | MTL | LODGING - MOTEL | New | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 0.10324 | 0.0070147 | 0.11727 | Cap-Tons/1000 sf | 6081.5 | 6627.5 | 6627.5 | 0.020111 | 0.24411 | 0.24411 | 0 | 0 | 0 | 6081.5 | 6627.5 | 6627.5 | 0.020111 | 0.24411 | 0.24411 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | New | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 0.18386 | 0.012492 | 0.20884 | Cap-Tons/1000 sf | 10199.5 | 10642.5 | 10642.5 | 0.006515 | 0.15652 | 0.15652 | 0 | 0 | 0 | 10199.5 | 10642.5 | 10642.5 | 0.006515 | 0.15652 | 0.15652 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFL | OFFICE - LARGE | New | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 0.13686 | 0.009299 | 0.15546 | Cap-Tons/1000 sf | 9501.5 | 9817.5 | 9817.5 | 0.0069509 | 0.21595 | 0.21595 | 0 | 0 | 0 | 9501.5 | 9817.5 | 9817.5 | 0.0069509 | 0.21595 | 0.21595 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFS | OFFICE - SMALL | New | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 0.15528 | 0.01055 | 0.17638 | Cap-Tons/1000 sf | 6880.5 | 7177.5 | 7177.5 | 0.0092374 | 0.22324 | 0.22324 | 0 | 0 | 0 | 6880.5 | 7177.5 | 7177.5 | 0.0092374 | 0.22324 | 0.22324 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | New | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 0.27074 | 0.018395 | 0.30753 | Cap-Tons/1000 sf | 15324 | 15840 | 15840 | 0.0075764 | 0.23258 | 0.23258 | 0 | 0 | 0 | 15324 | 15840 | 15840 | 0.0075764 | 0.23258 | 0.23258 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | New | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 0.18244 | 0.012395 | 0.20723 | Cap-Tons/1000 sf | 15465 | 15840 | 15840 | 0.0057468 | 0.24275 | 0.24275 | 0 | 0 | 0 | 15465 | 15840 | 15840 | 0.0057468 | 0.24275 | 0.24275 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | New | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 0.083286 | 0.0056587 | 0.094603 | Cap-Tons/1000 sf | 5644.5 | 6077.5 | 6077.5 | 0.020022 | 0.28102 | 0.28102 | 0 | 0 | 0 | 5644.5 | 6077.5 | 6077.5 | 0.020022 | 0.28102 | 0.28102 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | New | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 0.096963 | 0.006588 | 0.11014 | Cap-Tons/1000 sf | 5654.5 | 6077.5 | 6077.5 | 0.018552 | 0.26655 | 0.26655 | 0 | 0 | 0 | 5654.5 | 6077.5 | 6077.5 | 0.018552 | 0.26655 | 0.26655 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTS | RETAIL - SMALL | New | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 0.10735 | 0.0072936 | 0.12193 | Cap-Tons/1000 sf | 5692.5 | 6077.5 | 6077.5 | 0.017043 | 0.26904 | 0.26904 | 0 | 0 | 0 | 5692.5 | 6077.5 | 6077.5 | 0.017043 | 0.26904 | 0.26904 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | SCN | STORAGE - CONDITIONED | New | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 0.058722 | 0.0039897 | 0.066701 | Cap-Tons/1000 sf | 1878 | 2040 | 2040 | 0.013888 | 0.17489 | 0.17489 | 0 | 0 | 0 | 1878 | 2040 | 2040 | 0.013888 | 0.17489 | 0.17489 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ASM | ASSEMBLY | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.22241 | 0.015111 | 0.25263 | Cap-Tons/1000 sf | 3415 | 5215 | 3920 | 0.50653 | 1.4675 | 0.75653 | 0 | 0 | 0 | 3415 | 5215 | 3920 | 0.50653 | 1.4675 | 0.75653 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.18386 | 0.012492 | 0.20884 | Cap-Tons/1000 sf | 8562.5 | 10642.5 | 9091.5 | 0.16203 | 0.82903 | 0.31603 | 0 | 0 | 0 | 8562.5 | 10642.5 | 9091.5 | 0.16203 | 0.82903 | 0.31603 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFL | OFFICE - LARGE | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.13686 | 0.009299 | 0.15546 | Cap-Tons/1000 sf | 8397.5 | 9817.5 | 8736.5 | 0.14001 | 0.96801 | 0.33701 | 0 | 0 | 0 | 8397.5 | 9817.5 | 8736.5 | 0.14001 | 0.96801 | 0.33701 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFS | OFFICE - SMALL | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.15528 | 0.01055 | 0.17638 | Cap-Tons/1000 sf | 5957.5 | 7177.5 | 6241.5 | 0.1714 | 1.0084 | 0.3664 | 0 | 0 | 0 | 5957.5 | 7177.5 | 6241.5 | 0.1714 | 1.0084 | 0.3664 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.27074 | 0.018395 | 0.30753 | Cap-Tons/1000 sf | 13680 | 15840 | 14282 | 0.14037 | 1.0294 | 0.36337 | 0 | 0 | 0 | 13680 | 15840 | 14282 | 0.14037 | 1.0294 | 0.36337 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.18244 | 0.012395 | 0.20723 | Cap-Tons/1000 sf | 14110 | 15840 | 14583 | 0.11611 | 1.0631 | 0.35411 | 0 | 0 | 0 | 14110 | 15840 | 14583 | 0.11611 | 1.0631 | 0.35411 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.083286 | 0.0056587 | 0.094603 | Cap-Tons/1000 sf | 4427.5 | 6077.5 | 4851.5 | 0.35106 | 1.2931 | 0.59006 | 0 | 0 | 0 | 4427.5 | 6077.5 | 4851.5 | 0.35106 | 1.2931 | 0.59006 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.096963 | 0.006588 | 0.11014 | Cap-Tons/1000 sf | 4397.5 | 6077.5 | 4839.5 | 0.3446 | 1.2466 | 0.5716 | 0 | 0 | 0 | 4397.5 | 6077.5 | 4839.5 | 0.3446 | 1.2466 | 0.5716 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTS | RETAIL - SMALL | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.10735 | 0.0072936 | 0.12193 | Cap-Tons/1000 sf | 4517.5 | 6077.5 | 4920.5 | 0.32253 | 1.2565 | 0.55853 | 0 | 0 | 0 | 4517.5 | 6077.5 | 4920.5 | 0.32253 | 1.2565 | 0.55853 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | SCN | STORAGE - CONDITIONED | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.058722 | 0.0039897 | 0.066701 | Cap-Tons/1000 sf | 1432 | 2040 | 1615 | 0.25008 | 0.83908 | 0.40908 | 0 | 0 | 0 | 1432 | 2040 | 1615 | 0.25008 | 0.83908 | 0.40908 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ASM | ASSEMBLY | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.22241 | 0.015111 | 0.25263 | Cap-Tons/1000 sf | 4697 | 5215 | 5215 | 0.029887 | 0.30089 | 0.30089 | 0 | 0 | 0 | 4697 | 5215 | 5215 | 0.029887 | 0.30089 | 0.30089 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.12957 | 0.0088032 | 0.14717 | Cap-Tons/1000 sf | 4849.5 | 5252.5 | 5252.5 | 0.022354 | 0.29135 | 0.29135 | 0 | 0 | 0 | 4849.5 | 5252.5 | 5252.5 | 0.022354 | 0.29135 | 0.29135 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.14709 | 0.0099939 | 0.16708 | Cap-Tons/1000 sf | 2962.5 | 3217.5 | 3217.5 | 0.0041144 | 0.051914 | 0.051914 | 0 | 0 | 0 | 2962.5 | 3217.5 | 3217.5 | 0.0041144 | 0.051914 | 0.051914 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.17624 | 0.011975 | 0.20019 | Cap-Tons/1000 sf | 4842 | 5252.5 | 5252.5 | 0.021682 | 0.27768 | 0.27768 | 0 | 0 | 0 | 4842 | 5252.5 | 5252.5 | 0.021682 | 0.27768 | 0.27768 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.14499 | 0.0098513 | 0.16469 | Cap-Tons/1000 sf | 3237 | 3516 | 3516 | 0.0043785 | 0.055178 | 0.055178 | 0 | 0 | 0 | 3237 | 3516 | 3516 | 0.0043785 | 0.055178 | 0.055178 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EUN | EDUCATION - UNIVERSITY | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.12971 | 0.0088131 | 0.14734 | Cap-Tons/1000 sf | 4834.5 | 5252.5 | 5252.5 | 0.02101 | 0.26401 | 0.26401 | 0 | 0 | 0 | 4834.5 | 5252.5 | 5252.5 | 0.02101 | 0.26401 | 0.26401 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | GRO | GROCERY | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.2306 | 0.015668 | 0.26194 | Cap-Tons/1000 sf | 7393 | 7920 | 7920 | 0.015112 | 0.22711 | 0.22711 | 0 | 0 | 0 | 7393 | 7920 | 7920 | 0.015112 | 0.22711 | 0.22711 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.18386 | 0.012492 | 0.20884 | Cap-Tons/1000 sf | 10124.5 | 10642.5 | 10642.5 | 0.0088 | 0.1808 | 0.1808 | 0 | 0 | 0 | 10124.5 | 10642.5 | 10642.5 | 0.0088 | 0.1808 | 0.1808 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HTL | LODGING - HOTEL | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.10324 | 0.0070147 | 0.11727 | Cap-Tons/1000 sf | 5971.5 | 6627.5 | 6627.5 | 0.026695 | 0.26969 | 0.26969 | 0 | 0 | 0 | 5971.5 | 6627.5 | 6627.5 | 0.026695 | 0.26969 | 0.26969 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | MTL | LODGING - MOTEL | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.10324 | 0.0070147 | 0.11727 | Cap-Tons/1000 sf | 5971.5 | 6627.5 | 6627.5 | 0.026695 | 0.26969 | 0.26969 | 0 | 0 | 0 | 5971.5 | 6627.5 | 6627.5 | 0.026695 | 0.26969 | 0.26969 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.18386 | 0.012492 | 0.20884 | Cap-Tons/1000 sf | 10110.5 | 10642.5 | 10642.5 | 0.0085768 | 0.17158 | 0.17158 | 0 | 0 | 0 | 10110.5 | 10642.5 | 10642.5 | 0.0085768 | 0.17158 | 0.17158 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFL | OFFICE - LARGE | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.13686 | 0.009299 | 0.15546 | Cap-Tons/1000 sf | 9386.5 | 9817.5 | 9817.5 | 0.011387 | 0.25939 | 0.25939 | 0 | 0 | 0 | 9386.5 | 9817.5 | 9817.5 | 0.011387 | 0.25939 | 0.25939 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFS | OFFICE - SMALL | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.15528 | 0.01055 | 0.17638 | Cap-Tons/1000 sf | 6825.5 | 7177.5 | 7177.5 | 0.012687 | 0.25869 | 0.25869 | 0 | 0 | 0 | 6825.5 | 7177.5 | 7177.5 | 0.012687 | 0.25869 | 0.25869 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.27074 | 0.018395 | 0.30753 | Cap-Tons/1000 sf | 15135 | 15840 | 15840 | 0.012297 | 0.2763 | 0.2763 | 0 | 0 | 0 | 15135 | 15840 | 15840 | 0.012297 | 0.2763 | 0.2763 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.18244 | 0.012395 | 0.20723 | Cap-Tons/1000 sf | 15296 | 15840 | 15840 | 0.0097092 | 0.28271 | 0.28271 | 0 | 0 | 0 | 15296 | 15840 | 15840 | 0.0097092 | 0.28271 | 0.28271 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.083286 | 0.0056587 | 0.094603 | Cap-Tons/1000 sf | 5564.5 | 6077.5 | 6077.5 | 0.025629 | 0.30363 | 0.30363 | 0 | 0 | 0 | 5564.5 | 6077.5 | 6077.5 | 0.025629 | 0.30363 | 0.30363 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.096963 | 0.006588 | 0.11014 | Cap-Tons/1000 sf | 5582.5 | 6077.5 | 6077.5 | 0.023232 | 0.28523 | 0.28523 | 0 | 0 | 0 | 5582.5 | 6077.5 | 6077.5 | 0.023232 | 0.28523 | 0.28523 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTS | RETAIL - SMALL | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.10735 | 0.0072936 | 0.12193 | Cap-Tons/1000 sf | 5594.5 | 6077.5 | 6077.5 | 0.023569 | 0.29657 | 0.29657 | 0 | 0 | 0 | 5594.5 | 6077.5 | 6077.5 | 0.023569 | 0.29657 | 0.29657 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | SCN | STORAGE - CONDITIONED | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.058722 | 0.0039897 | 0.066701 | Cap-Tons/1000 sf | 1843 | 2040 | 2040 | 0.019561 | 0.20256 | 0.20256 | 0 | 0 | 0 | 1843 | 2040 | 2040 | 0.019561 | 0.20256 | 0.20256 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ASM | ASSEMBLY | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.22241 | 0.015111 | 0.25263 | Cap-Tons/1000 sf | 3165 | 5215 | 3702 | 0.71896 | 1.829 | 0.98496 | 0 | 0 | 0 | 3165 | 5215 | 3702 | 0.71896 | 1.829 | 0.98496 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.12957 | 0.0088032 | 0.14717 | Cap-Tons/1000 sf | 3662.5 | 5252.5 | 4054.5 | 0.11722 | 0.38722 | 0.17912 | 0 | 0 | 0 | 3662.5 | 5252.5 | 4054.5 | 0.11722 | 0.38722 | 0.17912 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.14709 | 0.0099939 | 0.16708 | Cap-Tons/1000 sf | 1930.5 | 3217.5 | 2236.5 | 0.23333 | 0.58333 | 0.30603 | 0 | 0 | 0 | 1930.5 | 3217.5 | 2236.5 | 0.23333 | 0.58333 | 0.30603 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.17624 | 0.011975 | 0.20019 | Cap-Tons/1000 sf | 3652.5 | 5252.5 | 4042.5 | 0.11541 | 0.37891 | 0.17581 | 0 | 0 | 0 | 3652.5 | 5252.5 | 4042.5 | 0.11541 | 0.37891 | 0.17581 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.14499 | 0.0098513 | 0.16469 | Cap-Tons/1000 sf | 2109.6 | 3516 | 2460.6 | 0.228 | 0.57 | 0.2995 | 0 | 0 | 0 | 2109.6 | 3516 | 2460.6 | 0.228 | 0.57 | 0.2995 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EUN | EDUCATION - UNIVERSITY | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.12971 | 0.0088131 | 0.14734 | Cap-Tons/1000 sf | 3642.5 | 5252.5 | 4030.5 | 0.1136 | 0.3706 | 0.1725 | 0 | 0 | 0 | 3642.5 | 5252.5 | 4030.5 | 0.1136 | 0.3706 | 0.1725 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | GRO | GROCERY | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.2306 | 0.015668 | 0.26194 | Cap-Tons/1000 sf | 5560 | 7920 | 6171 | 0.33745 | 1.1324 | 0.51945 | 0 | 0 | 0 | 5560 | 7920 | 6171 | 0.33745 | 1.1324 | 0.51945 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.18386 | 0.012492 | 0.20884 | Cap-Tons/1000 sf | 8682.5 | 10642.5 | 9158.5 | 0.15734 | 0.85434 | 0.31934 | 0 | 0 | 0 | 8682.5 | 10642.5 | 9158.5 | 0.15734 | 0.85434 | 0.31934 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HTL | LODGING - HOTEL | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.10324 | 0.0070147 | 0.11727 | Cap-Tons/1000 sf | 4307.5 | 6627.5 | 4867.5 | 0.5149 | 1.4709 | 0.7359 | 0 | 0 | 0 | 4307.5 | 6627.5 | 4867.5 | 0.5149 | 1.4709 | 0.7359 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | MTL | LODGING - MOTEL | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.10324 | 0.0070147 | 0.11727 | Cap-Tons/1000 sf | 4307.5 | 6627.5 | 4867.5 | 0.5149 | 1.4709 | 0.7359 | 0 | 0 | 0 | 4307.5 | 6627.5 | 4867.5 | 0.5149 | 1.4709 | 0.7359 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.18386 | 0.012492 | 0.20884 | Cap-Tons/1000 sf | 8482.5 | 10642.5 | 9046.5 | 0.18309 | 0.90209 | 0.35009 | 0 | 0 | 0 | 8482.5 | 10642.5 | 9046.5 | 0.18309 | 0.90209 | 0.35009 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTS | RETAIL - SMALL | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.10735 | 0.0072936 | 0.12193 | Cap-Tons/1000 sf | 4347.5 | 6077.5 | 4771.5 | 0.41783 | 1.4678 | 0.66283 | 0 | 0 | 0 | 4347.5 | 6077.5 | 4771.5 | 0.41783 | 1.4678 | 0.66283 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | SCN | STORAGE - CONDITIONED | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.058722 | 0.0039897 | 0.066701 | Cap-Tons/1000 sf | 1663 | 2040 | 2040 | 0.053048 | 0.28705 | 0.28705 | 0 | 0 | 0 | 1663 | 2040 | 2040 | 0.053048 | 0.28705 | 0.28705 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ASM | ASSEMBLY | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.22241 | 0.015111 | 0.25263 | Cap-Tons/1000 sf | 4681 | 5215 | 5215 | 0.031029 | 0.30303 | 0.30303 | 0 | 0 | 0 | 4681 | 5215 | 5215 | 0.031029 | 0.30303 | 0.30303 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.12957 | 0.0088032 | 0.14717 | Cap-Tons/1000 sf | 4776.5 | 5252.5 | 5252.5 | 0.0061587 | 0.067959 | 0.067959 | 0 | 0 | 0 | 4776.5 | 5252.5 | 5252.5 | 0.0061587 | 0.067959 | 0.067959 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.14709 | 0.0099939 | 0.16708 | Cap-Tons/1000 sf | 2914.5 | 3217.5 | 3217.5 | 0.0067264 | 0.071426 | 0.071426 | 0 | 0 | 0 | 2914.5 | 3217.5 | 3217.5 | 0.0067264 | 0.071426 | 0.071426 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.17624 | 0.011975 | 0.20019 | Cap-Tons/1000 sf | 4783.5 | 5252.5 | 5252.5 | 0.0059581 | 0.066708 | 0.066708 | 0 | 0 | 0 | 4783.5 | 5252.5 | 5252.5 | 0.0059581 | 0.066708 | 0.066708 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.14499 | 0.0098513 | 0.16469 | Cap-Tons/1000 sf | 3104 | 3516 | 3516 | 0.0093045 | 0.079405 | 0.079405 | 0 | 0 | 0 | 3104 | 3516 | 3516 | 0.0093045 | 0.079405 | 0.079405 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EUN | EDUCATION - UNIVERSITY | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.12971 | 0.0088131 | 0.14734 | Cap-Tons/1000 sf | 4790.5 | 5252.5 | 5252.5 | 0.0057575 | 0.065458 | 0.065458 | 0 | 0 | 0 | 4790.5 | 5252.5 | 5252.5 | 0.0057575 | 0.065458 | 0.065458 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | GRO | GROCERY | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.2306 | 0.015668 | 0.26194 | Cap-Tons/1000 sf | 7298 | 7920 | 7920 | 0.02037 | 0.25937 | 0.25937 | 0 | 0 | 0 | 7298 | 7920 | 7920 | 0.02037 | 0.25937 | 0.25937 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.18386 | 0.012492 | 0.20884 | Cap-Tons/1000 sf | 10154.5 | 10642.5 | 10642.5 | 0.008362 | 0.18236 | 0.18236 | 0 | 0 | 0 | 10154.5 | 10642.5 | 10642.5 | 0.008362 | 0.18236 | 0.18236 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HTL | LODGING - HOTEL | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.10324 | 0.0070147 | 0.11727 | Cap-Tons/1000 sf | 5991.5 | 6627.5 | 6627.5 | 0.02675 | 0.27875 | 0.27875 | 0 | 0 | 0 | 5991.5 | 6627.5 | 6627.5 | 0.02675 | 0.27875 | 0.27875 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | MTL | LODGING - MOTEL | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.10324 | 0.0070147 | 0.11727 | Cap-Tons/1000 sf | 5991.5 | 6627.5 | 6627.5 | 0.02675 | 0.27875 | 0.27875 | 0 | 0 | 0 | 5991.5 | 6627.5 | 6627.5 | 0.02675 | 0.27875 | 0.27875 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.18386 | 0.012492 | 0.20884 | Cap-Tons/1000 sf | 10091.5 | 10642.5 | 10642.5 | 0.0094459 | 0.18245 | 0.18245 | 0 | 0 | 0 | 10091.5 | 10642.5 | 10642.5 | 0.0094459 | 0.18245 | 0.18245 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFL | OFFICE - LARGE | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.13686 | 0.009299 | 0.15546 | Cap-Tons/1000 sf | 9431.5 | 9817.5 | 9817.5 | 0.010641 | 0.27064 | 0.27064 | 0 | 0 | 0 | 9431.5 | 9817.5 | 9817.5 | 0.010641 | 0.27064 | 0.27064 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFS | OFFICE - SMALL | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.15528 | 0.01055 | 0.17638 | Cap-Tons/1000 sf | 6832.5 | 7177.5 | 7177.5 | 0.013027 | 0.27103 | 0.27103 | 0 | 0 | 0 | 6832.5 | 7177.5 | 7177.5 | 0.013027 | 0.27103 | 0.27103 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.27074 | 0.018395 | 0.30753 | Cap-Tons/1000 sf | 15062 | 15840 | 15840 | 0.014101 | 0.2871 | 0.2871 | 0 | 0 | 0 | 15062 | 15840 | 15840 | 0.014101 | 0.2871 | 0.2871 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.18244 | 0.012395 | 0.20723 | Cap-Tons/1000 sf | 15225 | 15840 | 15840 | 0.010381 | 0.26738 | 0.26738 | 0 | 0 | 0 | 15225 | 15840 | 15840 | 0.010381 | 0.26738 | 0.26738 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.083286 | 0.0056587 | 0.094603 | Cap-Tons/1000 sf | 5535.5 | 6077.5 | 6077.5 | 0.028297 | 0.3173 | 0.3173 | 0 | 0 | 0 | 5535.5 | 6077.5 | 6077.5 | 0.028297 | 0.3173 | 0.3173 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.096963 | 0.006588 | 0.11014 | Cap-Tons/1000 sf | 5522.5 | 6077.5 | 6077.5 | 0.027737 | 0.30374 | 0.30374 | 0 | 0 | 0 | 5522.5 | 6077.5 | 6077.5 | 0.027737 | 0.30374 | 0.30374 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTS | RETAIL - SMALL | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.10735 | 0.0072936 | 0.12193 | Cap-Tons/1000 sf | 5563.5 | 6077.5 | 6077.5 | 0.026423 | 0.31242 | 0.31242 | 0 | 0 | 0 | 5563.5 | 6077.5 | 6077.5 | 0.026423 | 0.31242 | 0.31242 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | SCN | STORAGE - CONDITIONED | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.058722 | 0.0039897 | 0.066701 | Cap-Tons/1000 sf | 1663 | 2040 | 2040 | 0.053048 | 0.28705 | 0.28705 | 0 | 0 | 0 | 1663 | 2040 | 2040 | 0.053048 | 0.28705 | 0.28705 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ASM | ASSEMBLY | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.22241 | 0.015111 | 0.25263 | Cap-Tons/1000 sf | 3129 | 5215 | 3685 | 0.7 | 1.75 | 0.95 | 0 | 0 | 0 | 3129 | 5215 | 3685 | 0.7 | 1.75 | 0.95 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.12957 | 0.0088032 | 0.14717 | Cap-Tons/1000 sf | 3722.5 | 5252.5 | 4096.5 | 0.40033 | 1.3743 | 0.62233 | 0 | 0 | 0 | 3722.5 | 5252.5 | 4096.5 | 0.40033 | 1.3743 | 0.62233 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.14709 | 0.0099939 | 0.16708 | Cap-Tons/1000 sf | 1930.5 | 3217.5 | 2251.5 | 0.22133 | 0.55333 | 0.29103 | 0 | 0 | 0 | 1930.5 | 3217.5 | 2251.5 | 0.22133 | 0.55333 | 0.29103 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.17624 | 0.011975 | 0.20019 | Cap-Tons/1000 sf | 3712.5 | 5252.5 | 4083.5 | 0.39441 | 1.3454 | 0.61141 | 0 | 0 | 0 | 3712.5 | 5252.5 | 4083.5 | 0.39441 | 1.3454 | 0.61141 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.14499 | 0.0098513 | 0.16469 | Cap-Tons/1000 sf | 2109.6 | 3516 | 2466.6 | 0.20933 | 0.52333 | 0.27533 | 0 | 0 | 0 | 2109.6 | 3516 | 2466.6 | 0.20933 | 0.52333 | 0.27533 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EUN | EDUCATION - UNIVERSITY | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.12971 | 0.0088131 | 0.14734 | Cap-Tons/1000 sf | 3702.5 | 5252.5 | 4070.5 | 0.38849 | 1.3165 | 0.60049 | 0 | 0 | 0 | 3702.5 | 5252.5 | 4070.5 | 0.38849 | 1.3165 | 0.60049 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | GRO | GROCERY | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.2306 | 0.015668 | 0.26194 | Cap-Tons/1000 sf | 5540 | 7920 | 6205 | 0.30974 | 1.0307 | 0.48174 | 0 | 0 | 0 | 5540 | 7920 | 6205 | 0.30974 | 1.0307 | 0.48174 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.18386 | 0.012492 | 0.20884 | Cap-Tons/1000 sf | 8522.5 | 10642.5 | 9019.5 | 0.17562 | 0.88162 | 0.33362 | 0 | 0 | 0 | 8522.5 | 10642.5 | 9019.5 | 0.17562 | 0.88162 | 0.33362 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HTL | LODGING - HOTEL | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.10324 | 0.0070147 | 0.11727 | Cap-Tons/1000 sf | 4237.5 | 6627.5 | 4837.5 | 0.51889 | 1.4389 | 0.73789 | 0 | 0 | 0 | 4237.5 | 6627.5 | 4837.5 | 0.51889 | 1.4389 | 0.73789 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.083286 | 0.0056587 | 0.094603 | Cap-Tons/1000 sf | 4417.5 | 6077.5 | 4842.5 | 0.37315 | 1.3661 | 0.61315 | 0 | 0 | 0 | 4417.5 | 6077.5 | 4842.5 | 0.37315 | 1.3661 | 0.61315 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.096963 | 0.006588 | 0.11014 | Cap-Tons/1000 sf | 4197.5 | 6077.5 | 4684.5 | 0.43714 | 1.4131 | 0.67214 | 0 | 0 | 0 | 4197.5 | 6077.5 | 4684.5 | 0.43714 | 1.4131 | 0.67214 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTS | RETAIL - SMALL | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.10735 | 0.0072936 | 0.12193 | Cap-Tons/1000 sf | 4347.5 | 6077.5 | 4790.5 | 0.40987 | 1.4399 | 0.65787 | 0 | 0 | 0 | 4347.5 | 6077.5 | 4790.5 | 0.40987 | 1.4399 | 0.65787 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | New | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.18544 | 0.010304 | 0.20605 | Cap-Tons/1000 sf | 4884.5 | 5252.5 | 5252.5 | 0.016553 | 0.23605 | 0.23605 | 0 | 0 | 0 | 4884.5 | 5252.5 | 5252.5 | 0.016553 | 0.23605 | 0.23605 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | New | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.1526 | 0.0084793 | 0.16956 | Cap-Tons/1000 sf | 3262 | 3516 | 3516 | 0.016196 | 0.2242 | 0.2242 | 0 | 0 | 0 | 3262 | 3516 | 3516 | 0.016196 | 0.2242 | 0.2242 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EUN | EDUCATION - UNIVERSITY | New | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.13025 | 0.0072376 | 0.14473 | Cap-Tons/1000 sf | 4857.5 | 5252.5 | 5252.5 | 0.017971 | 0.23897 | 0.23897 | 0 | 0 | 0 | 4857.5 | 5252.5 | 5252.5 | 0.017971 | 0.23897 | 0.23897 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | GRO | GROCERY | New | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.23968 | 0.013318 | 0.26631 | Cap-Tons/1000 sf | 7534 | 7920 | 7920 | 0.0060457 | 0.12405 | 0.12405 | 0 | 0 | 0 | 7534 | 7920 | 7920 | 0.0060457 | 0.12405 | 0.12405 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | New | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.1869 | 0.010385 | 0.20767 | Cap-Tons/1000 sf | 10207.5 | 10642.5 | 10642.5 | 0.0048582 | 0.11886 | 0.11886 | 0 | 0 | 0 | 10207.5 | 10642.5 | 10642.5 | 0.0048582 | 0.11886 | 0.11886 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HTL | LODGING - HOTEL | New | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.10457 | 0.0058107 | 0.11619 | Cap-Tons/1000 sf | 5999.5 | 6627.5 | 6627.5 | 0.020621 | 0.21762 | 0.21762 | 0 | 0 | 0 | 5999.5 | 6627.5 | 6627.5 | 0.020621 | 0.21762 | 0.21762 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HTL | LODGING - HOTEL | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.10457 | 0.0058107 | 0.11619 | Cap-Tons/1000 sf | 5971.5 | 6627.5 | 6627.5 | 0.026695 | 0.26969 | 0.26969 | 0 | 0 | 0 | 5971.5 | 6627.5 | 6627.5 | 0.026695 | 0.26969 | 0.26969 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | MTL | LODGING - MOTEL | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.10457 | 0.0058107 | 0.11619 | Cap-Tons/1000 sf | 5971.5 | 6627.5 | 6627.5 | 0.026695 | 0.26969 | 0.26969 | 0 | 0 | 0 | 5971.5 | 6627.5 | 6627.5 | 0.026695 | 0.26969 | 0.26969 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.1869 | 0.010385 | 0.20767 | Cap-Tons/1000 sf | 10110.5 | 10642.5 | 10642.5 | 0.0085768 | 0.17158 | 0.17158 | 0 | 0 | 0 | 10110.5 | 10642.5 | 10642.5 | 0.0085768 | 0.17158 | 0.17158 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFL | OFFICE - LARGE | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.13653 | 0.0075866 | 0.1517 | Cap-Tons/1000 sf | 9386.5 | 9817.5 | 9817.5 | 0.011387 | 0.25939 | 0.25939 | 0 | 0 | 0 | 9386.5 | 9817.5 | 9817.5 | 0.011387 | 0.25939 | 0.25939 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFS | OFFICE - SMALL | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.16578 | 0.0092117 | 0.1842 | Cap-Tons/1000 sf | 6825.5 | 7177.5 | 7177.5 | 0.012687 | 0.25869 | 0.25869 | 0 | 0 | 0 | 6825.5 | 7177.5 | 7177.5 | 0.012687 | 0.25869 | 0.25869 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.29153 | 0.0162 | 0.32393 | Cap-Tons/1000 sf | 15135 | 15840 | 15840 | 0.012297 | 0.2763 | 0.2763 | 0 | 0 | 0 | 15135 | 15840 | 15840 | 0.012297 | 0.2763 | 0.2763 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.19242 | 0.010692 | 0.2138 | Cap-Tons/1000 sf | 15296 | 15840 | 15840 | 0.0097092 | 0.28271 | 0.28271 | 0 | 0 | 0 | 15296 | 15840 | 15840 | 0.0097092 | 0.28271 | 0.28271 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.083367 | 0.0046324 | 0.092632 | Cap-Tons/1000 sf | 5564.5 | 6077.5 | 6077.5 | 0.025629 | 0.30363 | 0.30363 | 0 | 0 | 0 | 5564.5 | 6077.5 | 6077.5 | 0.025629 | 0.30363 | 0.30363 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.10107 | 0.0056162 | 0.1123 | Cap-Tons/1000 sf | 5582.5 | 6077.5 | 6077.5 | 0.023232 | 0.28523 | 0.28523 | 0 | 0 | 0 | 5582.5 | 6077.5 | 6077.5 | 0.023232 | 0.28523 | 0.28523 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTS | RETAIL - SMALL | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.10985 | 0.0061039 | 0.12206 | Cap-Tons/1000 sf | 5594.5 | 6077.5 | 6077.5 | 0.023569 | 0.29657 | 0.29657 | 0 | 0 | 0 | 5594.5 | 6077.5 | 6077.5 | 0.023569 | 0.29657 | 0.29657 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | SCN | STORAGE - CONDITIONED | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.060165 | 0.0033432 | 0.066851 | Cap-Tons/1000 sf | 1843 | 2040 | 2040 | 0.019561 | 0.20256 | 0.20256 | 0 | 0 | 0 | 1843 | 2040 | 2040 | 0.019561 | 0.20256 | 0.20256 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ASM | ASSEMBLY | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.22348 | 0.012418 | 0.24831 | Cap-Tons/1000 sf | 3145 | 5215 | 3708 | 0.68452 | 1.7245 | 0.93752 | 0 | 0 | 0 | 3145 | 5215 | 3708 | 0.68452 | 1.7245 | 0.93752 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.12949 | 0.0071952 | 0.14388 | Cap-Tons/1000 sf | 3702.5 | 5252.5 | 4084.5 | 0.41278 | 1.3988 | 0.63978 | 0 | 0 | 0 | 3702.5 | 5252.5 | 4084.5 | 0.41278 | 1.3988 | 0.63978 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.15684 | 0.0087149 | 0.17427 | Cap-Tons/1000 sf | 1930.5 | 3217.5 | 2254.5 | 0.232 | 0.58 | 0.3031 | 0 | 0 | 0 | 1930.5 | 3217.5 | 2254.5 | 0.232 | 0.58 | 0.3031 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.18544 | 0.010304 | 0.20605 | Cap-Tons/1000 sf | 3692.5 | 5252.5 | 4072 | 0.40677 | 1.3698 | 0.62827 | 0 | 0 | 0 | 3692.5 | 5252.5 | 4072 | 0.40677 | 1.3698 | 0.62827 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | SCN | STORAGE - CONDITIONED | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.058722 | 0.0039897 | 0.066701 | Cap-Tons/1000 sf | 1630 | 2040 | 2040 | 0.053325 | 0.26533 | 0.26533 | 0 | 0 | 0 | 1630 | 2040 | 2040 | 0.053325 | 0.26533 | 0.26533 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ASM | ASSEMBLY | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.22241 | 0.015111 | 0.25263 | Cap-Tons/1000 sf | 4638 | 5215 | 5215 | 0.03247 | 0.29347 | 0.29347 | 0 | 0 | 0 | 4638 | 5215 | 5215 | 0.03247 | 0.29347 | 0.29347 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.12957 | 0.0088032 | 0.14717 | Cap-Tons/1000 sf | 4803.5 | 5252.5 | 5252.5 | 0.024677 | 0.28868 | 0.28868 | 0 | 0 | 0 | 4803.5 | 5252.5 | 5252.5 | 0.024677 | 0.28868 | 0.28868 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.14709 | 0.0099939 | 0.16708 | Cap-Tons/1000 sf | 2854.5 | 3217.5 | 3217.5 | 0.0082913 | 0.073491 | 0.073491 | 0 | 0 | 0 | 2854.5 | 3217.5 | 3217.5 | 0.0082913 | 0.073491 | 0.073491 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.17624 | 0.011975 | 0.20019 | Cap-Tons/1000 sf | 4814.5 | 5252.5 | 5252.5 | 0.023488 | 0.28149 | 0.28149 | 0 | 0 | 0 | 4814.5 | 5252.5 | 5252.5 | 0.023488 | 0.28149 | 0.28149 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.14499 | 0.0098513 | 0.16469 | Cap-Tons/1000 sf | 3078 | 3516 | 3516 | 0.0087372 | 0.070137 | 0.070137 | 0 | 0 | 0 | 3078 | 3516 | 3516 | 0.0087372 | 0.070137 | 0.070137 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EUN | EDUCATION - UNIVERSITY | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.12971 | 0.0088131 | 0.14734 | Cap-Tons/1000 sf | 4825.5 | 5252.5 | 5252.5 | 0.022299 | 0.2743 | 0.2743 | 0 | 0 | 0 | 4825.5 | 5252.5 | 5252.5 | 0.022299 | 0.2743 | 0.2743 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | GRO | GROCERY | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.2306 | 0.015668 | 0.26194 | Cap-Tons/1000 sf | 7244 | 7920 | 7920 | 0.02081 | 0.24381 | 0.24381 | 0 | 0 | 0 | 7244 | 7920 | 7920 | 0.02081 | 0.24381 | 0.24381 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.18386 | 0.012492 | 0.20884 | Cap-Tons/1000 sf | 10120.5 | 10642.5 | 10642.5 | 0.0088199 | 0.17982 | 0.17982 | 0 | 0 | 0 | 10120.5 | 10642.5 | 10642.5 | 0.0088199 | 0.17982 | 0.17982 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.18244 | 0.012395 | 0.20723 | Cap-Tons/1000 sf | 15198 | 15840 | 15840 | 0.011532 | 0.28453 | 0.28453 | 0 | 0 | 0 | 15198 | 15840 | 15840 | 0.011532 | 0.28453 | 0.28453 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.083286 | 0.0056587 | 0.094603 | Cap-Tons/1000 sf | 5560.5 | 6077.5 | 6077.5 | 0.025569 | 0.30057 | 0.30057 | 0 | 0 | 0 | 5560.5 | 6077.5 | 6077.5 | 0.025569 | 0.30057 | 0.30057 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.096963 | 0.006588 | 0.11014 | Cap-Tons/1000 sf | 5523.5 | 6077.5 | 6077.5 | 0.026379 | 0.28938 | 0.28938 | 0 | 0 | 0 | 5523.5 | 6077.5 | 6077.5 | 0.026379 | 0.28938 | 0.28938 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTS | RETAIL - SMALL | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.10735 | 0.0072936 | 0.12193 | Cap-Tons/1000 sf | 5561.5 | 6077.5 | 6077.5 | 0.025607 | 0.30161 | 0.30161 | 0 | 0 | 0 | 5561.5 | 6077.5 | 6077.5 | 0.025607 | 0.30161 | 0.30161 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | SCN | STORAGE - CONDITIONED | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.058722 | 0.0039897 | 0.066701 | Cap-Tons/1000 sf | 1630 | 2040 | 2040 | 0.053325 | 0.26533 | 0.26533 | 0 | 0 | 0 | 1630 | 2040 | 2040 | 0.053325 | 0.26533 | 0.26533 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ASM | ASSEMBLY | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.22241 | 0.015111 | 0.25263 | Cap-Tons/1000 sf | 3205 | 5215 | 3736 | 0.61962 | 1.6076 | 0.87762 | 0 | 0 | 0 | 3205 | 5215 | 3736 | 0.61962 | 1.6076 | 0.87762 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.12957 | 0.0088032 | 0.14717 | Cap-Tons/1000 sf | 3412.5 | 5252.5 | 3841.5 | 0.53919 | 1.5392 | 0.77119 | 0 | 0 | 0 | 3412.5 | 5252.5 | 3841.5 | 0.53919 | 1.5392 | 0.77119 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.14709 | 0.0099939 | 0.16708 | Cap-Tons/1000 sf | 1930.5 | 3217.5 | 2240.5 | 0.22267 | 0.55667 | 0.29607 | 0 | 0 | 0 | 1930.5 | 3217.5 | 2240.5 | 0.22267 | 0.55667 | 0.29607 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.17624 | 0.011975 | 0.20019 | Cap-Tons/1000 sf | 3372.5 | 5252.5 | 3808.5 | 0.54471 | 1.5222 | 0.77071 | 0 | 0 | 0 | 3372.5 | 5252.5 | 3808.5 | 0.54471 | 1.5222 | 0.77071 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.14499 | 0.0098513 | 0.16469 | Cap-Tons/1000 sf | 2109.6 | 3516 | 2462.6 | 0.214 | 0.535 | 0.2847 | 0 | 0 | 0 | 2109.6 | 3516 | 2462.6 | 0.214 | 0.535 | 0.2847 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EUN | EDUCATION - UNIVERSITY | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.12971 | 0.0088131 | 0.14734 | Cap-Tons/1000 sf | 3332.5 | 5252.5 | 3775.5 | 0.55022 | 1.5052 | 0.77022 | 0 | 0 | 0 | 3332.5 | 5252.5 | 3775.5 | 0.55022 | 1.5052 | 0.77022 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | GRO | GROCERY | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.2306 | 0.015668 | 0.26194 | Cap-Tons/1000 sf | 6030 | 7920 | 6532 | 0.22128 | 0.92728 | 0.39428 | 0 | 0 | 0 | 6030 | 7920 | 6532 | 0.22128 | 0.92728 | 0.39428 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.18386 | 0.012492 | 0.20884 | Cap-Tons/1000 sf | 8332.5 | 10642.5 | 8874.5 | 0.20626 | 0.95026 | 0.37826 | 0 | 0 | 0 | 8332.5 | 10642.5 | 8874.5 | 0.20626 | 0.95026 | 0.37826 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HTL | LODGING - HOTEL | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.10324 | 0.0070147 | 0.11727 | Cap-Tons/1000 sf | 3976.5 | 6627.5 | 4652.5 | 0.63267 | 1.5817 | 0.86567 | 0 | 0 | 0 | 3976.5 | 6627.5 | 4652.5 | 0.63267 | 1.5817 | 0.86567 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | MTL | LODGING - MOTEL | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.10324 | 0.0070147 | 0.11727 | Cap-Tons/1000 sf | 3976.5 | 6627.5 | 4652.5 | 5.728e-05 | 1.5817 | 0.23306 | 0 | 0 | 0 | 3976.5 | 6627.5 | 4652.5 | 5.728e-05 | 1.5817 | 0.23306 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.18386 | 0.012492 | 0.20884 | Cap-Tons/1000 sf | 8332.5 | 10642.5 | 8887.5 | 0.21679 | 0.99879 | 0.39579 | 0 | 0 | 0 | 8332.5 | 10642.5 | 8887.5 | 0.21679 | 0.99879 | 0.39579 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFL | OFFICE - LARGE | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.13686 | 0.009299 | 0.15546 | Cap-Tons/1000 sf | 8197.5 | 9817.5 | 8583.5 | 0.17114 | 1.0371 | 0.37814 | 0 | 0 | 0 | 8197.5 | 9817.5 | 8583.5 | 0.17114 | 1.0371 | 0.37814 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFS | OFFICE - SMALL | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.15528 | 0.01055 | 0.17638 | Cap-Tons/1000 sf | 5537.5 | 7177.5 | 5920.5 | 0.27573 | 1.2067 | 0.49273 | 0 | 0 | 0 | 5537.5 | 7177.5 | 5920.5 | 0.27573 | 1.2067 | 0.49273 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.27074 | 0.018395 | 0.30753 | Cap-Tons/1000 sf | 13420 | 15840 | 14048 | 0.1733 | 1.1343 | 0.4143 | 0 | 0 | 0 | 13420 | 15840 | 14048 | 0.1733 | 1.1343 | 0.4143 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.18244 | 0.012395 | 0.20723 | Cap-Tons/1000 sf | 13710 | 15840 | 14256 | 0.16468 | 1.2247 | 0.42868 | 0 | 0 | 0 | 13710 | 15840 | 14256 | 0.16468 | 1.2247 | 0.42868 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.083286 | 0.0056587 | 0.094603 | Cap-Tons/1000 sf | 4157.5 | 6077.5 | 4642.5 | 0.45397 | 1.437 | 0.70297 | 0 | 0 | 0 | 4157.5 | 6077.5 | 4642.5 | 0.45397 | 1.437 | 0.70297 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.096963 | 0.006588 | 0.11014 | Cap-Tons/1000 sf | 3997.5 | 6077.5 | 4531.5 | 0.52033 | 1.5203 | 0.77433 | 0 | 0 | 0 | 3997.5 | 6077.5 | 4531.5 | 0.52033 | 1.5203 | 0.77433 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTS | RETAIL - SMALL | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.10735 | 0.0072936 | 0.12193 | Cap-Tons/1000 sf | 4227.5 | 6077.5 | 4699.5 | 0.4293 | 1.4103 | 0.6783 | 0 | 0 | 0 | 4227.5 | 6077.5 | 4699.5 | 0.4293 | 1.4103 | 0.6783 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | SCN | STORAGE - CONDITIONED | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.058722 | 0.0039897 | 0.066701 | Cap-Tons/1000 sf | 1707 | 2040 | 2040 | 0.047014 | 0.28801 | 0.28801 | 0 | 0 | 0 | 1707 | 2040 | 2040 | 0.047014 | 0.28801 | 0.28801 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ASM | ASSEMBLY | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.22241 | 0.015111 | 0.25263 | Cap-Tons/1000 sf | 4671 | 5215 | 5215 | 0.032377 | 0.31038 | 0.31038 | 0 | 0 | 0 | 4671 | 5215 | 5215 | 0.032377 | 0.31038 | 0.31038 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.12957 | 0.0088032 | 0.14717 | Cap-Tons/1000 sf | 4737.5 | 5252.5 | 5252.5 | 0.027285 | 0.27829 | 0.27829 | 0 | 0 | 0 | 4737.5 | 5252.5 | 5252.5 | 0.027285 | 0.27829 | 0.27829 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.14709 | 0.0099939 | 0.16708 | Cap-Tons/1000 sf | 2888.5 | 3217.5 | 3217.5 | 0.0082691 | 0.080869 | 0.080869 | 0 | 0 | 0 | 2888.5 | 3217.5 | 3217.5 | 0.0082691 | 0.080869 | 0.080869 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.17624 | 0.011975 | 0.20019 | Cap-Tons/1000 sf | 4739 | 5252.5 | 5252.5 | 0.026765 | 0.27377 | 0.27377 | 0 | 0 | 0 | 4739 | 5252.5 | 5252.5 | 0.026765 | 0.27377 | 0.27377 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.14499 | 0.0098513 | 0.16469 | Cap-Tons/1000 sf | 3136 | 3516 | 3516 | 0.0084943 | 0.078594 | 0.078594 | 0 | 0 | 0 | 3136 | 3516 | 3516 | 0.0084943 | 0.078594 | 0.078594 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EUN | EDUCATION - UNIVERSITY | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.12971 | 0.0088131 | 0.14734 | Cap-Tons/1000 sf | 4740.5 | 5252.5 | 5252.5 | 0.026245 | 0.26925 | 0.26925 | 0 | 0 | 0 | 4740.5 | 5252.5 | 5252.5 | 0.026245 | 0.26925 | 0.26925 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | GRO | GROCERY | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.2306 | 0.015668 | 0.26194 | Cap-Tons/1000 sf | 7357 | 7920 | 7920 | 0.015076 | 0.21208 | 0.21208 | 0 | 0 | 0 | 7357 | 7920 | 7920 | 0.015076 | 0.21208 | 0.21208 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.18386 | 0.012492 | 0.20884 | Cap-Tons/1000 sf | 10068.5 | 10642.5 | 10642.5 | 0.010718 | 0.19872 | 0.19872 | 0 | 0 | 0 | 10068.5 | 10642.5 | 10642.5 | 0.010718 | 0.19872 | 0.19872 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HTL | LODGING - HOTEL | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.10324 | 0.0070147 | 0.11727 | Cap-Tons/1000 sf | 5854.5 | 6627.5 | 6627.5 | 0.033801 | 0.2898 | 0.2898 | 0 | 0 | 0 | 5854.5 | 6627.5 | 6627.5 | 0.033801 | 0.2898 | 0.2898 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | MTL | LODGING - MOTEL | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.10324 | 0.0070147 | 0.11727 | Cap-Tons/1000 sf | 5854.5 | 6627.5 | 6627.5 | 0.033801 | 0.2898 | 0.2898 | 0 | 0 | 0 | 5854.5 | 6627.5 | 6627.5 | 0.033801 | 0.2898 | 0.2898 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.18386 | 0.012492 | 0.20884 | Cap-Tons/1000 sf | 10085.5 | 10642.5 | 10642.5 | 0.010493 | 0.20049 | 0.20049 | 0 | 0 | 0 | 10085.5 | 10642.5 | 10642.5 | 0.010493 | 0.20049 | 0.20049 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFL | OFFICE - LARGE | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.13686 | 0.009299 | 0.15546 | Cap-Tons/1000 sf | 9351.5 | 9817.5 | 9817.5 | 0.012358 | 0.26036 | 0.26036 | 0 | 0 | 0 | 9351.5 | 9817.5 | 9817.5 | 0.012358 | 0.26036 | 0.26036 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFS | OFFICE - SMALL | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.15528 | 0.01055 | 0.17638 | Cap-Tons/1000 sf | 6698.5 | 7177.5 | 7177.5 | 0.019236 | 0.28824 | 0.28824 | 0 | 0 | 0 | 6698.5 | 7177.5 | 7177.5 | 0.019236 | 0.28824 | 0.28824 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.27074 | 0.018395 | 0.30753 | Cap-Tons/1000 sf | 15156 | 15840 | 15840 | 0.012411 | 0.28741 | 0.28741 | 0 | 0 | 0 | 15156 | 15840 | 15840 | 0.012411 | 0.28741 | 0.28741 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.18244 | 0.012395 | 0.20723 | Cap-Tons/1000 sf | 15257 | 15840 | 15840 | 0.010279 | 0.27928 | 0.27928 | 0 | 0 | 0 | 15257 | 15840 | 15840 | 0.010279 | 0.27928 | 0.27928 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.083286 | 0.0056587 | 0.094603 | Cap-Tons/1000 sf | 5516.5 | 6077.5 | 6077.5 | 0.029288 | 0.31729 | 0.31729 | 0 | 0 | 0 | 5516.5 | 6077.5 | 6077.5 | 0.029288 | 0.31729 | 0.31729 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.096963 | 0.006588 | 0.11014 | Cap-Tons/1000 sf | 5470.5 | 6077.5 | 6077.5 | 0.031623 | 0.31662 | 0.31662 | 0 | 0 | 0 | 5470.5 | 6077.5 | 6077.5 | 0.031623 | 0.31662 | 0.31662 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTS | RETAIL - SMALL | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.10735 | 0.0072936 | 0.12193 | Cap-Tons/1000 sf | 5524.5 | 6077.5 | 6077.5 | 0.028829 | 0.31683 | 0.31683 | 0 | 0 | 0 | 5524.5 | 6077.5 | 6077.5 | 0.028829 | 0.31683 | 0.31683 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | SCN | STORAGE - CONDITIONED | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.058722 | 0.0039897 | 0.066701 | Cap-Tons/1000 sf | 1707 | 2040 | 2040 | 0.047014 | 0.28801 | 0.28801 | 0 | 0 | 0 | 1707 | 2040 | 2040 | 0.047014 | 0.28801 | 0.28801 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ASM | ASSEMBLY | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.22241 | 0.015111 | 0.25263 | Cap-Tons/1000 sf | 3129 | 5215 | 4055 | 0.63933 | 1.5983 | 0.87333 | 0 | 0 | 0 | 3129 | 5215 | 4055 | 0.63933 | 1.5983 | 0.87333 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.12957 | 0.0088032 | 0.14717 | Cap-Tons/1000 sf | 3352.5 | 5252.5 | 3867.5 | 0.44036 | 1.2174 | 0.61836 | 0 | 0 | 0 | 3352.5 | 5252.5 | 3867.5 | 0.44036 | 1.2174 | 0.61836 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.14709 | 0.0099939 | 0.16708 | Cap-Tons/1000 sf | 1930.5 | 3217.5 | 2410.5 | 0.116 | 0.29 | 0.1511 | 0 | 0 | 0 | 1930.5 | 3217.5 | 2410.5 | 0.116 | 0.29 | 0.1511 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.17624 | 0.011975 | 0.20019 | Cap-Tons/1000 sf | 3467.5 | 5252.5 | 3944.5 | 0.39895 | 1.1709 | 0.57645 | 0 | 0 | 0 | 3467.5 | 5252.5 | 3944.5 | 0.39895 | 1.1709 | 0.57645 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.14499 | 0.0098513 | 0.16469 | Cap-Tons/1000 sf | 2109.6 | 3516 | 2683.6 | 0.099333 | 0.24833 | 0.12963 | 0 | 0 | 0 | 2109.6 | 3516 | 2683.6 | 0.099333 | 0.24833 | 0.12963 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EUN | EDUCATION - UNIVERSITY | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.12971 | 0.0088131 | 0.14734 | Cap-Tons/1000 sf | 3582.5 | 5252.5 | 4021.5 | 0.35754 | 1.1245 | 0.53454 | 0 | 0 | 0 | 3582.5 | 5252.5 | 4021.5 | 0.35754 | 1.1245 | 0.53454 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | GRO | GROCERY | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.2306 | 0.015668 | 0.26194 | Cap-Tons/1000 sf | 4752 | 7920 | 5832 | 0.382 | 0.955 | 0.517 | 0 | 0 | 0 | 4752 | 7920 | 5832 | 0.382 | 0.955 | 0.517 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.18386 | 0.012492 | 0.20884 | Cap-Tons/1000 sf | 8472.5 | 10642.5 | 9024.5 | 0.14906 | 0.73106 | 0.28206 | 0 | 0 | 0 | 8472.5 | 10642.5 | 9024.5 | 0.14906 | 0.73106 | 0.28206 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HTL | LODGING - HOTEL | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.10324 | 0.0070147 | 0.11727 | Cap-Tons/1000 sf | 4077.5 | 6627.5 | 4731.5 | 0.50281 | 1.3068 | 0.68781 | 0 | 0 | 0 | 4077.5 | 6627.5 | 4731.5 | 0.50281 | 1.3068 | 0.68781 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | MTL | LODGING - MOTEL | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.10324 | 0.0070147 | 0.11727 | Cap-Tons/1000 sf | 4077.5 | 6627.5 | 4731.5 | 0.50281 | 1.3068 | 0.68781 | 0 | 0 | 0 | 4077.5 | 6627.5 | 4731.5 | 0.50281 | 1.3068 | 0.68781 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.18386 | 0.012492 | 0.20884 | Cap-Tons/1000 sf | 7082.5 | 10642.5 | 8036.5 | 0.2845 | 0.8505 | 0.4125 | 0 | 0 | 0 | 7082.5 | 10642.5 | 8036.5 | 0.2845 | 0.8505 | 0.4125 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFL | OFFICE - LARGE | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.13686 | 0.009299 | 0.15546 | Cap-Tons/1000 sf | 8607.5 | 9817.5 | 8888.5 | 0.11162 | 0.90562 | 0.29162 | 0 | 0 | 0 | 8607.5 | 9817.5 | 8888.5 | 0.11162 | 0.90562 | 0.29162 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFS | OFFICE - SMALL | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.15528 | 0.01055 | 0.17638 | Cap-Tons/1000 sf | 5857.5 | 7177.5 | 6170.5 | 0.18885 | 1.0268 | 0.37585 | 0 | 0 | 0 | 5857.5 | 7177.5 | 6170.5 | 0.18885 | 1.0268 | 0.37585 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.27074 | 0.018395 | 0.30753 | Cap-Tons/1000 sf | 12470 | 15840 | 13490 | 0.1908 | 0.8968 | 0.3628 | 0 | 0 | 0 | 12470 | 15840 | 13490 | 0.1908 | 0.8968 | 0.3628 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.18244 | 0.012395 | 0.20723 | Cap-Tons/1000 sf | 12690 | 15840 | 13628 | 0.24376 | 1.2258 | 0.48176 | 0 | 0 | 0 | 12690 | 15840 | 13628 | 0.24376 | 1.2258 | 0.48176 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.083286 | 0.0056587 | 0.094603 | Cap-Tons/1000 sf | 3646.5 | 6077.5 | 4376.5 | 0.65 | 1.625 | 0.882 | 0 | 0 | 0 | 3646.5 | 6077.5 | 4376.5 | 0.65 | 1.625 | 0.882 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.096963 | 0.006588 | 0.11014 | Cap-Tons/1000 sf | 3646.5 | 6077.5 | 4408.5 | 0.592 | 1.48 | 0.807 | 0 | 0 | 0 | 3646.5 | 6077.5 | 4408.5 | 0.592 | 1.48 | 0.807 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTS | RETAIL - SMALL | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.10735 | 0.0072936 | 0.12193 | Cap-Tons/1000 sf | 3847.5 | 6077.5 | 4470.5 | 0.5141 | 1.4011 | 0.7261 | 0 | 0 | 0 | 3847.5 | 6077.5 | 4470.5 | 0.5141 | 1.4011 | 0.7261 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | SCN | STORAGE - CONDITIONED | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.058722 | 0.0039897 | 0.066701 | Cap-Tons/1000 sf | 1224 | 2040 | 2040 | 0.088667 | 0.22167 | 0.22167 | 0 | 0 | 0 | 1224 | 2040 | 2040 | 0.088667 | 0.22167 | 0.22167 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ASM | ASSEMBLY | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.22241 | 0.015111 | 0.25263 | Cap-Tons/1000 sf | 4035 | 5215 | 5215 | 0.073403 | 0.3244 | 0.3244 | 0 | 0 | 0 | 4035 | 5215 | 5215 | 0.073403 | 0.3244 | 0.3244 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.12957 | 0.0088032 | 0.14717 | Cap-Tons/1000 sf | 4531.5 | 5252.5 | 5252.5 | 0.034049 | 0.24805 | 0.24805 | 0 | 0 | 0 | 4531.5 | 5252.5 | 5252.5 | 0.034049 | 0.24805 | 0.24805 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.14709 | 0.0099939 | 0.16708 | Cap-Tons/1000 sf | 2583.5 | 3217.5 | 3217.5 | 0.0041228 | 0.020923 | 0.020923 | 0 | 0 | 0 | 2583.5 | 3217.5 | 3217.5 | 0.0041228 | 0.020923 | 0.020923 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.17624 | 0.011975 | 0.20019 | Cap-Tons/1000 sf | 4608 | 5252.5 | 5252.5 | 0.029938 | 0.24344 | 0.24344 | 0 | 0 | 0 | 4608 | 5252.5 | 5252.5 | 0.029938 | 0.24344 | 0.24344 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.14499 | 0.0098513 | 0.16469 | Cap-Tons/1000 sf | 2712 | 3516 | 3516 | 0.0048916 | 0.021392 | 0.021392 | 0 | 0 | 0 | 2712 | 3516 | 3516 | 0.0048916 | 0.021392 | 0.021392 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EUN | EDUCATION - UNIVERSITY | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.12971 | 0.0088131 | 0.14734 | Cap-Tons/1000 sf | 4684.5 | 5252.5 | 5252.5 | 0.025826 | 0.23883 | 0.23883 | 0 | 0 | 0 | 4684.5 | 5252.5 | 5252.5 | 0.025826 | 0.23883 | 0.23883 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | GRO | GROCERY | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.2306 | 0.015668 | 0.26194 | Cap-Tons/1000 sf | 6610 | 7920 | 7920 | 0.036466 | 0.22047 | 0.22047 | 0 | 0 | 0 | 6610 | 7920 | 7920 | 0.036466 | 0.22047 | 0.22047 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFS | OFFICE - SMALL | New | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.16578 | 0.0092117 | 0.1842 | Cap-Tons/1000 sf | 6850.5 | 7177.5 | 7177.5 | 0.0091649 | 0.20116 | 0.20116 | 0 | 0 | 0 | 6850.5 | 7177.5 | 7177.5 | 0.0091649 | 0.20116 | 0.20116 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | New | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.29153 | 0.0162 | 0.32393 | Cap-Tons/1000 sf | 15246 | 15840 | 15840 | 0.0071688 | 0.19117 | 0.19117 | 0 | 0 | 0 | 15246 | 15840 | 15840 | 0.0071688 | 0.19117 | 0.19117 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | New | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.19242 | 0.010692 | 0.2138 | Cap-Tons/1000 sf | 15442 | 15840 | 15840 | 0.0045877 | 0.18259 | 0.18259 | 0 | 0 | 0 | 15442 | 15840 | 15840 | 0.0045877 | 0.18259 | 0.18259 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | New | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.083367 | 0.0046324 | 0.092632 | Cap-Tons/1000 sf | 5729.5 | 6077.5 | 6077.5 | 0.011297 | 0.1973 | 0.1973 | 0 | 0 | 0 | 5729.5 | 6077.5 | 6077.5 | 0.011297 | 0.1973 | 0.1973 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | New | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.10107 | 0.0056162 | 0.1123 | Cap-Tons/1000 sf | 5754.5 | 6077.5 | 6077.5 | 0.008644 | 0.16264 | 0.16264 | 0 | 0 | 0 | 5754.5 | 6077.5 | 6077.5 | 0.008644 | 0.16264 | 0.16264 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTS | RETAIL - SMALL | New | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.10985 | 0.0061039 | 0.12206 | Cap-Tons/1000 sf | 5659.5 | 6077.5 | 6077.5 | 0.016249 | 0.23625 | 0.23625 | 0 | 0 | 0 | 5659.5 | 6077.5 | 6077.5 | 0.016249 | 0.23625 | 0.23625 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | SCN | STORAGE - CONDITIONED | New | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.060165 | 0.0033432 | 0.066851 | Cap-Tons/1000 sf | 1929 | 2040 | 2040 | 0.0043215 | 0.079421 | 0.079421 | 0 | 0 | 0 | 1929 | 2040 | 2040 | 0.0043215 | 0.079421 | 0.079421 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ASM | ASSEMBLY | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.22348 | 0.012418 | 0.24831 | Cap-Tons/1000 sf | 3665 | 5215 | 4069 | 0.29943 | 1.0074 | 0.47143 | 0 | 0 | 0 | 3665 | 5215 | 4069 | 0.29943 | 1.0074 | 0.47143 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.12949 | 0.0071952 | 0.14388 | Cap-Tons/1000 sf | 3852.5 | 5252.5 | 4181.5 | 0.32633 | 1.2243 | 0.53233 | 0 | 0 | 0 | 3852.5 | 5252.5 | 4181.5 | 0.32633 | 1.2243 | 0.53233 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.15684 | 0.0087149 | 0.17427 | Cap-Tons/1000 sf | 2167.5 | 3217.5 | 2395.5 | 0.40547 | 1.2425 | 0.57947 | 0 | 0 | 0 | 2167.5 | 3217.5 | 2395.5 | 0.40547 | 1.2425 | 0.57947 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.18544 | 0.010304 | 0.20605 | Cap-Tons/1000 sf | 3747.5 | 5252.5 | 4099 | 0.36516 | 1.2712 | 0.57316 | 0 | 0 | 0 | 3747.5 | 5252.5 | 4099 | 0.36516 | 1.2712 | 0.57316 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.1526 | 0.0084793 | 0.16956 | Cap-Tons/1000 sf | 2456 | 3516 | 2686 | 0.37937 | 1.2584 | 0.56237 | 0 | 0 | 0 | 2456 | 3516 | 2686 | 0.37937 | 1.2584 | 0.56237 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EUN | EDUCATION - UNIVERSITY | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.13025 | 0.0072376 | 0.14473 | Cap-Tons/1000 sf | 3642.5 | 5252.5 | 4016.5 | 0.40399 | 1.318 | 0.61399 | 0 | 0 | 0 | 3642.5 | 5252.5 | 4016.5 | 0.40399 | 1.318 | 0.61399 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | GRO | GROCERY | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.23968 | 0.013318 | 0.26631 | Cap-Tons/1000 sf | 6040 | 7920 | 6589 | 0.14411 | 0.60711 | 0.25811 | 0 | 0 | 0 | 6040 | 7920 | 6589 | 0.14411 | 0.60711 | 0.25811 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.1869 | 0.010385 | 0.20767 | Cap-Tons/1000 sf | 8392.5 | 10642.5 | 8895.5 | 0.16783 | 0.79383 | 0.30483 | 0 | 0 | 0 | 8392.5 | 10642.5 | 8895.5 | 0.16783 | 0.79383 | 0.30483 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.1869 | 0.010385 | 0.20767 | Cap-Tons/1000 sf | 7902.5 | 10642.5 | 8554.5 | 0.26733 | 1.0383 | 0.43533 | 0 | 0 | 0 | 7902.5 | 10642.5 | 8554.5 | 0.26733 | 1.0383 | 0.43533 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFL | OFFICE - LARGE | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.13653 | 0.0075866 | 0.1517 | Cap-Tons/1000 sf | 8537.5 | 9817.5 | 8859.5 | 0.12249 | 0.93949 | 0.32649 | 0 | 0 | 0 | 8537.5 | 9817.5 | 8859.5 | 0.12249 | 0.93949 | 0.32649 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFS | OFFICE - SMALL | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.16578 | 0.0092117 | 0.1842 | Cap-Tons/1000 sf | 5657.5 | 7177.5 | 5974.5 | 0.2821 | 1.3321 | 0.4981 | 0 | 0 | 0 | 5657.5 | 7177.5 | 5974.5 | 0.2821 | 1.3321 | 0.4981 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | Existing | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.29153 | 0.0162 | 0.32393 | Cap-Tons/1000 sf | 13410 | 15840 | 13948 | 0.13881 | 0.90481 | 0.29881 | 0 | 0 | 0 | 13410 | 15840 | 13948 | 0.13881 | 0.90481 | 0.29881 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | Existing | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.19242 | 0.010692 | 0.2138 | Cap-Tons/1000 sf | 13970 | 15840 | 14378 | 0.11552 | 0.97852 | 0.29452 | 0 | 0 | 0 | 13970 | 15840 | 14378 | 0.11552 | 0.97852 | 0.29452 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | Existing | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.083367 | 0.0046324 | 0.092632 | Cap-Tons/1000 sf | 4677.5 | 6077.5 | 5002.5 | 0.20502 | 0.89002 | 0.36502 | 0 | 0 | 0 | 4677.5 | 6077.5 | 5002.5 | 0.20502 | 0.89002 | 0.36502 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | Existing | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.10107 | 0.0056162 | 0.1123 | Cap-Tons/1000 sf | 4747.5 | 6077.5 | 5066.5 | 0.16809 | 0.76809 | 0.30709 | 0 | 0 | 0 | 4747.5 | 6077.5 | 5066.5 | 0.16809 | 0.76809 | 0.30709 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTS | RETAIL - SMALL | Existing | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.10985 | 0.0061039 | 0.12206 | Cap-Tons/1000 sf | 4537.5 | 6077.5 | 4900.5 | 0.26439 | 1.0434 | 0.44639 | 0 | 0 | 0 | 4537.5 | 6077.5 | 4900.5 | 0.26439 | 1.0434 | 0.44639 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | SCN | STORAGE - CONDITIONED | Existing | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.060165 | 0.0033432 | 0.066851 | Cap-Tons/1000 sf | 1621 | 2040 | 1734 | 0.082714 | 0.40271 | 0.15911 | 0 | 0 | 0 | 1621 | 2040 | 1734 | 0.082714 | 0.40271 | 0.15911 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ASM | ASSEMBLY | New | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.22348 | 0.012418 | 0.24831 | Cap-Tons/1000 sf | 4889 | 5215 | 5215 | 0.010669 | 0.17067 | 0.17067 | 0 | 0 | 0 | 4889 | 5215 | 5215 | 0.010669 | 0.17067 | 0.17067 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | New | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.12949 | 0.0071952 | 0.14388 | Cap-Tons/1000 sf | 4911.5 | 5252.5 | 5252.5 | 0.015135 | 0.23314 | 0.23314 | 0 | 0 | 0 | 4911.5 | 5252.5 | 5252.5 | 0.015135 | 0.23314 | 0.23314 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | New | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.15684 | 0.0087149 | 0.17427 | Cap-Tons/1000 sf | 2980.5 | 3217.5 | 3217.5 | 0.01479 | 0.20079 | 0.20079 | 0 | 0 | 0 | 2980.5 | 3217.5 | 3217.5 | 0.01479 | 0.20079 | 0.20079 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | MTL | LODGING - MOTEL | New | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.10457 | 0.0058107 | 0.11619 | Cap-Tons/1000 sf | 5999.5 | 6627.5 | 6627.5 | 0.020621 | 0.21762 | 0.21762 | 0 | 0 | 0 | 5999.5 | 6627.5 | 6627.5 | 0.020621 | 0.21762 | 0.21762 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | New | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.1869 | 0.010385 | 0.20767 | Cap-Tons/1000 sf | 10225.5 | 10642.5 | 10642.5 | 0.0042004 | 0.1072 | 0.1072 | 0 | 0 | 0 | 10225.5 | 10642.5 | 10642.5 | 0.0042004 | 0.1072 | 0.1072 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFL | OFFICE - LARGE | New | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.13653 | 0.0075866 | 0.1517 | Cap-Tons/1000 sf | 9451.5 | 9817.5 | 9817.5 | 0.0073188 | 0.19632 | 0.19632 | 0 | 0 | 0 | 9451.5 | 9817.5 | 9817.5 | 0.0073188 | 0.19632 | 0.19632 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.18386 | 0.012492 | 0.20884 | Cap-Tons/1000 sf | 10019.5 | 10642.5 | 10642.5 | 0.0089537 | 0.15295 | 0.15295 | 0 | 0 | 0 | 10019.5 | 10642.5 | 10642.5 | 0.0089537 | 0.15295 | 0.15295 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HTL | LODGING - HOTEL | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.10324 | 0.0070147 | 0.11727 | Cap-Tons/1000 sf | 5694.5 | 6627.5 | 6627.5 | 0.034407 | 0.24441 | 0.24441 | 0 | 0 | 0 | 5694.5 | 6627.5 | 6627.5 | 0.034407 | 0.24441 | 0.24441 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | MTL | LODGING - MOTEL | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.10324 | 0.0070147 | 0.11727 | Cap-Tons/1000 sf | 5694.5 | 6627.5 | 6627.5 | 0.034407 | 0.24441 | 0.24441 | 0 | 0 | 0 | 5694.5 | 6627.5 | 6627.5 | 0.034407 | 0.24441 | 0.24441 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.18386 | 0.012492 | 0.20884 | Cap-Tons/1000 sf | 9552.5 | 10642.5 | 10642.5 | 0.014606 | 0.14261 | 0.14261 | 0 | 0 | 0 | 9552.5 | 10642.5 | 10642.5 | 0.014606 | 0.14261 | 0.14261 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFL | OFFICE - LARGE | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.13686 | 0.009299 | 0.15546 | Cap-Tons/1000 sf | 9491.5 | 9817.5 | 9817.5 | 0.0076249 | 0.22962 | 0.22962 | 0 | 0 | 0 | 9491.5 | 9817.5 | 9817.5 | 0.0076249 | 0.22962 | 0.22962 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFS | OFFICE - SMALL | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.15528 | 0.01055 | 0.17638 | Cap-Tons/1000 sf | 6787.5 | 7177.5 | 7177.5 | 0.013215 | 0.24322 | 0.24322 | 0 | 0 | 0 | 6787.5 | 7177.5 | 7177.5 | 0.013215 | 0.24322 | 0.24322 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.27074 | 0.018395 | 0.30753 | Cap-Tons/1000 sf | 14410 | 15840 | 15840 | 0.019748 | 0.21875 | 0.21875 | 0 | 0 | 0 | 14410 | 15840 | 15840 | 0.019748 | 0.21875 | 0.21875 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.18244 | 0.012395 | 0.20723 | Cap-Tons/1000 sf | 14630 | 15840 | 15840 | 0.020842 | 0.27284 | 0.27284 | 0 | 0 | 0 | 14630 | 15840 | 15840 | 0.020842 | 0.27284 | 0.27284 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.083286 | 0.0056587 | 0.094603 | Cap-Tons/1000 sf | 4967.5 | 6077.5 | 6077.5 | 0.057874 | 0.31687 | 0.31687 | 0 | 0 | 0 | 4967.5 | 6077.5 | 6077.5 | 0.057874 | 0.31687 | 0.31687 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.096963 | 0.006588 | 0.11014 | Cap-Tons/1000 sf | 4957.5 | 6077.5 | 6077.5 | 0.056254 | 0.30525 | 0.30525 | 0 | 0 | 0 | 4957.5 | 6077.5 | 6077.5 | 0.056254 | 0.30525 | 0.30525 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTS | RETAIL - SMALL | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.10735 | 0.0072936 | 0.12193 | Cap-Tons/1000 sf | 5243.5 | 6077.5 | 6077.5 | 0.038968 | 0.28397 | 0.28397 | 0 | 0 | 0 | 5243.5 | 6077.5 | 6077.5 | 0.038968 | 0.28397 | 0.28397 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | SCN | STORAGE - CONDITIONED | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.058722 | 0.0039897 | 0.066701 | Cap-Tons/1000 sf | 1224 | 2040 | 2040 | 0.088667 | 0.22167 | 0.22167 | 0 | 0 | 0 | 1224 | 2040 | 2040 | 0.088667 | 0.22167 | 0.22167 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ASM | ASSEMBLY | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.22348 | 0.012418 | 0.24831 | Cap-Tons/1000 sf | 3755 | 5215 | 4142 | 0.26556 | 0.94856 | 0.43156 | 0 | 0 | 0 | 3755 | 5215 | 4142 | 0.26556 | 0.94856 | 0.43156 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.12949 | 0.0071952 | 0.14388 | Cap-Tons/1000 sf | 4022.5 | 5252.5 | 4305.5 | 0.17307 | 0.73907 | 0.29907 | 0 | 0 | 0 | 4022.5 | 5252.5 | 4305.5 | 0.17307 | 0.73907 | 0.29907 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.15684 | 0.0087149 | 0.17427 | Cap-Tons/1000 sf | 2378.5 | 3217.5 | 2562.5 | 0.011711 | 0.044911 | 0.018301 | 0 | 0 | 0 | 2378.5 | 3217.5 | 2562.5 | 0.011711 | 0.044911 | 0.018301 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.18544 | 0.010304 | 0.20605 | Cap-Tons/1000 sf | 3952.5 | 5252.5 | 4254 | 0.18551 | 0.74901 | 0.31301 | 0 | 0 | 0 | 3952.5 | 5252.5 | 4254 | 0.18551 | 0.74901 | 0.31301 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.1526 | 0.0084793 | 0.16956 | Cap-Tons/1000 sf | 2613 | 3516 | 2813 | 0.0067388 | 0.026239 | 0.010499 | 0 | 0 | 0 | 2613 | 3516 | 2813 | 0.0067388 | 0.026239 | 0.010499 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EUN | EDUCATION - UNIVERSITY | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.13025 | 0.0072376 | 0.14473 | Cap-Tons/1000 sf | 3882.5 | 5252.5 | 4202.5 | 0.19796 | 0.75896 | 0.32696 | 0 | 0 | 0 | 3882.5 | 5252.5 | 4202.5 | 0.19796 | 0.75896 | 0.32696 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | GRO | GROCERY | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.23968 | 0.013318 | 0.26631 | Cap-Tons/1000 sf | 5940 | 7920 | 6535 | 0.11567 | 0.46267 | 0.20127 | 0 | 0 | 0 | 5940 | 7920 | 6535 | 0.11567 | 0.46267 | 0.20127 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.1869 | 0.010385 | 0.20767 | Cap-Tons/1000 sf | 8562.5 | 10642.5 | 9025.5 | 0.12608 | 0.64508 | 0.23908 | 0 | 0 | 0 | 8562.5 | 10642.5 | 9025.5 | 0.12608 | 0.64508 | 0.23908 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HTL | LODGING - HOTEL | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.10457 | 0.0058107 | 0.11619 | Cap-Tons/1000 sf | 4527.5 | 6627.5 | 5043.5 | 0.28897 | 0.91197 | 0.43697 | 0 | 0 | 0 | 4527.5 | 6627.5 | 5043.5 | 0.28897 | 0.91197 | 0.43697 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | MTL | LODGING - MOTEL | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.10457 | 0.0058107 | 0.11619 | Cap-Tons/1000 sf | 4527.5 | 6627.5 | 5043.5 | 0.28897 | 0.91197 | 0.43697 | 0 | 0 | 0 | 4527.5 | 6627.5 | 5043.5 | 0.28897 | 0.91197 | 0.43697 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.1869 | 0.010385 | 0.20767 | Cap-Tons/1000 sf | 8682.5 | 10642.5 | 9141.5 | 0.10249 | 0.55649 | 0.20049 | 0 | 0 | 0 | 8682.5 | 10642.5 | 9141.5 | 0.10249 | 0.55649 | 0.20049 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFL | OFFICE - LARGE | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.13653 | 0.0075866 | 0.1517 | Cap-Tons/1000 sf | 8577.5 | 9817.5 | 8888.5 | 0.085437 | 0.67644 | 0.23344 | 0 | 0 | 0 | 8577.5 | 9817.5 | 8888.5 | 0.085437 | 0.67644 | 0.23344 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFS | OFFICE - SMALL | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.16578 | 0.0092117 | 0.1842 | Cap-Tons/1000 sf | 5957.5 | 7177.5 | 6208.5 | 0.13229 | 0.77829 | 0.26529 | 0 | 0 | 0 | 5957.5 | 7177.5 | 6208.5 | 0.13229 | 0.77829 | 0.26529 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.29153 | 0.0162 | 0.32393 | Cap-Tons/1000 sf | 13580 | 15840 | 14081 | 0.10534 | 0.73834 | 0.23634 | 0 | 0 | 0 | 13580 | 15840 | 14081 | 0.10534 | 0.73834 | 0.23634 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.19242 | 0.010692 | 0.2138 | Cap-Tons/1000 sf | 14010 | 15840 | 14413 | 0.10058 | 0.87058 | 0.26058 | 0 | 0 | 0 | 14010 | 15840 | 14413 | 0.10058 | 0.87058 | 0.26058 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.083367 | 0.0046324 | 0.092632 | Cap-Tons/1000 sf | 4757.5 | 6077.5 | 5066.5 | 0.18312 | 0.84312 | 0.33712 | 0 | 0 | 0 | 4757.5 | 6077.5 | 5066.5 | 0.18312 | 0.84312 | 0.33712 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.10107 | 0.0056162 | 0.1123 | Cap-Tons/1000 sf | 4447.5 | 6077.5 | 4842.5 | 0.26718 | 0.99618 | 0.43718 | 0 | 0 | 0 | 4447.5 | 6077.5 | 4842.5 | 0.26718 | 0.99618 | 0.43718 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTS | RETAIL - SMALL | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.10985 | 0.0061039 | 0.12206 | Cap-Tons/1000 sf | 4597.5 | 6077.5 | 4947.5 | 0.24015 | 0.98615 | 0.41415 | 0 | 0 | 0 | 4597.5 | 6077.5 | 4947.5 | 0.24015 | 0.98615 | 0.41415 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | SCN | STORAGE - CONDITIONED | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.060165 | 0.0033432 | 0.066851 | Cap-Tons/1000 sf | 1598 | 2040 | 1721 | 0.079936 | 0.36894 | 0.14864 | 0 | 0 | 0 | 1598 | 2040 | 1721 | 0.079936 | 0.36894 | 0.14864 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ASM | ASSEMBLY | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.22348 | 0.012418 | 0.24831 | Cap-Tons/1000 sf | 4843 | 5215 | 5215 | 0.012904 | 0.1809 | 0.1809 | 0 | 0 | 0 | 4843 | 5215 | 5215 | 0.012904 | 0.1809 | 0.1809 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.12949 | 0.0071952 | 0.14388 | Cap-Tons/1000 sf | 5015.5 | 5252.5 | 5252.5 | 0.0052451 | 0.11625 | 0.11625 | 0 | 0 | 0 | 5015.5 | 5252.5 | 5252.5 | 0.0052451 | 0.11625 | 0.11625 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.15684 | 0.0087149 | 0.17427 | Cap-Tons/1000 sf | 3030.5 | 3217.5 | 3217.5 | 0.00028385 | 0.0048838 | 0.0048838 | 0 | 0 | 0 | 3030.5 | 3217.5 | 3217.5 | 0.00028385 | 0.0048838 | 0.0048838 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.18544 | 0.010304 | 0.20605 | Cap-Tons/1000 sf | 4959.5 | 5252.5 | 5252.5 | 0.0080318 | 0.13953 | 0.13953 | 0 | 0 | 0 | 4959.5 | 5252.5 | 5252.5 | 0.0080318 | 0.13953 | 0.13953 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.1526 | 0.0084793 | 0.16956 | Cap-Tons/1000 sf | 3306 | 3516 | 3516 | 0.00014737 | 0.0024674 | 0.0024674 | 0 | 0 | 0 | 3306 | 3516 | 3516 | 0.00014737 | 0.0024674 | 0.0024674 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EUN | EDUCATION - UNIVERSITY | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.13025 | 0.0072376 | 0.14473 | Cap-Tons/1000 sf | 4903.5 | 5252.5 | 5252.5 | 0.010818 | 0.16282 | 0.16282 | 0 | 0 | 0 | 4903.5 | 5252.5 | 5252.5 | 0.010818 | 0.16282 | 0.16282 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | GRO | GROCERY | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.23968 | 0.013318 | 0.26631 | Cap-Tons/1000 sf | 7453 | 7920 | 7920 | 0.0083964 | 0.1424 | 0.1424 | 0 | 0 | 0 | 7453 | 7920 | 7920 | 0.0083964 | 0.1424 | 0.1424 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.1869 | 0.010385 | 0.20767 | Cap-Tons/1000 sf | 10176.5 | 10642.5 | 10642.5 | 0.005495 | 0.1255 | 0.1255 | 0 | 0 | 0 | 10176.5 | 10642.5 | 10642.5 | 0.005495 | 0.1255 | 0.1255 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HTL | LODGING - HOTEL | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.10457 | 0.0058107 | 0.11619 | Cap-Tons/1000 sf | 6122.5 | 6627.5 | 6627.5 | 0.012785 | 0.16778 | 0.16778 | 0 | 0 | 0 | 6122.5 | 6627.5 | 6627.5 | 0.012785 | 0.16778 | 0.16778 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | MTL | LODGING - MOTEL | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.10457 | 0.0058107 | 0.11619 | Cap-Tons/1000 sf | 6122.5 | 6627.5 | 6627.5 | 0.012785 | 0.16778 | 0.16778 | 0 | 0 | 0 | 6122.5 | 6627.5 | 6627.5 | 0.012785 | 0.16778 | 0.16778 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.1869 | 0.010385 | 0.20767 | Cap-Tons/1000 sf | 10253.5 | 10642.5 | 10642.5 | 0.0032323 | 0.088432 | 0.088432 | 0 | 0 | 0 | 10253.5 | 10642.5 | 10642.5 | 0.0032323 | 0.088432 | 0.088432 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFL | OFFICE - LARGE | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.13653 | 0.0075866 | 0.1517 | Cap-Tons/1000 sf | 9441.5 | 9817.5 | 9817.5 | 0.007248 | 0.18925 | 0.18925 | 0 | 0 | 0 | 9441.5 | 9817.5 | 9817.5 | 0.007248 | 0.18925 | 0.18925 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFS | OFFICE - SMALL | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.16578 | 0.0092117 | 0.1842 | Cap-Tons/1000 sf | 6892.5 | 7177.5 | 7177.5 | 0.0066986 | 0.1687 | 0.1687 | 0 | 0 | 0 | 6892.5 | 7177.5 | 7177.5 | 0.0066986 | 0.1687 | 0.1687 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.29153 | 0.0162 | 0.32393 | Cap-Tons/1000 sf | 15339 | 15840 | 15840 | 0.004638 | 0.14664 | 0.14664 | 0 | 0 | 0 | 15339 | 15840 | 15840 | 0.004638 | 0.14664 | 0.14664 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.19242 | 0.010692 | 0.2138 | Cap-Tons/1000 sf | 15435 | 15840 | 15840 | 0.0044606 | 0.17446 | 0.17446 | 0 | 0 | 0 | 15435 | 15840 | 15840 | 0.0044606 | 0.17446 | 0.17446 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.083367 | 0.0046324 | 0.092632 | Cap-Tons/1000 sf | 5747.5 | 6077.5 | 6077.5 | 0.010335 | 0.19033 | 0.19033 | 0 | 0 | 0 | 5747.5 | 6077.5 | 6077.5 | 0.010335 | 0.19033 | 0.19033 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.10107 | 0.0056162 | 0.1123 | Cap-Tons/1000 sf | 5649.5 | 6077.5 | 6077.5 | 0.015 | 0.213 | 0.213 | 0 | 0 | 0 | 5649.5 | 6077.5 | 6077.5 | 0.015 | 0.213 | 0.213 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTS | RETAIL - SMALL | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.10985 | 0.0061039 | 0.12206 | Cap-Tons/1000 sf | 5669.5 | 6077.5 | 6077.5 | 0.0154 | 0.2294 | 0.2294 | 0 | 0 | 0 | 5669.5 | 6077.5 | 6077.5 | 0.0154 | 0.2294 | 0.2294 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | SCN | STORAGE - CONDITIONED | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.060165 | 0.0033432 | 0.066851 | Cap-Tons/1000 sf | 1917 | 2040 | 2040 | 0.0041321 | 0.068532 | 0.068532 | 0 | 0 | 0 | 1917 | 2040 | 2040 | 0.0041321 | 0.068532 | 0.068532 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ASM | ASSEMBLY | Existing | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.22348 | 0.012418 | 0.24831 | Cap-Tons/1000 sf | 3905 | 5215 | 4245 | 0.21906 | 0.87206 | 0.37806 | 0 | 0 | 0 | 3905 | 5215 | 4245 | 0.21906 | 0.87206 | 0.37806 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | Existing | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.12949 | 0.0071952 | 0.14388 | Cap-Tons/1000 sf | 3972.5 | 5252.5 | 4273.5 | 0.25713 | 1.0551 | 0.44113 | 0 | 0 | 0 | 3972.5 | 5252.5 | 4273.5 | 0.25713 | 1.0551 | 0.44113 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | Existing | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.15684 | 0.0087149 | 0.17427 | Cap-Tons/1000 sf | 2177.5 | 3217.5 | 2403.5 | 0.38734 | 1.1983 | 0.55634 | 0 | 0 | 0 | 2177.5 | 3217.5 | 2403.5 | 0.38734 | 1.1983 | 0.55634 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | Existing | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.18544 | 0.010304 | 0.20605 | Cap-Tons/1000 sf | 3857.5 | 5252.5 | 4183.5 | 0.29278 | 1.0988 | 0.47828 | 0 | 0 | 0 | 3857.5 | 5252.5 | 4183.5 | 0.29278 | 1.0988 | 0.47828 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | Existing | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.1526 | 0.0084793 | 0.16956 | Cap-Tons/1000 sf | 2436 | 3516 | 2671 | 0.39458 | 1.2846 | 0.57958 | 0 | 0 | 0 | 2436 | 3516 | 2671 | 0.39458 | 1.2846 | 0.57958 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EUN | EDUCATION - UNIVERSITY | Existing | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.13025 | 0.0072376 | 0.14473 | Cap-Tons/1000 sf | 3742.5 | 5252.5 | 4093.5 | 0.32843 | 1.1424 | 0.51543 | 0 | 0 | 0 | 3742.5 | 5252.5 | 4093.5 | 0.32843 | 1.1424 | 0.51543 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | GRO | GROCERY | Existing | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.23968 | 0.013318 | 0.26631 | Cap-Tons/1000 sf | 6320 | 7920 | 6797 | 0.081772 | 0.40477 | 0.16177 | 0 | 0 | 0 | 6320 | 7920 | 6797 | 0.081772 | 0.40477 | 0.16177 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | Existing | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.1869 | 0.010385 | 0.20767 | Cap-Tons/1000 sf | 8682.5 | 10642.5 | 9119.5 | 0.11242 | 0.61042 | 0.22142 | 0 | 0 | 0 | 8682.5 | 10642.5 | 9119.5 | 0.11242 | 0.61042 | 0.22142 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HTL | LODGING - HOTEL | Existing | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.10457 | 0.0058107 | 0.11619 | Cap-Tons/1000 sf | 4337.5 | 6627.5 | 4902.5 | 0.37379 | 1.0818 | 0.54379 | 0 | 0 | 0 | 4337.5 | 6627.5 | 4902.5 | 0.37379 | 1.0818 | 0.54379 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | MTL | LODGING - MOTEL | Existing | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.10457 | 0.0058107 | 0.11619 | Cap-Tons/1000 sf | 4337.5 | 6627.5 | 4902.5 | 0.37379 | 1.0818 | 0.54379 | 0 | 0 | 0 | 4337.5 | 6627.5 | 4902.5 | 0.37379 | 1.0818 | 0.54379 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | Existing | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.1869 | 0.010385 | 0.20767 | Cap-Tons/1000 sf | 8662.5 | 10642.5 | 9127.5 | 0.1168 | 0.6278 | 0.2278 | 0 | 0 | 0 | 8662.5 | 10642.5 | 9127.5 | 0.1168 | 0.6278 | 0.2278 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFL | OFFICE - LARGE | Existing | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.13653 | 0.0075866 | 0.1517 | Cap-Tons/1000 sf | 8557.5 | 9817.5 | 8871.5 | 0.09335 | 0.72735 | 0.25135 | 0 | 0 | 0 | 8557.5 | 9817.5 | 8871.5 | 0.09335 | 0.72735 | 0.25135 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFS | OFFICE - SMALL | Existing | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.16578 | 0.0092117 | 0.1842 | Cap-Tons/1000 sf | 5847.5 | 7177.5 | 6122.5 | 0.17013 | 0.91813 | 0.32413 | 0 | 0 | 0 | 5847.5 | 7177.5 | 6122.5 | 0.17013 | 0.91813 | 0.32413 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.10107 | 0.0056162 | 0.1123 | Cap-Tons/1000 sf | 4077.5 | 6077.5 | 4574.5 | 0.50521 | 1.5352 | 0.74521 | 0 | 0 | 0 | 4077.5 | 6077.5 | 4574.5 | 0.50521 | 1.5352 | 0.74521 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTS | RETAIL - SMALL | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.10985 | 0.0061039 | 0.12206 | Cap-Tons/1000 sf | 4237.5 | 6077.5 | 4689.5 | 0.4733 | 1.5633 | 0.7273 | 0 | 0 | 0 | 4237.5 | 6077.5 | 4689.5 | 0.4733 | 1.5633 | 0.7273 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | SCN | STORAGE - CONDITIONED | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.060165 | 0.0033432 | 0.066851 | Cap-Tons/1000 sf | 1630 | 2040 | 2040 | 0.053325 | 0.26533 | 0.26533 | 0 | 0 | 0 | 1630 | 2040 | 2040 | 0.053325 | 0.26533 | 0.26533 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ASM | ASSEMBLY | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.22348 | 0.012418 | 0.24831 | Cap-Tons/1000 sf | 4638 | 5215 | 5215 | 0.03247 | 0.29347 | 0.29347 | 0 | 0 | 0 | 4638 | 5215 | 5215 | 0.03247 | 0.29347 | 0.29347 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.12949 | 0.0071952 | 0.14388 | Cap-Tons/1000 sf | 4803.5 | 5252.5 | 5252.5 | 0.024677 | 0.28868 | 0.28868 | 0 | 0 | 0 | 4803.5 | 5252.5 | 5252.5 | 0.024677 | 0.28868 | 0.28868 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.15684 | 0.0087149 | 0.17427 | Cap-Tons/1000 sf | 2854.5 | 3217.5 | 3217.5 | 0.0082913 | 0.073491 | 0.073491 | 0 | 0 | 0 | 2854.5 | 3217.5 | 3217.5 | 0.0082913 | 0.073491 | 0.073491 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.18544 | 0.010304 | 0.20605 | Cap-Tons/1000 sf | 4814.5 | 5252.5 | 5252.5 | 0.023488 | 0.28149 | 0.28149 | 0 | 0 | 0 | 4814.5 | 5252.5 | 5252.5 | 0.023488 | 0.28149 | 0.28149 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.1526 | 0.0084793 | 0.16956 | Cap-Tons/1000 sf | 3078 | 3516 | 3516 | 0.0087372 | 0.070137 | 0.070137 | 0 | 0 | 0 | 3078 | 3516 | 3516 | 0.0087372 | 0.070137 | 0.070137 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EUN | EDUCATION - UNIVERSITY | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.13025 | 0.0072376 | 0.14473 | Cap-Tons/1000 sf | 4825.5 | 5252.5 | 5252.5 | 0.022299 | 0.2743 | 0.2743 | 0 | 0 | 0 | 4825.5 | 5252.5 | 5252.5 | 0.022299 | 0.2743 | 0.2743 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | GRO | GROCERY | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.23968 | 0.013318 | 0.26631 | Cap-Tons/1000 sf | 7244 | 7920 | 7920 | 0.02081 | 0.24381 | 0.24381 | 0 | 0 | 0 | 7244 | 7920 | 7920 | 0.02081 | 0.24381 | 0.24381 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.1869 | 0.010385 | 0.20767 | Cap-Tons/1000 sf | 10120.5 | 10642.5 | 10642.5 | 0.0088199 | 0.17982 | 0.17982 | 0 | 0 | 0 | 10120.5 | 10642.5 | 10642.5 | 0.0088199 | 0.17982 | 0.17982 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HTL | LODGING - HOTEL | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.10457 | 0.0058107 | 0.11619 | Cap-Tons/1000 sf | 5897.5 | 6627.5 | 6627.5 | 0.030945 | 0.28095 | 0.28095 | 0 | 0 | 0 | 5897.5 | 6627.5 | 6627.5 | 0.030945 | 0.28095 | 0.28095 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | MTL | LODGING - MOTEL | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.10457 | 0.0058107 | 0.11619 | Cap-Tons/1000 sf | 5897.5 | 6627.5 | 6627.5 | 0.030945 | 0.28095 | 0.28095 | 0 | 0 | 0 | 5897.5 | 6627.5 | 6627.5 | 0.030945 | 0.28095 | 0.28095 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.1869 | 0.010385 | 0.20767 | Cap-Tons/1000 sf | 9967.5 | 10642.5 | 10642.5 | 0.01158 | 0.18258 | 0.18258 | 0 | 0 | 0 | 9967.5 | 10642.5 | 10642.5 | 0.01158 | 0.18258 | 0.18258 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFL | OFFICE - LARGE | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.13653 | 0.0075866 | 0.1517 | Cap-Tons/1000 sf | 9449.5 | 9817.5 | 9817.5 | 0.0096581 | 0.25766 | 0.25766 | 0 | 0 | 0 | 9449.5 | 9817.5 | 9817.5 | 0.0096581 | 0.25766 | 0.25766 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HTL | LODGING - HOTEL | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.10457 | 0.0058107 | 0.11619 | Cap-Tons/1000 sf | 4317.5 | 6627.5 | 4886.5 | 0.41465 | 1.1896 | 0.59965 | 0 | 0 | 0 | 4317.5 | 6627.5 | 4886.5 | 0.41465 | 1.1896 | 0.59965 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | MTL | LODGING - MOTEL | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.10457 | 0.0058107 | 0.11619 | Cap-Tons/1000 sf | 4317.5 | 6627.5 | 4886.5 | 0.41465 | 1.1896 | 0.59965 | 0 | 0 | 0 | 4317.5 | 6627.5 | 4886.5 | 0.41465 | 1.1896 | 0.59965 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.1869 | 0.010385 | 0.20767 | Cap-Tons/1000 sf | 8462.5 | 10642.5 | 8974.5 | 0.15972 | 0.77972 | 0.29472 | 0 | 0 | 0 | 8462.5 | 10642.5 | 8974.5 | 0.15972 | 0.77972 | 0.29472 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFL | OFFICE - LARGE | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.13653 | 0.0075866 | 0.1517 | Cap-Tons/1000 sf | 8557.5 | 9817.5 | 8872.5 | 0.1041 | 0.8111 | 0.2801 | 0 | 0 | 0 | 8557.5 | 9817.5 | 8872.5 | 0.1041 | 0.8111 | 0.2801 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFS | OFFICE - SMALL | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.16578 | 0.0092117 | 0.1842 | Cap-Tons/1000 sf | 5797.5 | 7177.5 | 6082.5 | 0.21042 | 1.0944 | 0.39242 | 0 | 0 | 0 | 5797.5 | 7177.5 | 6082.5 | 0.21042 | 1.0944 | 0.39242 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.29153 | 0.0162 | 0.32393 | Cap-Tons/1000 sf | 13420 | 15840 | 13954 | 0.15454 | 1.0115 | 0.33354 | 0 | 0 | 0 | 13420 | 15840 | 13954 | 0.15454 | 1.0115 | 0.33354 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.19242 | 0.010692 | 0.2138 | Cap-Tons/1000 sf | 13850 | 15840 | 14283 | 0.13621 | 1.0842 | 0.33321 | 0 | 0 | 0 | 13850 | 15840 | 14283 | 0.13621 | 1.0842 | 0.33321 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.083367 | 0.0046324 | 0.092632 | Cap-Tons/1000 sf | 4297.5 | 6077.5 | 4715.5 | 0.35289 | 1.2049 | 0.55189 | 0 | 0 | 0 | 4297.5 | 6077.5 | 4715.5 | 0.35289 | 1.2049 | 0.55189 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.10107 | 0.0056162 | 0.1123 | Cap-Tons/1000 sf | 4277.5 | 6077.5 | 4709.5 | 0.34296 | 1.158 | 0.53196 | 0 | 0 | 0 | 4277.5 | 6077.5 | 4709.5 | 0.34296 | 1.158 | 0.53196 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTS | RETAIL - SMALL | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.10985 | 0.0061039 | 0.12206 | Cap-Tons/1000 sf | 4467.5 | 6077.5 | 4848.5 | 0.29335 | 1.1073 | 0.48335 | 0 | 0 | 0 | 4467.5 | 6077.5 | 4848.5 | 0.29335 | 1.1073 | 0.48335 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | SCN | STORAGE - CONDITIONED | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.060165 | 0.0033432 | 0.066851 | Cap-Tons/1000 sf | 1390 | 2040 | 1559 | 0.24129 | 0.75729 | 0.36429 | 0 | 0 | 0 | 1390 | 2040 | 1559 | 0.24129 | 0.75729 | 0.36429 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ASM | ASSEMBLY | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.22348 | 0.012418 | 0.24831 | Cap-Tons/1000 sf | 4823 | 5215 | 5215 | 0.014224 | 0.18922 | 0.18922 | 0 | 0 | 0 | 4823 | 5215 | 5215 | 0.014224 | 0.18922 | 0.18922 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.12949 | 0.0071952 | 0.14388 | Cap-Tons/1000 sf | 4894.5 | 5252.5 | 5252.5 | 0.016896 | 0.2479 | 0.2479 | 0 | 0 | 0 | 4894.5 | 5252.5 | 5252.5 | 0.016896 | 0.2479 | 0.2479 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.15684 | 0.0087149 | 0.17427 | Cap-Tons/1000 sf | 2978.5 | 3217.5 | 3217.5 | 0.015567 | 0.20957 | 0.20957 | 0 | 0 | 0 | 2978.5 | 3217.5 | 3217.5 | 0.015567 | 0.20957 | 0.20957 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.18544 | 0.010304 | 0.20605 | Cap-Tons/1000 sf | 4863.5 | 5252.5 | 5252.5 | 0.019008 | 0.25601 | 0.25601 | 0 | 0 | 0 | 4863.5 | 5252.5 | 5252.5 | 0.019008 | 0.25601 | 0.25601 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.1526 | 0.0084793 | 0.16956 | Cap-Tons/1000 sf | 3272 | 3516 | 3516 | 0.015287 | 0.22029 | 0.22029 | 0 | 0 | 0 | 3272 | 3516 | 3516 | 0.015287 | 0.22029 | 0.22029 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EUN | EDUCATION - UNIVERSITY | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.13025 | 0.0072376 | 0.14473 | Cap-Tons/1000 sf | 4832.5 | 5252.5 | 5252.5 | 0.02112 | 0.26412 | 0.26412 | 0 | 0 | 0 | 4832.5 | 5252.5 | 5252.5 | 0.02112 | 0.26412 | 0.26412 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | GRO | GROCERY | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.23968 | 0.013318 | 0.26631 | Cap-Tons/1000 sf | 7430 | 7920 | 7920 | 0.010354 | 0.16735 | 0.16735 | 0 | 0 | 0 | 7430 | 7920 | 7920 | 0.010354 | 0.16735 | 0.16735 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.1869 | 0.010385 | 0.20767 | Cap-Tons/1000 sf | 10128.5 | 10642.5 | 10642.5 | 0.0074092 | 0.15341 | 0.15341 | 0 | 0 | 0 | 10128.5 | 10642.5 | 10642.5 | 0.0074092 | 0.15341 | 0.15341 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HTL | LODGING - HOTEL | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.10457 | 0.0058107 | 0.11619 | Cap-Tons/1000 sf | 5985.5 | 6627.5 | 6627.5 | 0.023168 | 0.23917 | 0.23917 | 0 | 0 | 0 | 5985.5 | 6627.5 | 6627.5 | 0.023168 | 0.23917 | 0.23917 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | MTL | LODGING - MOTEL | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.10457 | 0.0058107 | 0.11619 | Cap-Tons/1000 sf | 5985.5 | 6627.5 | 6627.5 | 0.023168 | 0.23917 | 0.23917 | 0 | 0 | 0 | 5985.5 | 6627.5 | 6627.5 | 0.023168 | 0.23917 | 0.23917 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.1869 | 0.010385 | 0.20767 | Cap-Tons/1000 sf | 10129.5 | 10642.5 | 10642.5 | 0.0069889 | 0.14499 | 0.14499 | 0 | 0 | 0 | 10129.5 | 10642.5 | 10642.5 | 0.0069889 | 0.14499 | 0.14499 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFL | OFFICE - LARGE | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.13653 | 0.0075866 | 0.1517 | Cap-Tons/1000 sf | 9455.5 | 9817.5 | 9817.5 | 0.008078 | 0.21908 | 0.21908 | 0 | 0 | 0 | 9455.5 | 9817.5 | 9817.5 | 0.008078 | 0.21908 | 0.21908 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFS | OFFICE - SMALL | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.16578 | 0.0092117 | 0.1842 | Cap-Tons/1000 sf | 6843.5 | 7177.5 | 7177.5 | 0.010786 | 0.23179 | 0.23179 | 0 | 0 | 0 | 6843.5 | 7177.5 | 7177.5 | 0.010786 | 0.23179 | 0.23179 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.29153 | 0.0162 | 0.32393 | Cap-Tons/1000 sf | 15247 | 15840 | 15840 | 0.007973 | 0.21297 | 0.21297 | 0 | 0 | 0 | 15247 | 15840 | 15840 | 0.007973 | 0.21297 | 0.21297 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.19242 | 0.010692 | 0.2138 | Cap-Tons/1000 sf | 15407 | 15840 | 15840 | 0.0057332 | 0.20973 | 0.20973 | 0 | 0 | 0 | 15407 | 15840 | 15840 | 0.0057332 | 0.20973 | 0.20973 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.083367 | 0.0046324 | 0.092632 | Cap-Tons/1000 sf | 5592.5 | 6077.5 | 6077.5 | 0.020727 | 0.25973 | 0.25973 | 0 | 0 | 0 | 5592.5 | 6077.5 | 6077.5 | 0.020727 | 0.25973 | 0.25973 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.10107 | 0.0056162 | 0.1123 | Cap-Tons/1000 sf | 5629.5 | 6077.5 | 6077.5 | 0.016155 | 0.21915 | 0.21915 | 0 | 0 | 0 | 5629.5 | 6077.5 | 6077.5 | 0.016155 | 0.21915 | 0.21915 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTS | RETAIL - SMALL | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.10985 | 0.0061039 | 0.12206 | Cap-Tons/1000 sf | 5638.5 | 6077.5 | 6077.5 | 0.017596 | 0.2436 | 0.2436 | 0 | 0 | 0 | 5638.5 | 6077.5 | 6077.5 | 0.017596 | 0.2436 | 0.2436 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | SCN | STORAGE - CONDITIONED | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.060165 | 0.0033432 | 0.066851 | Cap-Tons/1000 sf | 1869 | 2040 | 2040 | 0.01162 | 0.13862 | 0.13862 | 0 | 0 | 0 | 1869 | 2040 | 2040 | 0.01162 | 0.13862 | 0.13862 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ASM | ASSEMBLY | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.22348 | 0.012418 | 0.24831 | Cap-Tons/1000 sf | 3205 | 5215 | 3726 | 0.66477 | 1.7248 | 0.92377 | 0 | 0 | 0 | 3205 | 5215 | 3726 | 0.66477 | 1.7248 | 0.92377 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.12949 | 0.0071952 | 0.14388 | Cap-Tons/1000 sf | 3852.5 | 5252.5 | 4184.5 | 0.33724 | 1.2652 | 0.55124 | 0 | 0 | 0 | 3852.5 | 5252.5 | 4184.5 | 0.33724 | 1.2652 | 0.55124 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.15684 | 0.0087149 | 0.17427 | Cap-Tons/1000 sf | 2067.5 | 3217.5 | 2316.5 | 0.16297 | 0.45597 | 0.22277 | 0 | 0 | 0 | 2067.5 | 3217.5 | 2316.5 | 0.16297 | 0.45597 | 0.22277 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.18544 | 0.010304 | 0.20605 | Cap-Tons/1000 sf | 3767.5 | 5252.5 | 4117 | 0.35536 | 1.2574 | 0.56336 | 0 | 0 | 0 | 3767.5 | 5252.5 | 4117 | 0.35536 | 1.2574 | 0.56336 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.1526 | 0.0084793 | 0.16956 | Cap-Tons/1000 sf | 2306 | 3516 | 2568 | 0.15374 | 0.44674 | 0.21374 | 0 | 0 | 0 | 2306 | 3516 | 2568 | 0.15374 | 0.44674 | 0.21374 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EUN | EDUCATION - UNIVERSITY | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.13025 | 0.0072376 | 0.14473 | Cap-Tons/1000 sf | 3682.5 | 5252.5 | 4049.5 | 0.37347 | 1.2495 | 0.57547 | 0 | 0 | 0 | 3682.5 | 5252.5 | 4049.5 | 0.37347 | 1.2495 | 0.57547 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | GRO | GROCERY | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.23968 | 0.013318 | 0.26631 | Cap-Tons/1000 sf | 6010 | 7920 | 6561 | 0.20435 | 0.84735 | 0.36335 | 0 | 0 | 0 | 6010 | 7920 | 6561 | 0.20435 | 0.84735 | 0.36335 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.1869 | 0.010385 | 0.20767 | Cap-Tons/1000 sf | 8362.5 | 10642.5 | 8871.5 | 0.20285 | 0.94685 | 0.36485 | 0 | 0 | 0 | 8362.5 | 10642.5 | 8871.5 | 0.20285 | 0.94685 | 0.36485 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HTL | LODGING - HOTEL | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.10457 | 0.0058107 | 0.11619 | Cap-Tons/1000 sf | 4337.5 | 6627.5 | 4905.5 | 0.45932 | 1.3293 | 0.66832 | 0 | 0 | 0 | 4337.5 | 6627.5 | 4905.5 | 0.45932 | 1.3293 | 0.66832 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | MTL | LODGING - MOTEL | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.10457 | 0.0058107 | 0.11619 | Cap-Tons/1000 sf | 4337.5 | 6627.5 | 4905.5 | 0.45932 | 1.3293 | 0.66832 | 0 | 0 | 0 | 4337.5 | 6627.5 | 4905.5 | 0.45932 | 1.3293 | 0.66832 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.1869 | 0.010385 | 0.20767 | Cap-Tons/1000 sf | 8322.5 | 10642.5 | 8866.5 | 0.20461 | 0.93861 | 0.36461 | 0 | 0 | 0 | 8322.5 | 10642.5 | 8866.5 | 0.20461 | 0.93861 | 0.36461 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFL | OFFICE - LARGE | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.13653 | 0.0075866 | 0.1517 | Cap-Tons/1000 sf | 8437.5 | 9817.5 | 8782.5 | 0.13215 | 0.94015 | 0.33415 | 0 | 0 | 0 | 8437.5 | 9817.5 | 8782.5 | 0.13215 | 0.94015 | 0.33415 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFS | OFFICE - SMALL | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.16578 | 0.0092117 | 0.1842 | Cap-Tons/1000 sf | 5777.5 | 7177.5 | 6066.5 | 0.23117 | 1.1852 | 0.42817 | 0 | 0 | 0 | 5777.5 | 7177.5 | 6066.5 | 0.23117 | 1.1852 | 0.42817 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.29153 | 0.0162 | 0.32393 | Cap-Tons/1000 sf | 13120 | 15840 | 13719 | 0.2239 | 1.3039 | 0.4499 | 0 | 0 | 0 | 13120 | 15840 | 13719 | 0.2239 | 1.3039 | 0.4499 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.19242 | 0.010692 | 0.2138 | Cap-Tons/1000 sf | 13680 | 15840 | 14151 | 0.18316 | 1.3432 | 0.42516 | 0 | 0 | 0 | 13680 | 15840 | 14151 | 0.18316 | 1.3432 | 0.42516 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.083367 | 0.0046324 | 0.092632 | Cap-Tons/1000 sf | 4227.5 | 6077.5 | 4663.5 | 0.45949 | 1.5095 | 0.70549 | 0 | 0 | 0 | 4227.5 | 6077.5 | 4663.5 | 0.45949 | 1.5095 | 0.70549 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.10107 | 0.0056162 | 0.1123 | Cap-Tons/1000 sf | 4167.5 | 6077.5 | 4624.5 | 0.46747 | 1.4875 | 0.70347 | 0 | 0 | 0 | 4167.5 | 6077.5 | 4624.5 | 0.46747 | 1.4875 | 0.70347 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTS | RETAIL - SMALL | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.10985 | 0.0061039 | 0.12206 | Cap-Tons/1000 sf | 4327.5 | 6077.5 | 4742.5 | 0.42461 | 1.4746 | 0.66861 | 0 | 0 | 0 | 4327.5 | 6077.5 | 4742.5 | 0.42461 | 1.4746 | 0.66861 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | SCN | STORAGE - CONDITIONED | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.060165 | 0.0033432 | 0.066851 | Cap-Tons/1000 sf | 1224 | 2040 | 1441 | 0.54333 | 1.3583 | 0.73533 | 0 | 0 | 0 | 1224 | 2040 | 1441 | 0.54333 | 1.3583 | 0.73533 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ASM | ASSEMBLY | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.22348 | 0.012418 | 0.24831 | Cap-Tons/1000 sf | 4697 | 5215 | 5215 | 0.029887 | 0.30089 | 0.30089 | 0 | 0 | 0 | 4697 | 5215 | 5215 | 0.029887 | 0.30089 | 0.30089 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.12949 | 0.0071952 | 0.14388 | Cap-Tons/1000 sf | 4849.5 | 5252.5 | 5252.5 | 0.022354 | 0.29135 | 0.29135 | 0 | 0 | 0 | 4849.5 | 5252.5 | 5252.5 | 0.022354 | 0.29135 | 0.29135 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.15684 | 0.0087149 | 0.17427 | Cap-Tons/1000 sf | 2962.5 | 3217.5 | 3217.5 | 0.0041144 | 0.051914 | 0.051914 | 0 | 0 | 0 | 2962.5 | 3217.5 | 3217.5 | 0.0041144 | 0.051914 | 0.051914 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.18544 | 0.010304 | 0.20605 | Cap-Tons/1000 sf | 4842 | 5252.5 | 5252.5 | 0.021682 | 0.27768 | 0.27768 | 0 | 0 | 0 | 4842 | 5252.5 | 5252.5 | 0.021682 | 0.27768 | 0.27768 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.1526 | 0.0084793 | 0.16956 | Cap-Tons/1000 sf | 3237 | 3516 | 3516 | 0.0043785 | 0.055178 | 0.055178 | 0 | 0 | 0 | 3237 | 3516 | 3516 | 0.0043785 | 0.055178 | 0.055178 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EUN | EDUCATION - UNIVERSITY | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.13025 | 0.0072376 | 0.14473 | Cap-Tons/1000 sf | 4834.5 | 5252.5 | 5252.5 | 0.02101 | 0.26401 | 0.26401 | 0 | 0 | 0 | 4834.5 | 5252.5 | 5252.5 | 0.02101 | 0.26401 | 0.26401 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | GRO | GROCERY | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.23968 | 0.013318 | 0.26631 | Cap-Tons/1000 sf | 7393 | 7920 | 7920 | 0.015112 | 0.22711 | 0.22711 | 0 | 0 | 0 | 7393 | 7920 | 7920 | 0.015112 | 0.22711 | 0.22711 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.1869 | 0.010385 | 0.20767 | Cap-Tons/1000 sf | 10124.5 | 10642.5 | 10642.5 | 0.0088 | 0.1808 | 0.1808 | 0 | 0 | 0 | 10124.5 | 10642.5 | 10642.5 | 0.0088 | 0.1808 | 0.1808 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.1526 | 0.0084793 | 0.16956 | Cap-Tons/1000 sf | 2109.6 | 3516 | 2468.6 | 0.21933 | 0.54833 | 0.28663 | 0 | 0 | 0 | 2109.6 | 3516 | 2468.6 | 0.21933 | 0.54833 | 0.28663 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EUN | EDUCATION - UNIVERSITY | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.13025 | 0.0072376 | 0.14473 | Cap-Tons/1000 sf | 3682.5 | 5252.5 | 4059.5 | 0.40076 | 1.3408 | 0.61676 | 0 | 0 | 0 | 3682.5 | 5252.5 | 4059.5 | 0.40076 | 1.3408 | 0.61676 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | GRO | GROCERY | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.23968 | 0.013318 | 0.26631 | Cap-Tons/1000 sf | 5590 | 7920 | 6269 | 0.29386 | 0.99886 | 0.46686 | 0 | 0 | 0 | 5590 | 7920 | 6269 | 0.29386 | 0.99886 | 0.46686 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.1869 | 0.010385 | 0.20767 | Cap-Tons/1000 sf | 8412.5 | 10642.5 | 8919.5 | 0.19563 | 0.93363 | 0.35663 | 0 | 0 | 0 | 8412.5 | 10642.5 | 8919.5 | 0.19563 | 0.93363 | 0.35663 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HTL | LODGING - HOTEL | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.10457 | 0.0058107 | 0.11619 | Cap-Tons/1000 sf | 4277.5 | 6627.5 | 4874.5 | 0.49939 | 1.4084 | 0.71739 | 0 | 0 | 0 | 4277.5 | 6627.5 | 4874.5 | 0.49939 | 1.4084 | 0.71739 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | MTL | LODGING - MOTEL | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.10457 | 0.0058107 | 0.11619 | Cap-Tons/1000 sf | 4277.5 | 6627.5 | 4874.5 | 0.49939 | 1.4084 | 0.71739 | 0 | 0 | 0 | 4277.5 | 6627.5 | 4874.5 | 0.49939 | 1.4084 | 0.71739 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.29153 | 0.0162 | 0.32393 | Cap-Tons/1000 sf | 12810 | 15840 | 13491 | 0.25782 | 1.3478 | 0.48582 | 0 | 0 | 0 | 12810 | 15840 | 13491 | 0.25782 | 1.3478 | 0.48582 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.19242 | 0.010692 | 0.2138 | Cap-Tons/1000 sf | 13250 | 15840 | 13823 | 0.24434 | 1.4943 | 0.50434 | 0 | 0 | 0 | 13250 | 15840 | 13823 | 0.24434 | 1.4943 | 0.50434 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.083367 | 0.0046324 | 0.092632 | Cap-Tons/1000 sf | 4317.5 | 6077.5 | 4749.5 | 0.42803 | 1.478 | 0.67203 | 0 | 0 | 0 | 4317.5 | 6077.5 | 4749.5 | 0.42803 | 1.478 | 0.67203 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFS | OFFICE - SMALL | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.16578 | 0.0092117 | 0.1842 | Cap-Tons/1000 sf | 6802.5 | 7177.5 | 7177.5 | 0.014553 | 0.27855 | 0.27855 | 0 | 0 | 0 | 6802.5 | 7177.5 | 7177.5 | 0.014553 | 0.27855 | 0.27855 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.29153 | 0.0162 | 0.32393 | Cap-Tons/1000 sf | 14985 | 15840 | 15840 | 0.014949 | 0.27695 | 0.27695 | 0 | 0 | 0 | 14985 | 15840 | 15840 | 0.014949 | 0.27695 | 0.27695 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.19242 | 0.010692 | 0.2138 | Cap-Tons/1000 sf | 15198 | 15840 | 15840 | 0.011532 | 0.28453 | 0.28453 | 0 | 0 | 0 | 15198 | 15840 | 15840 | 0.011532 | 0.28453 | 0.28453 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.083367 | 0.0046324 | 0.092632 | Cap-Tons/1000 sf | 5560.5 | 6077.5 | 6077.5 | 0.025569 | 0.30057 | 0.30057 | 0 | 0 | 0 | 5560.5 | 6077.5 | 6077.5 | 0.025569 | 0.30057 | 0.30057 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.10107 | 0.0056162 | 0.1123 | Cap-Tons/1000 sf | 5523.5 | 6077.5 | 6077.5 | 0.026379 | 0.28938 | 0.28938 | 0 | 0 | 0 | 5523.5 | 6077.5 | 6077.5 | 0.026379 | 0.28938 | 0.28938 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTS | RETAIL - SMALL | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.10985 | 0.0061039 | 0.12206 | Cap-Tons/1000 sf | 5561.5 | 6077.5 | 6077.5 | 0.025607 | 0.30161 | 0.30161 | 0 | 0 | 0 | 5561.5 | 6077.5 | 6077.5 | 0.025607 | 0.30161 | 0.30161 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | SCN | STORAGE - CONDITIONED | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.060165 | 0.0033432 | 0.066851 | Cap-Tons/1000 sf | 1630 | 2040 | 2040 | 0.053325 | 0.26533 | 0.26533 | 0 | 0 | 0 | 1630 | 2040 | 2040 | 0.053325 | 0.26533 | 0.26533 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ASM | ASSEMBLY | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.22348 | 0.012418 | 0.24831 | Cap-Tons/1000 sf | 3129 | 5215 | 3682 | 0.72 | 1.8 | 0.986 | 0 | 0 | 0 | 3129 | 5215 | 3682 | 0.72 | 1.8 | 0.986 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.12949 | 0.0071952 | 0.14388 | Cap-Tons/1000 sf | 4737.5 | 5252.5 | 5252.5 | 0.027285 | 0.27829 | 0.27829 | 0 | 0 | 0 | 4737.5 | 5252.5 | 5252.5 | 0.027285 | 0.27829 | 0.27829 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.15684 | 0.0087149 | 0.17427 | Cap-Tons/1000 sf | 1930.5 | 3217.5 | 2246.5 | 0.24667 | 0.61667 | 0.32257 | 0 | 0 | 0 | 1930.5 | 3217.5 | 2246.5 | 0.24667 | 0.61667 | 0.32257 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.18544 | 0.010304 | 0.20605 | Cap-Tons/1000 sf | 4740.5 | 5252.5 | 5252.5 | 0.026245 | 0.26925 | 0.26925 | 0 | 0 | 0 | 4740.5 | 5252.5 | 5252.5 | 0.026245 | 0.26925 | 0.26925 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.1526 | 0.0084793 | 0.16956 | Cap-Tons/1000 sf | 2109.6 | 3516 | 2468.6 | 0.23733 | 0.59333 | 0.31033 | 0 | 0 | 0 | 2109.6 | 3516 | 2468.6 | 0.23733 | 0.59333 | 0.31033 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EUN | EDUCATION - UNIVERSITY | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.13025 | 0.0072376 | 0.14473 | Cap-Tons/1000 sf | 4740.5 | 5252.5 | 5252.5 | 0.026245 | 0.26925 | 0.26925 | 0 | 0 | 0 | 4740.5 | 5252.5 | 5252.5 | 0.026245 | 0.26925 | 0.26925 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | GRO | GROCERY | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.23968 | 0.013318 | 0.26631 | Cap-Tons/1000 sf | 6000 | 7920 | 6513 | 0.22848 | 0.94248 | 0.40348 | 0 | 0 | 0 | 6000 | 7920 | 6513 | 0.22848 | 0.94248 | 0.40348 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.1869 | 0.010385 | 0.20767 | Cap-Tons/1000 sf | 10068.5 | 10642.5 | 10642.5 | 0.010718 | 0.19872 | 0.19872 | 0 | 0 | 0 | 10068.5 | 10642.5 | 10642.5 | 0.010718 | 0.19872 | 0.19872 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HTL | LODGING - HOTEL | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.10457 | 0.0058107 | 0.11619 | Cap-Tons/1000 sf | 3976.5 | 6627.5 | 4651.5 | 0.64867 | 1.6217 | 0.88167 | 0 | 0 | 0 | 3976.5 | 6627.5 | 4651.5 | 0.64867 | 1.6217 | 0.88167 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | MTL | LODGING - MOTEL | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.10457 | 0.0058107 | 0.11619 | Cap-Tons/1000 sf | 3976.5 | 6627.5 | 4651.5 | 5.8729e-05 | 1.6217 | 0.23306 | 0 | 0 | 0 | 3976.5 | 6627.5 | 4651.5 | 5.8729e-05 | 1.6217 | 0.23306 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.1869 | 0.010385 | 0.20767 | Cap-Tons/1000 sf | 10085.5 | 10642.5 | 10642.5 | 0.010493 | 0.20049 | 0.20049 | 0 | 0 | 0 | 10085.5 | 10642.5 | 10642.5 | 0.010493 | 0.20049 | 0.20049 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFL | OFFICE - LARGE | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.13653 | 0.0075866 | 0.1517 | Cap-Tons/1000 sf | 8227.5 | 9817.5 | 8625.5 | 0.16388 | 1.0119 | 0.37588 | 0 | 0 | 0 | 8227.5 | 9817.5 | 8625.5 | 0.16388 | 1.0119 | 0.37588 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFS | OFFICE - SMALL | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.16578 | 0.0092117 | 0.1842 | Cap-Tons/1000 sf | 5317.5 | 7177.5 | 5702.5 | 0.37078 | 1.4308 | 0.58978 | 0 | 0 | 0 | 5317.5 | 7177.5 | 5702.5 | 0.37078 | 1.4308 | 0.58978 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.29153 | 0.0162 | 0.32393 | Cap-Tons/1000 sf | 12840 | 15840 | 13480 | 0.27336 | 1.4434 | 0.51936 | 0 | 0 | 0 | 12840 | 15840 | 13480 | 0.27336 | 1.4434 | 0.51936 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.19242 | 0.010692 | 0.2138 | Cap-Tons/1000 sf | 13200 | 15840 | 13758 | 0.262 | 1.572 | 0.535 | 0 | 0 | 0 | 13200 | 15840 | 13758 | 0.262 | 1.572 | 0.535 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.083367 | 0.0046324 | 0.092632 | Cap-Tons/1000 sf | 3927.5 | 6077.5 | 4429.5 | 0.60216 | 1.7022 | 0.85916 | 0 | 0 | 0 | 3927.5 | 6077.5 | 4429.5 | 0.60216 | 1.7022 | 0.85916 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.10107 | 0.0056162 | 0.1123 | Cap-Tons/1000 sf | 3747.5 | 6077.5 | 4297.5 | 0.69636 | 1.8164 | 0.95836 | 0 | 0 | 0 | 3747.5 | 6077.5 | 4297.5 | 0.69636 | 1.8164 | 0.95836 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTS | RETAIL - SMALL | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.10985 | 0.0061039 | 0.12206 | Cap-Tons/1000 sf | 3997.5 | 6077.5 | 4485.5 | 0.57236 | 1.6724 | 0.82936 | 0 | 0 | 0 | 3997.5 | 6077.5 | 4485.5 | 0.57236 | 1.6724 | 0.82936 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | SCN | STORAGE - CONDITIONED | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.060165 | 0.0033432 | 0.066851 | Cap-Tons/1000 sf | 1707 | 2040 | 2040 | 0.047014 | 0.28801 | 0.28801 | 0 | 0 | 0 | 1707 | 2040 | 2040 | 0.047014 | 0.28801 | 0.28801 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ASM | ASSEMBLY | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.22348 | 0.012418 | 0.24831 | Cap-Tons/1000 sf | 4671 | 5215 | 5215 | 0.032377 | 0.31038 | 0.31038 | 0 | 0 | 0 | 4671 | 5215 | 5215 | 0.032377 | 0.31038 | 0.31038 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.12949 | 0.0071952 | 0.14388 | Cap-Tons/1000 sf | 4737.5 | 5252.5 | 5252.5 | 0.027285 | 0.27829 | 0.27829 | 0 | 0 | 0 | 4737.5 | 5252.5 | 5252.5 | 0.027285 | 0.27829 | 0.27829 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.15684 | 0.0087149 | 0.17427 | Cap-Tons/1000 sf | 2888.5 | 3217.5 | 3217.5 | 0.0082691 | 0.080869 | 0.080869 | 0 | 0 | 0 | 2888.5 | 3217.5 | 3217.5 | 0.0082691 | 0.080869 | 0.080869 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.18544 | 0.010304 | 0.20605 | Cap-Tons/1000 sf | 4739 | 5252.5 | 5252.5 | 0.026765 | 0.27377 | 0.27377 | 0 | 0 | 0 | 4739 | 5252.5 | 5252.5 | 0.026765 | 0.27377 | 0.27377 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.1526 | 0.0084793 | 0.16956 | Cap-Tons/1000 sf | 3136 | 3516 | 3516 | 0.0084943 | 0.078594 | 0.078594 | 0 | 0 | 0 | 3136 | 3516 | 3516 | 0.0084943 | 0.078594 | 0.078594 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | EUN | EDUCATION - UNIVERSITY | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.13025 | 0.0072376 | 0.14473 | Cap-Tons/1000 sf | 4740.5 | 5252.5 | 5252.5 | 0.026245 | 0.26925 | 0.26925 | 0 | 0 | 0 | 4740.5 | 5252.5 | 5252.5 | 0.026245 | 0.26925 | 0.26925 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | GRO | GROCERY | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.23968 | 0.013318 | 0.26631 | Cap-Tons/1000 sf | 7357 | 7920 | 7920 | 0.015076 | 0.21208 | 0.21208 | 0 | 0 | 0 | 7357 | 7920 | 7920 | 0.015076 | 0.21208 | 0.21208 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.1869 | 0.010385 | 0.20767 | Cap-Tons/1000 sf | 10068.5 | 10642.5 | 10642.5 | 0.010718 | 0.19872 | 0.19872 | 0 | 0 | 0 | 10068.5 | 10642.5 | 10642.5 | 0.010718 | 0.19872 | 0.19872 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | HTL | LODGING - HOTEL | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.10457 | 0.0058107 | 0.11619 | Cap-Tons/1000 sf | 5854.5 | 6627.5 | 6627.5 | 0.033801 | 0.2898 | 0.2898 | 0 | 0 | 0 | 5854.5 | 6627.5 | 6627.5 | 0.033801 | 0.2898 | 0.2898 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | MTL | LODGING - MOTEL | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.10457 | 0.0058107 | 0.11619 | Cap-Tons/1000 sf | 5854.5 | 6627.5 | 6627.5 | 0.033801 | 0.2898 | 0.2898 | 0 | 0 | 0 | 5854.5 | 6627.5 | 6627.5 | 0.033801 | 0.2898 | 0.2898 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.1869 | 0.010385 | 0.20767 | Cap-Tons/1000 sf | 10085.5 | 10642.5 | 10642.5 | 0.010493 | 0.20049 | 0.20049 | 0 | 0 | 0 | 10085.5 | 10642.5 | 10642.5 | 0.010493 | 0.20049 | 0.20049 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFL | OFFICE - LARGE | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.13653 | 0.0075866 | 0.1517 | Cap-Tons/1000 sf | 9351.5 | 9817.5 | 9817.5 | 0.012358 | 0.26036 | 0.26036 | 0 | 0 | 0 | 9351.5 | 9817.5 | 9817.5 | 0.012358 | 0.26036 | 0.26036 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | OFS | OFFICE - SMALL | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.16578 | 0.0092117 | 0.1842 | Cap-Tons/1000 sf | 6698.5 | 7177.5 | 7177.5 | 0.019236 | 0.28824 | 0.28824 | 0 | 0 | 0 | 6698.5 | 7177.5 | 7177.5 | 0.019236 | 0.28824 | 0.28824 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.29153 | 0.0162 | 0.32393 | Cap-Tons/1000 sf | 15156 | 15840 | 15840 | 0.012411 | 0.28741 | 0.28741 | 0 | 0 | 0 | 15156 | 15840 | 15840 | 0.012411 | 0.28741 | 0.28741 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.19242 | 0.010692 | 0.2138 | Cap-Tons/1000 sf | 15257 | 15840 | 15840 | 0.010279 | 0.27928 | 0.27928 | 0 | 0 | 0 | 15257 | 15840 | 15840 | 0.010279 | 0.27928 | 0.27928 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.083367 | 0.0046324 | 0.092632 | Cap-Tons/1000 sf | 5516.5 | 6077.5 | 6077.5 | 0.029288 | 0.31729 | 0.31729 | 0 | 0 | 0 | 5516.5 | 6077.5 | 6077.5 | 0.029288 | 0.31729 | 0.31729 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.10107 | 0.0056162 | 0.1123 | Cap-Tons/1000 sf | 5470.5 | 6077.5 | 6077.5 | 0.031623 | 0.31662 | 0.31662 | 0 | 0 | 0 | 5470.5 | 6077.5 | 6077.5 | 0.031623 | 0.31662 | 0.31662 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | RTS | RETAIL - SMALL | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.10985 | 0.0061039 | 0.12206 | Cap-Tons/1000 sf | 5524.5 | 6077.5 | 6077.5 | 0.028829 | 0.31683 | 0.31683 | 0 | 0 | 0 | 5524.5 | 6077.5 | 6077.5 | 0.028829 | 0.31683 | 0.31683 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-048 | HVAC - SEER Rated Package Rooftop HP (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Package Rooftop HP (SEER 15) | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 | Packaged SEER-Rated Heat Pump - SEER = 13 | Packaged SEER-Rated Heat Pump - SEER = 14 | HVAC | HeatCool | dxHP_equip | pkgSEER | pkgSEER15 | 1 | 0 | 1 | 0.85 | 16 | NA | 1 | Package SEER HP | Cap-Tons | SCN | STORAGE - CONDITIONED | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.060165 | 0.0033432 | 0.066851 | Cap-Tons/1000 sf | 1707 | 2040 | 2040 | 0.047014 | 0.28801 | 0.28801 | 0 | 0 | 0 | 1707 | 2040 | 2040 | 0.047014 | 0.28801 | 0.28801 | 0 | 0 | 0 | 75 | 15 | 15 | 15 | 5 | 0.5 | 1800 | 710 | 1680 | 397.7768 | 397.7768 | 397.7768 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | Existing | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.51248 | 0.040289 | 0.59306 | Cap-Tons/1000 sf | 667.25 | 996.25 | 790.2 | 0.30306 | 0.45306 | 0.34476 | 0 | 0 | 0 | 667.25 | 996.25 | 790.2 | 0.30306 | 0.45306 | 0.34476 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | Existing | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.6128 | 0.048175 | 0.70915 | Cap-Tons/1000 sf | 809 | 1244 | 1108 | 0.2066 | 0.3187 | 0.24615 | 0 | 0 | 0 | 809 | 1244 | 1108 | 0.2066 | 0.3187 | 0.24615 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | Existing | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.49429 | 0.038858 | 0.57201 | Cap-Tons/1000 sf | 876.5 | 1192.5 | 1007.3 | 0.32456 | 0.44146 | 0.36196 | 0 | 0 | 0 | 876.5 | 1192.5 | 1007.3 | 0.32456 | 0.44146 | 0.36196 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EUN | EDUCATION - UNIVERSITY | Existing | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.51877 | 0.037811 | 0.55658 | Cap-Tons/1000 sf | 829.65 | 1382.75 | 1033.6 | 0.3542 | 0.59033 | 0.39663 | 0 | 0 | 0 | 829.65 | 1382.75 | 1033.6 | 0.3542 | 0.59033 | 0.39663 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | GRO | GROCERY | Existing | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.86635 | 0.063144 | 0.92949 | Cap-Tons/1000 sf | 1121.25 | 1599.25 | 1490.75 | 0.17586 | 0.25081 | 0.23016 | 0 | 0 | 0 | 1121.25 | 1599.25 | 1490.75 | 0.17586 | 0.25081 | 0.23016 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | Existing | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.71085 | 0.055883 | 0.82262 | Cap-Tons/1000 sf | 1440.45 | 2400.75 | 1818.95 | 0.26703 | 0.44505 | 0.31238 | 0 | 0 | 0 | 1440.45 | 2400.75 | 1818.95 | 0.26703 | 0.44505 | 0.31238 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HTL | LODGING - HOTEL | Existing | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.4087 | 0.029788 | 0.43849 | Cap-Tons/1000 sf | 1365.15 | 2275.25 | 1701.15 | 0.30121 | 0.50202 | 0.34391 | 0 | 0 | 0 | 1365.15 | 2275.25 | 1701.15 | 0.30121 | 0.50202 | 0.34391 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | MTL | LODGING - MOTEL | Existing | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.4087 | 0.029788 | 0.43849 | Cap-Tons/1000 sf | 1365.15 | 2275.25 | 1701.15 | 0.30121 | 0.50202 | 0.34391 | 0 | 0 | 0 | 1365.15 | 2275.25 | 1701.15 | 0.30121 | 0.50202 | 0.34391 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | Existing | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.76674 | 0.055883 | 0.82262 | Cap-Tons/1000 sf | 1165.6 | 1867 | 1525.6 | 0.17268 | 0.27679 | 0.21518 | 0 | 0 | 0 | 1165.6 | 1867 | 1525.6 | 0.17268 | 0.27679 | 0.21518 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFL | OFFICE - LARGE | Existing | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.54446 | 0.039683 | 0.58414 | Cap-Tons/1000 sf | 880.448 | 1435.5599 | 1029.748 | 0.36629 | 0.59747 | 0.40748 | 0 | 0 | 0 | 880.448 | 1435.5599 | 1029.748 | 0.36629 | 0.59747 | 0.40748 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFS | OFFICE - SMALL | Existing | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.59035 | 0.04641 | 0.68317 | Cap-Tons/1000 sf | 707.3 | 1168.5 | 852.25 | 0.31759 | 0.52484 | 0.36109 | 0 | 0 | 0 | 707.3 | 1168.5 | 852.25 | 0.31759 | 0.52484 | 0.36109 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | Existing | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 1.0264 | 0.080693 | 1.1878 | Cap-Tons/1000 sf | 1173.95 | 1838.25 | 1499.45 | 0.21344 | 0.33498 | 0.25864 | 0 | 0 | 0 | 1173.95 | 1838.25 | 1499.45 | 0.21344 | 0.33498 | 0.25864 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | Existing | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.67965 | 0.05343 | 0.78651 | Cap-Tons/1000 sf | 1087.8109 | 1545.3109 | 1303.3109 | 0.25218 | 0.35958 | 0.29438 | 0 | 0 | 0 | 1087.8109 | 1545.3109 | 1303.3109 | 0.25218 | 0.35958 | 0.29438 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | Existing | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.34638 | 0.025246 | 0.37163 | Cap-Tons/1000 sf | 933.35 | 1434.25 | 1124.45 | 0.16337 | 0.25152 | 0.20082 | 0 | 0 | 0 | 933.35 | 1434.25 | 1124.45 | 0.16337 | 0.25152 | 0.20082 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | Existing | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.34652 | 0.027242 | 0.40101 | Cap-Tons/1000 sf | 987 | 1520 | 1205.5 | 0.16511 | 0.25226 | 0.19939 | 0 | 0 | 0 | 987 | 1520 | 1205.5 | 0.16511 | 0.25226 | 0.19939 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTS | RETAIL - SMALL | Existing | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.39888 | 0.031358 | 0.46159 | Cap-Tons/1000 sf | 867.25 | 1369.25 | 1069.25 | 0.23661 | 0.37392 | 0.28171 | 0 | 0 | 0 | 867.25 | 1369.25 | 1069.25 | 0.23661 | 0.37392 | 0.28171 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | SCN | STORAGE - CONDITIONED | Existing | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.22128 | 0.017396 | 0.25607 | Cap-Tons/1000 sf | 676.5 | 1028.5 | 874 | 0.14949 | 0.22819 | 0.18824 | 0 | 0 | 0 | 676.5 | 1028.5 | 874 | 0.14949 | 0.22819 | 0.18824 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ASM | ASSEMBLY | New | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.83582 | 0.065708 | 0.96724 | Cap-Tons/1000 sf | 1183.85 | 1348.5 | 1348.5 | 0.11976 | 0.1391 | 0.1391 | 0 | 0 | 0 | 1183.85 | 1348.5 | 1348.5 | 0.11976 | 0.1391 | 0.1391 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | New | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.4818 | 0.037877 | 0.55756 | Cap-Tons/1000 sf | 989 | 1177 | 1177 | 0.13709 | 0.1746 | 0.1746 | 0 | 0 | 0 | 989 | 1177 | 1177 | 0.13709 | 0.1746 | 0.1746 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | New | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.51248 | 0.040289 | 0.59306 | Cap-Tons/1000 sf | 874.65 | 996.25 | 996.25 | 0.15462 | 0.18872 | 0.18872 | 0 | 0 | 0 | 874.65 | 996.25 | 996.25 | 0.15462 | 0.18872 | 0.18872 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | New | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.6128 | 0.048175 | 0.70915 | Cap-Tons/1000 sf | 998 | 1244 | 1244 | 0.060417 | 0.076167 | 0.076167 | 0 | 0 | 0 | 998 | 1244 | 1244 | 0.060417 | 0.076167 | 0.076167 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | New | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.49429 | 0.038858 | 0.57201 | Cap-Tons/1000 sf | 1052.95 | 1192.5 | 1192.5 | 0.18657 | 0.21765 | 0.21765 | 0 | 0 | 0 | 1052.95 | 1192.5 | 1192.5 | 0.18657 | 0.21765 | 0.21765 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EUN | EDUCATION - UNIVERSITY | New | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.51877 | 0.037811 | 0.55658 | Cap-Tons/1000 sf | 1182.6 | 1382.75 | 1382.75 | 0.27139 | 0.31889 | 0.31889 | 0 | 0 | 0 | 1182.6 | 1382.75 | 1382.75 | 0.27139 | 0.31889 | 0.31889 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | GRO | GROCERY | New | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.86635 | 0.063144 | 0.92949 | Cap-Tons/1000 sf | 1239.75 | 1599.25 | 1599.25 | 0.18878 | 0.24443 | 0.24443 | 0 | 0 | 0 | 1239.75 | 1599.25 | 1599.25 | 0.18878 | 0.24443 | 0.24443 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | New | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 1.0264 | 0.080693 | 1.1878 | Cap-Tons/1000 sf | 1492.25 | 1838.25 | 1838.25 | 0.17389 | 0.21634 | 0.21634 | 0 | 0 | 0 | 1492.25 | 1838.25 | 1838.25 | 0.17389 | 0.21634 | 0.21634 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | New | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.67965 | 0.05343 | 0.78651 | Cap-Tons/1000 sf | 1349.3109 | 1545.3109 | 1545.3109 | 0.13882 | 0.15992 | 0.15992 | 0 | 0 | 0 | 1349.3109 | 1545.3109 | 1545.3109 | 0.13882 | 0.15992 | 0.15992 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | New | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.34638 | 0.025246 | 0.37163 | Cap-Tons/1000 sf | 1243.45 | 1434.25 | 1434.25 | 0.15366 | 0.19366 | 0.19366 | 0 | 0 | 0 | 1243.45 | 1434.25 | 1434.25 | 0.15366 | 0.19366 | 0.19366 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | New | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.34652 | 0.027242 | 0.40101 | Cap-Tons/1000 sf | 1324.5 | 1520 | 1520 | 0.2319 | 0.2619 | 0.2619 | 0 | 0 | 0 | 1324.5 | 1520 | 1520 | 0.2319 | 0.2619 | 0.2619 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTS | RETAIL - SMALL | New | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.39888 | 0.031358 | 0.46159 | Cap-Tons/1000 sf | 1169.75 | 1369.25 | 1369.25 | 0.15822 | 0.19739 | 0.19739 | 0 | 0 | 0 | 1169.75 | 1369.25 | 1369.25 | 0.15822 | 0.19739 | 0.19739 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | SCN | STORAGE - CONDITIONED | New | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.22128 | 0.017396 | 0.25607 | Cap-Tons/1000 sf | 831 | 1028.5 | 1028.5 | 0.1569 | 0.19595 | 0.19595 | 0 | 0 | 0 | 831 | 1028.5 | 1028.5 | 0.1569 | 0.19595 | 0.19595 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ASM | ASSEMBLY | Existing | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.83582 | 0.065708 | 0.96724 | Cap-Tons/1000 sf | 809.1 | 1348.5 | 1034.6 | 0.26905 | 0.44842 | 0.32025 | 0 | 0 | 0 | 809.1 | 1348.5 | 1034.6 | 0.26905 | 0.44842 | 0.32025 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | Existing | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.4818 | 0.037877 | 0.55756 | Cap-Tons/1000 sf | 706.2 | 1177 | 900.7 | 0.23193 | 0.38655 | 0.28218 | 0 | 0 | 0 | 706.2 | 1177 | 900.7 | 0.23193 | 0.38655 | 0.28218 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | Existing | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.51248 | 0.040289 | 0.59306 | Cap-Tons/1000 sf | 601.95 | 996.25 | 735.7 | 0.01965 | 0.032527 | 0.02314 | 0 | 0 | 0 | 601.95 | 996.25 | 735.7 | 0.01965 | 0.032527 | 0.02314 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | Existing | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.6128 | 0.048175 | 0.70915 | Cap-Tons/1000 sf | 746.4 | 1244 | 1041.9 | 0.10951 | 0.18252 | 0.13966 | 0 | 0 | 0 | 746.4 | 1244 | 1041.9 | 0.10951 | 0.18252 | 0.13966 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | Existing | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.49429 | 0.038858 | 0.57201 | Cap-Tons/1000 sf | 755.5 | 1192.5 | 897.05 | 0.012918 | 0.020404 | 0.014944 | 0 | 0 | 0 | 755.5 | 1192.5 | 897.05 | 0.012918 | 0.020404 | 0.014944 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EUN | EDUCATION - UNIVERSITY | Existing | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.51877 | 0.037811 | 0.55658 | Cap-Tons/1000 sf | 829.65 | 1382.75 | 1048.15 | 0.24586 | 0.40976 | 0.29616 | 0 | 0 | 0 | 829.65 | 1382.75 | 1048.15 | 0.24586 | 0.40976 | 0.29616 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | GRO | GROCERY | Existing | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.86635 | 0.063144 | 0.92949 | Cap-Tons/1000 sf | 959.55 | 1599.25 | 1304.55 | 0.30119 | 0.50198 | 0.34829 | 0 | 0 | 0 | 959.55 | 1599.25 | 1304.55 | 0.30119 | 0.50198 | 0.34829 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | Existing | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.71085 | 0.055883 | 0.82262 | Cap-Tons/1000 sf | 1440.45 | 2400.75 | 1832.45 | 0.24059 | 0.40098 | 0.29264 | 0 | 0 | 0 | 1440.45 | 2400.75 | 1832.45 | 0.24059 | 0.40098 | 0.29264 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HTL | LODGING - HOTEL | Existing | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.4087 | 0.029788 | 0.43849 | Cap-Tons/1000 sf | 1365.15 | 2275.25 | 1734.15 | 0.2723 | 0.45383 | 0.3237 | 0 | 0 | 0 | 1365.15 | 2275.25 | 1734.15 | 0.2723 | 0.45383 | 0.3237 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | MTL | LODGING - MOTEL | Existing | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.4087 | 0.029788 | 0.43849 | Cap-Tons/1000 sf | 1365.15 | 2275.25 | 1734.15 | 0.2723 | 0.45383 | 0.3237 | 0 | 0 | 0 | 1365.15 | 2275.25 | 1734.15 | 0.2723 | 0.45383 | 0.3237 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | Existing | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.76674 | 0.055883 | 0.82262 | Cap-Tons/1000 sf | 1120.2 | 1867 | 1497.7 | 0.23988 | 0.3998 | 0.29198 | 0 | 0 | 0 | 1120.2 | 1867 | 1497.7 | 0.23988 | 0.3998 | 0.29198 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFL | OFFICE - LARGE | Existing | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.54446 | 0.039683 | 0.58414 | Cap-Tons/1000 sf | 861.336 | 1435.5599 | 1022.786 | 0.29325 | 0.48875 | 0.344 | 0 | 0 | 0 | 861.336 | 1435.5599 | 1022.786 | 0.29325 | 0.48875 | 0.344 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFS | OFFICE - SMALL | Existing | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.59035 | 0.04641 | 0.68317 | Cap-Tons/1000 sf | 701.1 | 1168.5 | 854.4 | 0.26284 | 0.43806 | 0.31394 | 0 | 0 | 0 | 701.1 | 1168.5 | 854.4 | 0.26284 | 0.43806 | 0.31394 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | Existing | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 1.0264 | 0.080693 | 1.1878 | Cap-Tons/1000 sf | 1102.95 | 1838.25 | 1432.45 | 0.26941 | 0.44901 | 0.32186 | 0 | 0 | 0 | 1102.95 | 1838.25 | 1432.45 | 0.26941 | 0.44901 | 0.32186 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | Existing | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.67965 | 0.05343 | 0.78651 | Cap-Tons/1000 sf | 927.1865 | 1545.3109 | 1165.6865 | 0.3069 | 0.5115 | 0.3599 | 0 | 0 | 0 | 927.1865 | 1545.3109 | 1165.6865 | 0.3069 | 0.5115 | 0.3599 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | Existing | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.34638 | 0.025246 | 0.37163 | Cap-Tons/1000 sf | 860.55 | 1434.25 | 1077.55 | 0.26506 | 0.44177 | 0.31406 | 0 | 0 | 0 | 860.55 | 1434.25 | 1077.55 | 0.26506 | 0.44177 | 0.31406 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | Existing | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.34652 | 0.027242 | 0.40101 | Cap-Tons/1000 sf | 912 | 1520 | 1169.5 | 0.29026 | 0.48377 | 0.34766 | 0 | 0 | 0 | 912 | 1520 | 1169.5 | 0.29026 | 0.48377 | 0.34766 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTS | RETAIL - SMALL | Existing | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.39888 | 0.031358 | 0.46159 | Cap-Tons/1000 sf | 821.55 | 1369.25 | 1034.55 | 0.27855 | 0.46425 | 0.3283 | 0 | 0 | 0 | 821.55 | 1369.25 | 1034.55 | 0.27855 | 0.46425 | 0.3283 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | SCN | STORAGE - CONDITIONED | Existing | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.22128 | 0.017396 | 0.25607 | Cap-Tons/1000 sf | 630.5 | 1028.5 | 830 | 0.2414 | 0.3936 | 0.2943 | 0 | 0 | 0 | 630.5 | 1028.5 | 830 | 0.2414 | 0.3936 | 0.2943 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ASM | ASSEMBLY | New | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.83582 | 0.065708 | 0.96724 | Cap-Tons/1000 sf | 1112.5 | 1348.5 | 1348.5 | 0.14975 | 0.18535 | 0.18535 | 0 | 0 | 0 | 1112.5 | 1348.5 | 1348.5 | 0.14975 | 0.18535 | 0.18535 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | New | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.4818 | 0.037877 | 0.55756 | Cap-Tons/1000 sf | 982.5 | 1177 | 1177 | 0.061896 | 0.081446 | 0.081446 | 0 | 0 | 0 | 982.5 | 1177 | 1177 | 0.061896 | 0.081446 | 0.081446 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | New | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.51248 | 0.040289 | 0.59306 | Cap-Tons/1000 sf | 864 | 996.25 | 996.25 | 0 | 0 | 0 | 0 | 0 | 0 | 864 | 996.25 | 996.25 | 0 | 0 | 0 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | New | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.6128 | 0.048175 | 0.70915 | Cap-Tons/1000 sf | 1038.5 | 1244 | 1244 | 0.24807 | 0.29707 | 0.29707 | 0 | 0 | 0 | 1038.5 | 1244 | 1244 | 0.24807 | 0.29707 | 0.29707 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | New | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.49429 | 0.038858 | 0.57201 | Cap-Tons/1000 sf | 1046.8 | 1192.5 | 1192.5 | 0 | 0 | 0 | 0 | 0 | 0 | 1046.8 | 1192.5 | 1192.5 | 0 | 0 | 0 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EUN | EDUCATION - UNIVERSITY | New | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.51877 | 0.037811 | 0.55658 | Cap-Tons/1000 sf | 1167.75 | 1382.75 | 1382.75 | 0.18486 | 0.21761 | 0.21761 | 0 | 0 | 0 | 1167.75 | 1382.75 | 1382.75 | 0.18486 | 0.21761 | 0.21761 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | GRO | GROCERY | New | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.86635 | 0.063144 | 0.92949 | Cap-Tons/1000 sf | 1250.75 | 1599.25 | 1599.25 | 0.18938 | 0.24493 | 0.24493 | 0 | 0 | 0 | 1250.75 | 1599.25 | 1599.25 | 0.18938 | 0.24493 | 0.24493 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | New | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.71085 | 0.055883 | 0.82262 | Cap-Tons/1000 sf | 2005.25 | 2400.75 | 2400.75 | 0.23444 | 0.27569 | 0.27569 | 0 | 0 | 0 | 2005.25 | 2400.75 | 2400.75 | 0.23444 | 0.27569 | 0.27569 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HTL | LODGING - HOTEL | New | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.4087 | 0.029788 | 0.43849 | Cap-Tons/1000 sf | 1912.75 | 2275.25 | 2275.25 | 0.24517 | 0.28702 | 0.28702 | 0 | 0 | 0 | 1912.75 | 2275.25 | 2275.25 | 0.24517 | 0.28702 | 0.28702 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | MTL | LODGING - MOTEL | New | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.4087 | 0.029788 | 0.43849 | Cap-Tons/1000 sf | 1912.75 | 2275.25 | 2275.25 | 0.24517 | 0.28702 | 0.28702 | 0 | 0 | 0 | 1912.75 | 2275.25 | 2275.25 | 0.24517 | 0.28702 | 0.28702 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | New | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.76674 | 0.055883 | 0.82262 | Cap-Tons/1000 sf | 1490.5 | 1867 | 1867 | 0.18968 | 0.23313 | 0.23313 | 0 | 0 | 0 | 1490.5 | 1867 | 1867 | 0.18968 | 0.23313 | 0.23313 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFL | OFFICE - LARGE | New | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.54446 | 0.039683 | 0.58414 | Cap-Tons/1000 sf | 1283.7099 | 1435.5599 | 1435.5599 | 0.35279 | 0.38619 | 0.38619 | 0 | 0 | 0 | 1283.7099 | 1435.5599 | 1435.5599 | 0.35279 | 0.38619 | 0.38619 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFS | OFFICE - SMALL | New | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.59035 | 0.04641 | 0.68317 | Cap-Tons/1000 sf | 1017.2 | 1168.5 | 1168.5 | 0.28802 | 0.32407 | 0.32407 | 0 | 0 | 0 | 1017.2 | 1168.5 | 1168.5 | 0.28802 | 0.32407 | 0.32407 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | New | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 1.0264 | 0.080693 | 1.1878 | Cap-Tons/1000 sf | 1485.75 | 1838.25 | 1838.25 | 0.13463 | 0.16873 | 0.16873 | 0 | 0 | 0 | 1485.75 | 1838.25 | 1838.25 | 0.13463 | 0.16873 | 0.16873 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | New | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.67965 | 0.05343 | 0.78651 | Cap-Tons/1000 sf | 1299.3109 | 1545.3109 | 1545.3109 | 0.38221 | 0.44886 | 0.44886 | 0 | 0 | 0 | 1299.3109 | 1545.3109 | 1545.3109 | 0.38221 | 0.44886 | 0.44886 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | New | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.34638 | 0.025246 | 0.37163 | Cap-Tons/1000 sf | 1212.75 | 1434.25 | 1434.25 | 0.14285 | 0.169 | 0.169 | 0 | 0 | 0 | 1212.75 | 1434.25 | 1434.25 | 0.14285 | 0.169 | 0.169 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | New | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.34652 | 0.027242 | 0.40101 | Cap-Tons/1000 sf | 1258 | 1520 | 1520 | 0.16635 | 0.19985 | 0.19985 | 0 | 0 | 0 | 1258 | 1520 | 1520 | 0.16635 | 0.19985 | 0.19985 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTS | RETAIL - SMALL | New | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.39888 | 0.031358 | 0.46159 | Cap-Tons/1000 sf | 1152.75 | 1369.25 | 1369.25 | 0.19444 | 0.22854 | 0.22854 | 0 | 0 | 0 | 1152.75 | 1369.25 | 1369.25 | 0.19444 | 0.22854 | 0.22854 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | SCN | STORAGE - CONDITIONED | New | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.22128 | 0.017396 | 0.25607 | Cap-Tons/1000 sf | 826 | 1028.5 | 1028.5 | 0.19211 | 0.23586 | 0.23586 | 0 | 0 | 0 | 826 | 1028.5 | 1028.5 | 0.19211 | 0.23586 | 0.23586 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ASM | ASSEMBLY | Existing | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.83582 | 0.065708 | 0.96724 | Cap-Tons/1000 sf | 809.1 | 1348.5 | 1012.75 | 0.23499 | 0.39166 | 0.27436 | 0 | 0 | 0 | 809.1 | 1348.5 | 1012.75 | 0.23499 | 0.39166 | 0.27436 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.67965 | 0.05343 | 0.78651 | Cap-Tons/1000 sf | 1348.3109 | 1545.3109 | 1545.3109 | 0.39378 | 0.44393 | 0.44393 | 0 | 0 | 0 | 1348.3109 | 1545.3109 | 1545.3109 | 0.39378 | 0.44393 | 0.44393 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.34638 | 0.025246 | 0.37163 | Cap-Tons/1000 sf | 1226.65 | 1434.25 | 1434.25 | 0.36708 | 0.41588 | 0.41588 | 0 | 0 | 0 | 1226.65 | 1434.25 | 1434.25 | 0.36708 | 0.41588 | 0.41588 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.34652 | 0.027242 | 0.40101 | Cap-Tons/1000 sf | 1283.5 | 1520 | 1520 | 0.40148 | 0.45943 | 0.45943 | 0 | 0 | 0 | 1283.5 | 1520 | 1520 | 0.40148 | 0.45943 | 0.45943 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | New | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 1.0264 | 0.080693 | 1.1878 | Cap-Tons/1000 sf | 1486.75 | 1838.25 | 1838.25 | 0.14399 | 0.17929 | 0.17929 | 0 | 0 | 0 | 1486.75 | 1838.25 | 1838.25 | 0.14399 | 0.17929 | 0.17929 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | New | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.67965 | 0.05343 | 0.78651 | Cap-Tons/1000 sf | 1296.8109 | 1545.3109 | 1545.3109 | 0.26871 | 0.31946 | 0.31946 | 0 | 0 | 0 | 1296.8109 | 1545.3109 | 1545.3109 | 0.26871 | 0.31946 | 0.31946 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | New | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.34638 | 0.025246 | 0.37163 | Cap-Tons/1000 sf | 1210.25 | 1434.25 | 1434.25 | 0.21261 | 0.25096 | 0.25096 | 0 | 0 | 0 | 1210.25 | 1434.25 | 1434.25 | 0.21261 | 0.25096 | 0.25096 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | GRO | GROCERY | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 1.0397 | 0.066148 | 1.1059 | Cap-Tons/1000 sf | 1263.25 | 1599.25 | 1599.25 | 0.18531 | 0.23851 | 0.23851 | 0 | 0 | 0 | 1263.25 | 1599.25 | 1599.25 | 0.18531 | 0.23851 | 0.23851 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.77621 | 0.052738 | 0.88169 | Cap-Tons/1000 sf | 2000.25 | 2400.75 | 2400.75 | 0.232 | 0.2733 | 0.2733 | 0 | 0 | 0 | 2000.25 | 2400.75 | 2400.75 | 0.232 | 0.2733 | 0.2733 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HTL | LODGING - HOTEL | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.46549 | 0.029615 | 0.49511 | Cap-Tons/1000 sf | 1889.75 | 2275.25 | 2275.25 | 0.24957 | 0.29402 | 0.29402 | 0 | 0 | 0 | 1889.75 | 2275.25 | 2275.25 | 0.24957 | 0.29402 | 0.29402 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.79463 | 0.050555 | 0.84519 | Cap-Tons/1000 sf | 989 | 1244 | 1244 | 0.23422 | 0.29452 | 0.29452 | 0 | 0 | 0 | 989 | 1244 | 1244 | 0.23422 | 0.29452 | 0.29452 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ASM | ASSEMBLY | Existing | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.83582 | 0.065708 | 0.96724 | Cap-Tons/1000 sf | 983.5 | 1348.5 | 1140.5 | 0.198 | 0.27085 | 0.22448 | 0 | 0 | 0 | 983.5 | 1348.5 | 1140.5 | 0.198 | 0.27085 | 0.22448 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | Existing | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.4818 | 0.037877 | 0.55756 | Cap-Tons/1000 sf | 714 | 1177 | 897.1 | 0.26326 | 0.43405 | 0.30546 | 0 | 0 | 0 | 714 | 1177 | 897.1 | 0.26326 | 0.43405 | 0.30546 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | New | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.71085 | 0.055883 | 0.82262 | Cap-Tons/1000 sf | 2019.25 | 2400.75 | 2400.75 | 0.23584 | 0.28214 | 0.28214 | 0 | 0 | 0 | 2019.25 | 2400.75 | 2400.75 | 0.23584 | 0.28214 | 0.28214 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HTL | LODGING - HOTEL | New | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.4087 | 0.029788 | 0.43849 | Cap-Tons/1000 sf | 1980.75 | 2275.25 | 2275.25 | 0.25897 | 0.30282 | 0.30282 | 0 | 0 | 0 | 1980.75 | 2275.25 | 2275.25 | 0.25897 | 0.30282 | 0.30282 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | MTL | LODGING - MOTEL | New | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.4087 | 0.029788 | 0.43849 | Cap-Tons/1000 sf | 1980.75 | 2275.25 | 2275.25 | 0.25897 | 0.30282 | 0.30282 | 0 | 0 | 0 | 1980.75 | 2275.25 | 2275.25 | 0.25897 | 0.30282 | 0.30282 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | New | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.76674 | 0.055883 | 0.82262 | Cap-Tons/1000 sf | 1509.5 | 1867 | 1867 | 0.18322 | 0.22822 | 0.22822 | 0 | 0 | 0 | 1509.5 | 1867 | 1867 | 0.18322 | 0.22822 | 0.22822 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFL | OFFICE - LARGE | New | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.54446 | 0.039683 | 0.58414 | Cap-Tons/1000 sf | 1294.4099 | 1435.5599 | 1435.5599 | 0.52091 | 0.56816 | 0.56816 | 0 | 0 | 0 | 1294.4099 | 1435.5599 | 1435.5599 | 0.52091 | 0.56816 | 0.56816 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFS | OFFICE - SMALL | New | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.59035 | 0.04641 | 0.68317 | Cap-Tons/1000 sf | 1024.9 | 1168.5 | 1168.5 | 0.19592 | 0.23676 | 0.23676 | 0 | 0 | 0 | 1024.9 | 1168.5 | 1168.5 | 0.19592 | 0.23676 | 0.23676 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | New | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.49429 | 0.038858 | 0.57201 | Cap-Tons/1000 sf | 1060.7 | 1192.5 | 1192.5 | 0 | 0 | 0 | 0 | 0 | 0 | 1060.7 | 1192.5 | 1192.5 | 0 | 0 | 0 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EUN | EDUCATION - UNIVERSITY | New | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.51877 | 0.037811 | 0.55658 | Cap-Tons/1000 sf | 1179.6 | 1382.75 | 1382.75 | 0.38137 | 0.42897 | 0.42897 | 0 | 0 | 0 | 1179.6 | 1382.75 | 1382.75 | 0.38137 | 0.42897 | 0.42897 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | GRO | GROCERY | New | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.86635 | 0.063144 | 0.92949 | Cap-Tons/1000 sf | 1249.25 | 1599.25 | 1599.25 | 0.17831 | 0.23136 | 0.23136 | 0 | 0 | 0 | 1249.25 | 1599.25 | 1599.25 | 0.17831 | 0.23136 | 0.23136 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | New | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.51248 | 0.040289 | 0.59306 | Cap-Tons/1000 sf | 866.9 | 996.25 | 996.25 | 0.30144 | 0.34374 | 0.34374 | 0 | 0 | 0 | 866.9 | 996.25 | 996.25 | 0.30144 | 0.34374 | 0.34374 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | New | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.6128 | 0.048175 | 0.70915 | Cap-Tons/1000 sf | 1055 | 1244 | 1244 | 0.29635 | 0.34925 | 0.34925 | 0 | 0 | 0 | 1055 | 1244 | 1244 | 0.29635 | 0.34925 | 0.34925 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | New | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.49429 | 0.038858 | 0.57201 | Cap-Tons/1000 sf | 1050.55 | 1192.5 | 1192.5 | 0.33299 | 0.37639 | 0.37639 | 0 | 0 | 0 | 1050.55 | 1192.5 | 1192.5 | 0.33299 | 0.37639 | 0.37639 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | MTL | LODGING - MOTEL | Existing | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.4087 | 0.029788 | 0.43849 | Cap-Tons/1000 sf | 1365.15 | 2275.25 | 1736.65 | 0.2819 | 0.46984 | 0.322 | 0 | 0 | 0 | 1365.15 | 2275.25 | 1736.65 | 0.2819 | 0.46984 | 0.322 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | Existing | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.76674 | 0.055883 | 0.82262 | Cap-Tons/1000 sf | 1120.2 | 1867 | 1501.7 | 0.25636 | 0.42727 | 0.29951 | 0 | 0 | 0 | 1120.2 | 1867 | 1501.7 | 0.25636 | 0.42727 | 0.29951 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFL | OFFICE - LARGE | Existing | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.54446 | 0.039683 | 0.58414 | Cap-Tons/1000 sf | 861.336 | 1435.5599 | 1023.936 | 0.30686 | 0.51143 | 0.34786 | 0 | 0 | 0 | 861.336 | 1435.5599 | 1023.936 | 0.30686 | 0.51143 | 0.34786 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTS | RETAIL - SMALL | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.39888 | 0.031358 | 0.46159 | Cap-Tons/1000 sf | 1143.75 | 1369.25 | 1369.25 | 0.23052 | 0.27342 | 0.27342 | 0 | 0 | 0 | 1143.75 | 1369.25 | 1369.25 | 0.23052 | 0.27342 | 0.27342 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | SCN | STORAGE - CONDITIONED | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.22128 | 0.017396 | 0.25607 | Cap-Tons/1000 sf | 822 | 1028.5 | 1028.5 | 0.17193 | 0.21578 | 0.21578 | 0 | 0 | 0 | 822 | 1028.5 | 1028.5 | 0.17193 | 0.21578 | 0.21578 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ASM | ASSEMBLY | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.93897 | 0.063797 | 1.0666 | Cap-Tons/1000 sf | 820.8 | 1348.5 | 985.4 | 0.32034 | 0.52602 | 0.35589 | 0 | 0 | 0 | 820.8 | 1348.5 | 985.4 | 0.32034 | 0.52602 | 0.35589 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.77022 | 0.052331 | 0.87488 | Cap-Tons/1000 sf | 1307.8109 | 1545.3109 | 1545.3109 | 0.36871 | 0.42476 | 0.42476 | 0 | 0 | 0 | 1307.8109 | 1545.3109 | 1545.3109 | 0.36871 | 0.42476 | 0.42476 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.37551 | 0.02389 | 0.3994 | Cap-Tons/1000 sf | 1208.75 | 1434.25 | 1434.25 | 0.24524 | 0.28594 | 0.28594 | 0 | 0 | 0 | 1208.75 | 1434.25 | 1434.25 | 0.24524 | 0.28594 | 0.28594 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.40936 | 0.027814 | 0.46499 | Cap-Tons/1000 sf | 1252 | 1520 | 1520 | 0.21329 | 0.25574 | 0.25574 | 0 | 0 | 0 | 1252 | 1520 | 1520 | 0.21329 | 0.25574 | 0.25574 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFS | OFFICE - SMALL | New | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 0.65556 | 0.044541 | 0.74464 | Cap-Tons/1000 sf | 1012.9 | 1168.5 | 1168.5 | 0.33832 | 0.37982 | 0.37982 | 0 | 0 | 0 | 1012.9 | 1168.5 | 1168.5 | 0.33832 | 0.37982 | 0.37982 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | New | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 1.143 | 0.077662 | 1.2984 | Cap-Tons/1000 sf | 1490.25 | 1838.25 | 1838.25 | 0.13129 | 0.16244 | 0.16244 | 0 | 0 | 0 | 1490.25 | 1838.25 | 1838.25 | 0.13129 | 0.16244 | 0.16244 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | New | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 0.77022 | 0.052331 | 0.87488 | Cap-Tons/1000 sf | 1296.8109 | 1545.3109 | 1545.3109 | 0.10351 | 0.12481 | 0.12481 | 0 | 0 | 0 | 1296.8109 | 1545.3109 | 1545.3109 | 0.10351 | 0.12481 | 0.12481 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.61214 | 0.041591 | 0.69532 | Cap-Tons/1000 sf | 1028 | 1192.5 | 1192.5 | 0.19487 | 0.22662 | 0.22662 | 0 | 0 | 0 | 1028 | 1192.5 | 1192.5 | 0.19487 | 0.22662 | 0.22662 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EUN | EDUCATION - UNIVERSITY | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.58484 | 0.037208 | 0.62204 | Cap-Tons/1000 sf | 1159.25 | 1382.75 | 1382.75 | 0.19883 | 0.23543 | 0.23543 | 0 | 0 | 0 | 1159.25 | 1382.75 | 1382.75 | 0.19883 | 0.23543 | 0.23543 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ASM | ASSEMBLY | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.93897 | 0.063797 | 1.0666 | Cap-Tons/1000 sf | 1115 | 1348.5 | 1348.5 | 0.34371 | 0.40741 | 0.40741 | 0 | 0 | 0 | 1115 | 1348.5 | 1348.5 | 0.34371 | 0.40741 | 0.40741 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.54701 | 0.037166 | 0.62134 | Cap-Tons/1000 sf | 967 | 1177 | 1177 | 0.21929 | 0.26269 | 0.26269 | 0 | 0 | 0 | 967 | 1177 | 1177 | 0.21929 | 0.26269 | 0.26269 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.621 | 0.042193 | 0.70538 | Cap-Tons/1000 sf | 856.9 | 996.25 | 996.25 | 0 | 0 | 0 | 0 | 0 | 0 | 856.9 | 996.25 | 996.25 | 0 | 0 | 0 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | SCN | STORAGE - CONDITIONED | Existing | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.25401 | 0.014114 | 0.28224 | Cap-Tons/1000 sf | 642 | 1028.5 | 835.5 | 0.28975 | 0.46199 | 0.34045 | 0 | 0 | 0 | 642 | 1028.5 | 835.5 | 0.28975 | 0.46199 | 0.34045 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ASM | ASSEMBLY | New | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.94349 | 0.052426 | 1.0483 | Cap-Tons/1000 sf | 1162.1 | 1348.5 | 1348.5 | 0.60906 | 0.66341 | 0.66341 | 0 | 0 | 0 | 1162.1 | 1348.5 | 1348.5 | 0.60906 | 0.66341 | 0.66341 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | New | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.54668 | 0.030377 | 0.60743 | Cap-Tons/1000 sf | 999.25 | 1177 | 1177 | 0.34967 | 0.39757 | 0.39757 | 0 | 0 | 0 | 999.25 | 1177 | 1177 | 0.34967 | 0.39757 | 0.39757 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | Existing | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.4818 | 0.037877 | 0.55756 | Cap-Tons/1000 sf | 706.2 | 1177 | 891 | 0.085736 | 0.14289 | 0.10712 | 0 | 0 | 0 | 706.2 | 1177 | 891 | 0.085736 | 0.14289 | 0.10712 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | Existing | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.51248 | 0.040289 | 0.59306 | Cap-Tons/1000 sf | 616.45 | 996.25 | 739.85 | 0.0017723 | 0.0028603 | 0.0021188 | 0 | 0 | 0 | 616.45 | 996.25 | 739.85 | 0.0017723 | 0.0028603 | 0.0021188 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | Existing | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.6128 | 0.048175 | 0.70915 | Cap-Tons/1000 sf | 769.6 | 1244 | 1020.6 | 0.029125 | 0.047154 | 0.036495 | 0 | 0 | 0 | 769.6 | 1244 | 1020.6 | 0.029125 | 0.047154 | 0.036495 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | Existing | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.49429 | 0.038858 | 0.57201 | Cap-Tons/1000 sf | 772.5 | 1192.5 | 905.1 | 0 | 0 | 0 | 0 | 0 | 0 | 772.5 | 1192.5 | 905.1 | 0 | 0 | 0 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EUN | EDUCATION - UNIVERSITY | Existing | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.51877 | 0.037811 | 0.55658 | Cap-Tons/1000 sf | 829.65 | 1382.75 | 1039.25 | 0.1329 | 0.2215 | 0.16038 | 0 | 0 | 0 | 829.65 | 1382.75 | 1039.25 | 0.1329 | 0.2215 | 0.16038 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | GRO | GROCERY | Existing | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.86635 | 0.063144 | 0.92949 | Cap-Tons/1000 sf | 1000.25 | 1599.25 | 1352.75 | 0.25474 | 0.40974 | 0.30249 | 0 | 0 | 0 | 1000.25 | 1599.25 | 1352.75 | 0.25474 | 0.40974 | 0.30249 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | Existing | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.71085 | 0.055883 | 0.82262 | Cap-Tons/1000 sf | 1440.45 | 2400.75 | 1825.45 | 0.2369 | 0.39484 | 0.28205 | 0 | 0 | 0 | 1440.45 | 2400.75 | 1825.45 | 0.2369 | 0.39484 | 0.28205 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HTL | LODGING - HOTEL | Existing | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.4087 | 0.029788 | 0.43849 | Cap-Tons/1000 sf | 1365.15 | 2275.25 | 1727.15 | 0.27477 | 0.45794 | 0.31792 | 0 | 0 | 0 | 1365.15 | 2275.25 | 1727.15 | 0.27477 | 0.45794 | 0.31792 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | MTL | LODGING - MOTEL | Existing | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.4087 | 0.029788 | 0.43849 | Cap-Tons/1000 sf | 1365.15 | 2275.25 | 1727.15 | 0.27477 | 0.45794 | 0.31792 | 0 | 0 | 0 | 1365.15 | 2275.25 | 1727.15 | 0.27477 | 0.45794 | 0.31792 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | Existing | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.76674 | 0.055883 | 0.82262 | Cap-Tons/1000 sf | 1120.2 | 1867 | 1488.7 | 0.23457 | 0.39096 | 0.28312 | 0 | 0 | 0 | 1120.2 | 1867 | 1488.7 | 0.23457 | 0.39096 | 0.28312 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFL | OFFICE - LARGE | Existing | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.54446 | 0.039683 | 0.58414 | Cap-Tons/1000 sf | 861.336 | 1435.5599 | 1016.336 | 0.23103 | 0.38505 | 0.26743 | 0 | 0 | 0 | 861.336 | 1435.5599 | 1016.336 | 0.23103 | 0.38505 | 0.26743 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFS | OFFICE - SMALL | Existing | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.59035 | 0.04641 | 0.68317 | Cap-Tons/1000 sf | 701.1 | 1168.5 | 849.7 | 0.18471 | 0.30785 | 0.21223 | 0 | 0 | 0 | 701.1 | 1168.5 | 849.7 | 0.18471 | 0.30785 | 0.21223 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | Existing | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 1.0264 | 0.080693 | 1.1878 | Cap-Tons/1000 sf | 1102.95 | 1838.25 | 1427.45 | 0.26359 | 0.43932 | 0.31149 | 0 | 0 | 0 | 1102.95 | 1838.25 | 1427.45 | 0.26359 | 0.43932 | 0.31149 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | Existing | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.67965 | 0.05343 | 0.78651 | Cap-Tons/1000 sf | 957.2487 | 1545.3109 | 1177.7487 | 0.27363 | 0.4406 | 0.309 | 0 | 0 | 0 | 957.2487 | 1545.3109 | 1177.7487 | 0.27363 | 0.4406 | 0.309 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | Existing | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.34638 | 0.025246 | 0.37163 | Cap-Tons/1000 sf | 860.55 | 1434.25 | 1074.55 | 0.28692 | 0.47819 | 0.33382 | 0 | 0 | 0 | 860.55 | 1434.25 | 1074.55 | 0.28692 | 0.47819 | 0.33382 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | Existing | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.34652 | 0.027242 | 0.40101 | Cap-Tons/1000 sf | 912 | 1520 | 1160.5 | 0.28046 | 0.46744 | 0.32986 | 0 | 0 | 0 | 912 | 1520 | 1160.5 | 0.28046 | 0.46744 | 0.32986 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTS | RETAIL - SMALL | Existing | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.39888 | 0.031358 | 0.46159 | Cap-Tons/1000 sf | 821.55 | 1369.25 | 1031.55 | 0.29901 | 0.49834 | 0.34521 | 0 | 0 | 0 | 821.55 | 1369.25 | 1031.55 | 0.29901 | 0.49834 | 0.34521 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | SCN | STORAGE - CONDITIONED | Existing | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.22128 | 0.017396 | 0.25607 | Cap-Tons/1000 sf | 669 | 1028.5 | 860 | 0.13943 | 0.21492 | 0.17793 | 0 | 0 | 0 | 669 | 1028.5 | 860 | 0.13943 | 0.21492 | 0.17793 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ASM | ASSEMBLY | New | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.83582 | 0.065708 | 0.96724 | Cap-Tons/1000 sf | 1166.5 | 1348.5 | 1348.5 | 0.48185 | 0.5367 | 0.5367 | 0 | 0 | 0 | 1166.5 | 1348.5 | 1348.5 | 0.48185 | 0.5367 | 0.5367 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | New | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.4818 | 0.037877 | 0.55756 | Cap-Tons/1000 sf | 990.25 | 1177 | 1177 | 0.33194 | 0.38219 | 0.38219 | 0 | 0 | 0 | 990.25 | 1177 | 1177 | 0.33194 | 0.38219 | 0.38219 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | New | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.51248 | 0.040289 | 0.59306 | Cap-Tons/1000 sf | 874.6 | 996.25 | 996.25 | 0 | 0 | 0 | 0 | 0 | 0 | 874.6 | 996.25 | 996.25 | 0 | 0 | 0 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | New | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.6128 | 0.048175 | 0.70915 | Cap-Tons/1000 sf | 1067 | 1244 | 1244 | 0 | 0 | 0 | 0 | 0 | 0 | 1067 | 1244 | 1244 | 0 | 0 | 0 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | New | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.71085 | 0.055883 | 0.82262 | Cap-Tons/1000 sf | 2010.25 | 2400.75 | 2400.75 | 0.26458 | 0.31078 | 0.31078 | 0 | 0 | 0 | 2010.25 | 2400.75 | 2400.75 | 0.26458 | 0.31078 | 0.31078 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HTL | LODGING - HOTEL | New | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.4087 | 0.029788 | 0.43849 | Cap-Tons/1000 sf | 1933.25 | 2275.25 | 2275.25 | 0.32645 | 0.37495 | 0.37495 | 0 | 0 | 0 | 1933.25 | 2275.25 | 2275.25 | 0.32645 | 0.37495 | 0.37495 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | MTL | LODGING - MOTEL | New | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.4087 | 0.029788 | 0.43849 | Cap-Tons/1000 sf | 1933.25 | 2275.25 | 2275.25 | 0.32645 | 0.37495 | 0.37495 | 0 | 0 | 0 | 1933.25 | 2275.25 | 2275.25 | 0.32645 | 0.37495 | 0.37495 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | New | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.76674 | 0.055883 | 0.82262 | Cap-Tons/1000 sf | 1498.5 | 1867 | 1867 | 0.20742 | 0.25557 | 0.25557 | 0 | 0 | 0 | 1498.5 | 1867 | 1867 | 0.20742 | 0.25557 | 0.25557 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFL | OFFICE - LARGE | New | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.54446 | 0.039683 | 0.58414 | Cap-Tons/1000 sf | 1287.5099 | 1435.5599 | 1435.5599 | 0.58328 | 0.62928 | 0.62928 | 0 | 0 | 0 | 1287.5099 | 1435.5599 | 1435.5599 | 0.58328 | 0.62928 | 0.62928 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFS | OFFICE - SMALL | New | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.59035 | 0.04641 | 0.68317 | Cap-Tons/1000 sf | 1020.7 | 1168.5 | 1168.5 | 0.43149 | 0.48024 | 0.48024 | 0 | 0 | 0 | 1020.7 | 1168.5 | 1168.5 | 0.43149 | 0.48024 | 0.48024 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | New | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 1.0264 | 0.080693 | 1.1878 | Cap-Tons/1000 sf | 1504.75 | 1838.25 | 1838.25 | 0.24135 | 0.29245 | 0.29245 | 0 | 0 | 0 | 1504.75 | 1838.25 | 1838.25 | 0.24135 | 0.29245 | 0.29245 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | New | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.67965 | 0.05343 | 0.78651 | Cap-Tons/1000 sf | 1339.3109 | 1545.3109 | 1545.3109 | 0.36003 | 0.41258 | 0.41258 | 0 | 0 | 0 | 1339.3109 | 1545.3109 | 1545.3109 | 0.36003 | 0.41258 | 0.41258 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | New | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.34638 | 0.025246 | 0.37163 | Cap-Tons/1000 sf | 1219.25 | 1434.25 | 1434.25 | 0.31266 | 0.35896 | 0.35896 | 0 | 0 | 0 | 1219.25 | 1434.25 | 1434.25 | 0.31266 | 0.35896 | 0.35896 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | New | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.34652 | 0.027242 | 0.40101 | Cap-Tons/1000 sf | 1278 | 1520 | 1520 | 0.32605 | 0.3771 | 0.3771 | 0 | 0 | 0 | 1278 | 1520 | 1520 | 0.32605 | 0.3771 | 0.3771 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTS | RETAIL - SMALL | New | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.39888 | 0.031358 | 0.46159 | Cap-Tons/1000 sf | 1157.75 | 1369.25 | 1369.25 | 0.29769 | 0.34574 | 0.34574 | 0 | 0 | 0 | 1157.75 | 1369.25 | 1369.25 | 0.29769 | 0.34574 | 0.34574 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | SCN | STORAGE - CONDITIONED | New | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.22128 | 0.017396 | 0.25607 | Cap-Tons/1000 sf | 837 | 1028.5 | 1028.5 | 0.23171 | 0.28461 | 0.28461 | 0 | 0 | 0 | 837 | 1028.5 | 1028.5 | 0.23171 | 0.28461 | 0.28461 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ASM | ASSEMBLY | Existing | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.83582 | 0.065708 | 0.96724 | Cap-Tons/1000 sf | 809.1 | 1348.5 | 1030.1 | 0.29961 | 0.49935 | 0.34646 | 0 | 0 | 0 | 809.1 | 1348.5 | 1030.1 | 0.29961 | 0.49935 | 0.34646 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | Existing | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.4818 | 0.037877 | 0.55756 | Cap-Tons/1000 sf | 706.2 | 1177 | 897.2 | 0.11444 | 0.19074 | 0.13789 | 0 | 0 | 0 | 706.2 | 1177 | 897.2 | 0.11444 | 0.19074 | 0.13789 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | Existing | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.51248 | 0.040289 | 0.59306 | Cap-Tons/1000 sf | 597.75 | 996.25 | 727.95 | 0.050739 | 0.084565 | 0.061474 | 0 | 0 | 0 | 597.75 | 996.25 | 727.95 | 0.050739 | 0.084565 | 0.061474 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | Existing | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.6128 | 0.048175 | 0.70915 | Cap-Tons/1000 sf | 746.4 | 1244 | 1010.4 | 0.21217 | 0.35361 | 0.26997 | 0 | 0 | 0 | 746.4 | 1244 | 1010.4 | 0.21217 | 0.35361 | 0.26997 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | Existing | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.49429 | 0.038858 | 0.57201 | Cap-Tons/1000 sf | 738 | 1192.5 | 876.85 | 0.025126 | 0.040555 | 0.029236 | 0 | 0 | 0 | 738 | 1192.5 | 876.85 | 0.025126 | 0.040555 | 0.029236 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EUN | EDUCATION - UNIVERSITY | Existing | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.51877 | 0.037811 | 0.55658 | Cap-Tons/1000 sf | 829.65 | 1382.75 | 1048.15 | 0.14997 | 0.24995 | 0.18282 | 0 | 0 | 0 | 829.65 | 1382.75 | 1048.15 | 0.14997 | 0.24995 | 0.18282 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | GRO | GROCERY | Existing | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.86635 | 0.063144 | 0.92949 | Cap-Tons/1000 sf | 959.55 | 1599.25 | 1303.55 | 0.30078 | 0.50131 | 0.34923 | 0 | 0 | 0 | 959.55 | 1599.25 | 1303.55 | 0.30078 | 0.50131 | 0.34923 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | Existing | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.71085 | 0.055883 | 0.82262 | Cap-Tons/1000 sf | 1440.45 | 2400.75 | 1831.45 | 0.2388 | 0.39799 | 0.28435 | 0 | 0 | 0 | 1440.45 | 2400.75 | 1831.45 | 0.2388 | 0.39799 | 0.28435 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HTL | LODGING - HOTEL | Existing | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.4087 | 0.029788 | 0.43849 | Cap-Tons/1000 sf | 1365.15 | 2275.25 | 1740.65 | 0.27245 | 0.45408 | 0.3186 | 0 | 0 | 0 | 1365.15 | 2275.25 | 1740.65 | 0.27245 | 0.45408 | 0.3186 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | MTL | LODGING - MOTEL | Existing | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.4087 | 0.029788 | 0.43849 | Cap-Tons/1000 sf | 1365.15 | 2275.25 | 1740.65 | 0.27245 | 0.45408 | 0.3186 | 0 | 0 | 0 | 1365.15 | 2275.25 | 1740.65 | 0.27245 | 0.45408 | 0.3186 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | Existing | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.76674 | 0.055883 | 0.82262 | Cap-Tons/1000 sf | 1120.2 | 1867 | 1496.2 | 0.25479 | 0.42465 | 0.30139 | 0 | 0 | 0 | 1120.2 | 1867 | 1496.2 | 0.25479 | 0.42465 | 0.30139 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFL | OFFICE - LARGE | Existing | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.54446 | 0.039683 | 0.58414 | Cap-Tons/1000 sf | 861.336 | 1435.5599 | 1023.336 | 0.22843 | 0.38072 | 0.26908 | 0 | 0 | 0 | 861.336 | 1435.5599 | 1023.336 | 0.22843 | 0.38072 | 0.26908 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFS | OFFICE - SMALL | Existing | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.59035 | 0.04641 | 0.68317 | Cap-Tons/1000 sf | 701.1 | 1168.5 | 855.9 | 0.18069 | 0.30115 | 0.21494 | 0 | 0 | 0 | 701.1 | 1168.5 | 855.9 | 0.18069 | 0.30115 | 0.21494 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | Existing | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 1.0264 | 0.080693 | 1.1878 | Cap-Tons/1000 sf | 1102.95 | 1838.25 | 1431.95 | 0.29414 | 0.49024 | 0.33989 | 0 | 0 | 0 | 1102.95 | 1838.25 | 1431.95 | 0.29414 | 0.49024 | 0.33989 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | Existing | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.67965 | 0.05343 | 0.78651 | Cap-Tons/1000 sf | 927.1865 | 1545.3109 | 1164.6865 | 0.34682 | 0.57804 | 0.39302 | 0 | 0 | 0 | 927.1865 | 1545.3109 | 1164.6865 | 0.34682 | 0.57804 | 0.39302 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | Existing | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.34638 | 0.025246 | 0.37163 | Cap-Tons/1000 sf | 860.55 | 1434.25 | 1081.55 | 0.27566 | 0.45944 | 0.31926 | 0 | 0 | 0 | 860.55 | 1434.25 | 1081.55 | 0.27566 | 0.45944 | 0.31926 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | Existing | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.34652 | 0.027242 | 0.40101 | Cap-Tons/1000 sf | 912 | 1520 | 1174 | 0.28727 | 0.47879 | 0.33702 | 0 | 0 | 0 | 912 | 1520 | 1174 | 0.28727 | 0.47879 | 0.33702 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTS | RETAIL - SMALL | Existing | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.39888 | 0.031358 | 0.46159 | Cap-Tons/1000 sf | 821.55 | 1369.25 | 1036.05 | 0.28053 | 0.46755 | 0.32578 | 0 | 0 | 0 | 821.55 | 1369.25 | 1036.05 | 0.28053 | 0.46755 | 0.32578 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | SCN | STORAGE - CONDITIONED | Existing | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.22128 | 0.017396 | 0.25607 | Cap-Tons/1000 sf | 622.5 | 1028.5 | 822 | 0.28459 | 0.46986 | 0.33509 | 0 | 0 | 0 | 622.5 | 1028.5 | 822 | 0.28459 | 0.46986 | 0.33509 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ASM | ASSEMBLY | New | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.83582 | 0.065708 | 0.96724 | Cap-Tons/1000 sf | 1113.5 | 1348.5 | 1348.5 | 0.2772 | 0.32755 | 0.32755 | 0 | 0 | 0 | 1113.5 | 1348.5 | 1348.5 | 0.2772 | 0.32755 | 0.32755 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | New | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.4818 | 0.037877 | 0.55756 | Cap-Tons/1000 sf | 982.5 | 1177 | 1177 | 0.17185 | 0.20605 | 0.20605 | 0 | 0 | 0 | 982.5 | 1177 | 1177 | 0.17185 | 0.20605 | 0.20605 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.34652 | 0.027242 | 0.40101 | Cap-Tons/1000 sf | 912 | 1520 | 1154 | 0.31538 | 0.52563 | 0.37138 | 0 | 0 | 0 | 912 | 1520 | 1154 | 0.31538 | 0.52563 | 0.37138 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTS | RETAIL - SMALL | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.39888 | 0.031358 | 0.46159 | Cap-Tons/1000 sf | 821.55 | 1369.25 | 1034.55 | 0.29742 | 0.49571 | 0.34787 | 0 | 0 | 0 | 821.55 | 1369.25 | 1034.55 | 0.29742 | 0.49571 | 0.34787 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | SCN | STORAGE - CONDITIONED | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.22128 | 0.017396 | 0.25607 | Cap-Tons/1000 sf | 673.5 | 1028.5 | 863 | 0.17785 | 0.27134 | 0.22045 | 0 | 0 | 0 | 673.5 | 1028.5 | 863 | 0.17785 | 0.27134 | 0.22045 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EUN | EDUCATION - UNIVERSITY | New | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.51877 | 0.037811 | 0.55658 | Cap-Tons/1000 sf | 1165.25 | 1382.75 | 1382.75 | 0.23778 | 0.27518 | 0.27518 | 0 | 0 | 0 | 1165.25 | 1382.75 | 1382.75 | 0.23778 | 0.27518 | 0.27518 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | GRO | GROCERY | New | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.86635 | 0.063144 | 0.92949 | Cap-Tons/1000 sf | 1254.25 | 1599.25 | 1599.25 | 0.17789 | 0.23009 | 0.23009 | 0 | 0 | 0 | 1254.25 | 1599.25 | 1599.25 | 0.17789 | 0.23009 | 0.23009 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | New | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.71085 | 0.055883 | 0.82262 | Cap-Tons/1000 sf | 2000.25 | 2400.75 | 2400.75 | 0.23653 | 0.27923 | 0.27923 | 0 | 0 | 0 | 2000.25 | 2400.75 | 2400.75 | 0.23653 | 0.27923 | 0.27923 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HTL | LODGING - HOTEL | New | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.4087 | 0.029788 | 0.43849 | Cap-Tons/1000 sf | 1904.25 | 2275.25 | 2275.25 | 0.25967 | 0.30332 | 0.30332 | 0 | 0 | 0 | 1904.25 | 2275.25 | 2275.25 | 0.25967 | 0.30332 | 0.30332 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | MTL | LODGING - MOTEL | New | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.4087 | 0.029788 | 0.43849 | Cap-Tons/1000 sf | 1904.25 | 2275.25 | 2275.25 | 0.25967 | 0.30332 | 0.30332 | 0 | 0 | 0 | 1904.25 | 2275.25 | 2275.25 | 0.25967 | 0.30332 | 0.30332 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | New | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.76674 | 0.055883 | 0.82262 | Cap-Tons/1000 sf | 1488 | 1867 | 1867 | 0.19512 | 0.24022 | 0.24022 | 0 | 0 | 0 | 1488 | 1867 | 1867 | 0.19512 | 0.24022 | 0.24022 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFL | OFFICE - LARGE | New | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.54446 | 0.039683 | 0.58414 | Cap-Tons/1000 sf | 1281.1599 | 1435.5599 | 1435.5599 | 0.41546 | 0.45511 | 0.45511 | 0 | 0 | 0 | 1281.1599 | 1435.5599 | 1435.5599 | 0.41546 | 0.45511 | 0.45511 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFS | OFFICE - SMALL | New | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.59035 | 0.04641 | 0.68317 | Cap-Tons/1000 sf | 1013.4 | 1168.5 | 1168.5 | 0.3592 | 0.40415 | 0.40415 | 0 | 0 | 0 | 1013.4 | 1168.5 | 1168.5 | 0.3592 | 0.40415 | 0.40415 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | New | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 1.0264 | 0.080693 | 1.1878 | Cap-Tons/1000 sf | 1490.75 | 1838.25 | 1838.25 | 0.1977 | 0.24265 | 0.24265 | 0 | 0 | 0 | 1490.75 | 1838.25 | 1838.25 | 0.1977 | 0.24265 | 0.24265 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | New | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.67965 | 0.05343 | 0.78651 | Cap-Tons/1000 sf | 1298.3109 | 1545.3109 | 1545.3109 | 0.28142 | 0.33037 | 0.33037 | 0 | 0 | 0 | 1298.3109 | 1545.3109 | 1545.3109 | 0.28142 | 0.33037 | 0.33037 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | New | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.34638 | 0.025246 | 0.37163 | Cap-Tons/1000 sf | 1208.75 | 1434.25 | 1434.25 | 0.17226 | 0.20416 | 0.20416 | 0 | 0 | 0 | 1208.75 | 1434.25 | 1434.25 | 0.17226 | 0.20416 | 0.20416 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | New | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.34652 | 0.027242 | 0.40101 | Cap-Tons/1000 sf | 1254.5 | 1520 | 1520 | 0.19508 | 0.23438 | 0.23438 | 0 | 0 | 0 | 1254.5 | 1520 | 1520 | 0.19508 | 0.23438 | 0.23438 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTS | RETAIL - SMALL | New | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.39888 | 0.031358 | 0.46159 | Cap-Tons/1000 sf | 1149.25 | 1369.25 | 1369.25 | 0.1917 | 0.2267 | 0.2267 | 0 | 0 | 0 | 1149.25 | 1369.25 | 1369.25 | 0.1917 | 0.2267 | 0.2267 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | SCN | STORAGE - CONDITIONED | New | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.22128 | 0.017396 | 0.25607 | Cap-Tons/1000 sf | 827 | 1028.5 | 1028.5 | 0.20845 | 0.25545 | 0.25545 | 0 | 0 | 0 | 827 | 1028.5 | 1028.5 | 0.20845 | 0.25545 | 0.25545 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ASM | ASSEMBLY | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.83582 | 0.065708 | 0.96724 | Cap-Tons/1000 sf | 817.8 | 1348.5 | 982.35 | 0.32088 | 0.5289 | 0.35648 | 0 | 0 | 0 | 817.8 | 1348.5 | 982.35 | 0.32088 | 0.5289 | 0.35648 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.4818 | 0.037877 | 0.55756 | Cap-Tons/1000 sf | 706.2 | 1177 | 887.8 | 0.26305 | 0.43842 | 0.3077 | 0 | 0 | 0 | 706.2 | 1177 | 887.8 | 0.26305 | 0.43842 | 0.3077 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.51248 | 0.040289 | 0.59306 | Cap-Tons/1000 sf | 607.45 | 996.25 | 728.55 | 0.33101 | 0.54224 | 0.37656 | 0 | 0 | 0 | 607.45 | 996.25 | 728.55 | 0.33101 | 0.54224 | 0.37656 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.6128 | 0.048175 | 0.70915 | Cap-Tons/1000 sf | 746.4 | 1244 | 1016.4 | 0.24128 | 0.40213 | 0.27933 | 0 | 0 | 0 | 746.4 | 1244 | 1016.4 | 0.24128 | 0.40213 | 0.27933 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.49429 | 0.038858 | 0.57201 | Cap-Tons/1000 sf | 766.5 | 1192.5 | 894.05 | 0.4614 | 0.71374 | 0.50935 | 0 | 0 | 0 | 766.5 | 1192.5 | 894.05 | 0.4614 | 0.71374 | 0.50935 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EUN | EDUCATION - UNIVERSITY | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.51877 | 0.037811 | 0.55658 | Cap-Tons/1000 sf | 829.65 | 1382.75 | 1039.25 | 0.27067 | 0.45111 | 0.31912 | 0 | 0 | 0 | 829.65 | 1382.75 | 1039.25 | 0.27067 | 0.45111 | 0.31912 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | GRO | GROCERY | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.86635 | 0.063144 | 0.92949 | Cap-Tons/1000 sf | 1010.25 | 1599.25 | 1363.75 | 0.31107 | 0.49557 | 0.35912 | 0 | 0 | 0 | 1010.25 | 1599.25 | 1363.75 | 0.31107 | 0.49557 | 0.35912 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.71085 | 0.055883 | 0.82262 | Cap-Tons/1000 sf | 1440.45 | 2400.75 | 1823.95 | 0.24058 | 0.40096 | 0.28758 | 0 | 0 | 0 | 1440.45 | 2400.75 | 1823.95 | 0.24058 | 0.40096 | 0.28758 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HTL | LODGING - HOTEL | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.4087 | 0.029788 | 0.43849 | Cap-Tons/1000 sf | 1365.15 | 2275.25 | 1730.15 | 0.27424 | 0.45707 | 0.32434 | 0 | 0 | 0 | 1365.15 | 2275.25 | 1730.15 | 0.27424 | 0.45707 | 0.32434 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | MTL | LODGING - MOTEL | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.4087 | 0.029788 | 0.43849 | Cap-Tons/1000 sf | 1365.15 | 2275.25 | 1730.15 | 0.27424 | 0.45707 | 0.32434 | 0 | 0 | 0 | 1365.15 | 2275.25 | 1730.15 | 0.27424 | 0.45707 | 0.32434 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.76674 | 0.055883 | 0.82262 | Cap-Tons/1000 sf | 1120.2 | 1867 | 1489.7 | 0.25791 | 0.42985 | 0.30471 | 0 | 0 | 0 | 1120.2 | 1867 | 1489.7 | 0.25791 | 0.42985 | 0.30471 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFL | OFFICE - LARGE | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.54446 | 0.039683 | 0.58414 | Cap-Tons/1000 sf | 861.336 | 1435.5599 | 1020.086 | 0.2793 | 0.4655 | 0.3289 | 0 | 0 | 0 | 861.336 | 1435.5599 | 1020.086 | 0.2793 | 0.4655 | 0.3289 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFS | OFFICE - SMALL | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.59035 | 0.04641 | 0.68317 | Cap-Tons/1000 sf | 701.1 | 1168.5 | 851.75 | 0.25785 | 0.42975 | 0.3071 | 0 | 0 | 0 | 701.1 | 1168.5 | 851.75 | 0.25785 | 0.42975 | 0.3071 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 1.0264 | 0.080693 | 1.1878 | Cap-Tons/1000 sf | 1102.95 | 1838.25 | 1425.45 | 0.28836 | 0.48059 | 0.33471 | 0 | 0 | 0 | 1102.95 | 1838.25 | 1425.45 | 0.28836 | 0.48059 | 0.33471 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.67965 | 0.05343 | 0.78651 | Cap-Tons/1000 sf | 955.7487 | 1545.3109 | 1176.7487 | 0.3277 | 0.52827 | 0.36895 | 0 | 0 | 0 | 955.7487 | 1545.3109 | 1176.7487 | 0.3277 | 0.52827 | 0.36895 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.34638 | 0.025246 | 0.37163 | Cap-Tons/1000 sf | 860.55 | 1434.25 | 1074.75 | 0.31253 | 0.52088 | 0.36333 | 0 | 0 | 0 | 860.55 | 1434.25 | 1074.75 | 0.31253 | 0.52088 | 0.36333 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ASM | ASSEMBLY | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.83582 | 0.065708 | 0.96724 | Cap-Tons/1000 sf | 1188.45 | 1348.5 | 1348.5 | 0.52549 | 0.57679 | 0.57679 | 0 | 0 | 0 | 1188.45 | 1348.5 | 1348.5 | 0.52549 | 0.57679 | 0.57679 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.4818 | 0.037877 | 0.55756 | Cap-Tons/1000 sf | 989.5 | 1177 | 1177 | 0.322 | 0.37345 | 0.37345 | 0 | 0 | 0 | 989.5 | 1177 | 1177 | 0.322 | 0.37345 | 0.37345 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.51248 | 0.040289 | 0.59306 | Cap-Tons/1000 sf | 873.45 | 996.25 | 996.25 | 0.39759 | 0.44749 | 0.44749 | 0 | 0 | 0 | 873.45 | 996.25 | 996.25 | 0.39759 | 0.44749 | 0.44749 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.6128 | 0.048175 | 0.70915 | Cap-Tons/1000 sf | 1063.5 | 1244 | 1244 | 0.24183 | 0.28263 | 0.28263 | 0 | 0 | 0 | 1063.5 | 1244 | 1244 | 0.24183 | 0.28263 | 0.28263 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.49429 | 0.038858 | 0.57201 | Cap-Tons/1000 sf | 1066.6 | 1192.5 | 1192.5 | 0.46856 | 0.51851 | 0.51851 | 0 | 0 | 0 | 1066.6 | 1192.5 | 1192.5 | 0.46856 | 0.51851 | 0.51851 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EUN | EDUCATION - UNIVERSITY | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.51877 | 0.037811 | 0.55658 | Cap-Tons/1000 sf | 1178.55 | 1382.75 | 1382.75 | 0.45568 | 0.50878 | 0.50878 | 0 | 0 | 0 | 1178.55 | 1382.75 | 1382.75 | 0.45568 | 0.50878 | 0.50878 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | GRO | GROCERY | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.86635 | 0.063144 | 0.92949 | Cap-Tons/1000 sf | 1250.75 | 1599.25 | 1599.25 | 0.17986 | 0.23391 | 0.23391 | 0 | 0 | 0 | 1250.75 | 1599.25 | 1599.25 | 0.17986 | 0.23391 | 0.23391 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.71085 | 0.055883 | 0.82262 | Cap-Tons/1000 sf | 2013.75 | 2400.75 | 2400.75 | 0.27622 | 0.32512 | 0.32512 | 0 | 0 | 0 | 2013.75 | 2400.75 | 2400.75 | 0.27622 | 0.32512 | 0.32512 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HTL | LODGING - HOTEL | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.4087 | 0.029788 | 0.43849 | Cap-Tons/1000 sf | 1927.25 | 2275.25 | 2275.25 | 0.31601 | 0.36706 | 0.36706 | 0 | 0 | 0 | 1927.25 | 2275.25 | 2275.25 | 0.31601 | 0.36706 | 0.36706 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | MTL | LODGING - MOTEL | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.4087 | 0.029788 | 0.43849 | Cap-Tons/1000 sf | 1927.25 | 2275.25 | 2275.25 | 0.31601 | 0.36706 | 0.36706 | 0 | 0 | 0 | 1927.25 | 2275.25 | 2275.25 | 0.31601 | 0.36706 | 0.36706 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.76674 | 0.055883 | 0.82262 | Cap-Tons/1000 sf | 1501.5 | 1867 | 1867 | 0.19782 | 0.24487 | 0.24487 | 0 | 0 | 0 | 1501.5 | 1867 | 1867 | 0.19782 | 0.24487 | 0.24487 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFL | OFFICE - LARGE | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.54446 | 0.039683 | 0.58414 | Cap-Tons/1000 sf | 1283.9099 | 1435.5599 | 1435.5599 | 0.57036 | 0.62036 | 0.62036 | 0 | 0 | 0 | 1283.9099 | 1435.5599 | 1435.5599 | 0.57036 | 0.62036 | 0.62036 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFS | OFFICE - SMALL | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.59035 | 0.04641 | 0.68317 | Cap-Tons/1000 sf | 1019.1 | 1168.5 | 1168.5 | 0.43325 | 0.4862 | 0.4862 | 0 | 0 | 0 | 1019.1 | 1168.5 | 1168.5 | 0.43325 | 0.4862 | 0.4862 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 1.0264 | 0.080693 | 1.1878 | Cap-Tons/1000 sf | 1509.25 | 1838.25 | 1838.25 | 0.24163 | 0.29288 | 0.29288 | 0 | 0 | 0 | 1509.25 | 1838.25 | 1838.25 | 0.24163 | 0.29288 | 0.29288 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTS | RETAIL - SMALL | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.39888 | 0.031358 | 0.46159 | Cap-Tons/1000 sf | 1159.75 | 1369.25 | 1369.25 | 0.32984 | 0.38139 | 0.38139 | 0 | 0 | 0 | 1159.75 | 1369.25 | 1369.25 | 0.32984 | 0.38139 | 0.38139 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | SCN | STORAGE - CONDITIONED | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.22128 | 0.017396 | 0.25607 | Cap-Tons/1000 sf | 838 | 1028.5 | 1028.5 | 0.21404 | 0.26464 | 0.26464 | 0 | 0 | 0 | 838 | 1028.5 | 1028.5 | 0.21404 | 0.26464 | 0.26464 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ASM | ASSEMBLY | Existing | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.83582 | 0.065708 | 0.96724 | Cap-Tons/1000 sf | 809.1 | 1348.5 | 1032.1 | 0.27141 | 0.45236 | 0.30631 | 0 | 0 | 0 | 809.1 | 1348.5 | 1032.1 | 0.27141 | 0.45236 | 0.30631 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | Existing | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.4818 | 0.037877 | 0.55756 | Cap-Tons/1000 sf | 706.2 | 1177 | 920.2 | 0.13708 | 0.22847 | 0.16603 | 0 | 0 | 0 | 706.2 | 1177 | 920.2 | 0.13708 | 0.22847 | 0.16603 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | Existing | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.51248 | 0.040289 | 0.59306 | Cap-Tons/1000 sf | 597.75 | 996.25 | 756.25 | 0.16259 | 0.27098 | 0.20384 | 0 | 0 | 0 | 597.75 | 996.25 | 756.25 | 0.16259 | 0.27098 | 0.20384 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | Existing | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.6128 | 0.048175 | 0.70915 | Cap-Tons/1000 sf | 746.4 | 1244 | 1052.9 | 0.22085 | 0.36808 | 0.28105 | 0 | 0 | 0 | 746.4 | 1244 | 1052.9 | 0.22085 | 0.36808 | 0.28105 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | Existing | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.49429 | 0.038858 | 0.57201 | Cap-Tons/1000 sf | 715.5 | 1192.5 | 895 | 0.18119 | 0.30199 | 0.22289 | 0 | 0 | 0 | 715.5 | 1192.5 | 895 | 0.18119 | 0.30199 | 0.22289 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EUN | EDUCATION - UNIVERSITY | Existing | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.51877 | 0.037811 | 0.55658 | Cap-Tons/1000 sf | 829.65 | 1382.75 | 1059.15 | 0.15915 | 0.26524 | 0.19045 | 0 | 0 | 0 | 829.65 | 1382.75 | 1059.15 | 0.15915 | 0.26524 | 0.19045 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | GRO | GROCERY | Existing | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.86635 | 0.063144 | 0.92949 | Cap-Tons/1000 sf | 959.55 | 1599.25 | 1300.05 | 0.28037 | 0.46729 | 0.32922 | 0 | 0 | 0 | 959.55 | 1599.25 | 1300.05 | 0.28037 | 0.46729 | 0.32922 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | Existing | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.71085 | 0.055883 | 0.82262 | Cap-Tons/1000 sf | 1440.45 | 2400.75 | 1836.45 | 0.24321 | 0.40535 | 0.28471 | 0 | 0 | 0 | 1440.45 | 2400.75 | 1836.45 | 0.24321 | 0.40535 | 0.28471 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HTL | LODGING - HOTEL | Existing | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.4087 | 0.029788 | 0.43849 | Cap-Tons/1000 sf | 1365.15 | 2275.25 | 1739.65 | 0.27982 | 0.46636 | 0.32072 | 0 | 0 | 0 | 1365.15 | 2275.25 | 1739.65 | 0.27982 | 0.46636 | 0.32072 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | MTL | LODGING - MOTEL | Existing | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.4087 | 0.029788 | 0.43849 | Cap-Tons/1000 sf | 1365.15 | 2275.25 | 1739.65 | 0.27982 | 0.46636 | 0.32072 | 0 | 0 | 0 | 1365.15 | 2275.25 | 1739.65 | 0.27982 | 0.46636 | 0.32072 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | Existing | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.76674 | 0.055883 | 0.82262 | Cap-Tons/1000 sf | 1120.2 | 1867 | 1505.2 | 0.23657 | 0.39429 | 0.27862 | 0 | 0 | 0 | 1120.2 | 1867 | 1505.2 | 0.23657 | 0.39429 | 0.27862 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFL | OFFICE - LARGE | Existing | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.54446 | 0.039683 | 0.58414 | Cap-Tons/1000 sf | 861.336 | 1435.5599 | 1031.736 | 0.24502 | 0.40836 | 0.28392 | 0 | 0 | 0 | 861.336 | 1435.5599 | 1031.736 | 0.24502 | 0.40836 | 0.28392 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFS | OFFICE - SMALL | Existing | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.59035 | 0.04641 | 0.68317 | Cap-Tons/1000 sf | 701.1 | 1168.5 | 861.75 | 0.22273 | 0.37122 | 0.26053 | 0 | 0 | 0 | 701.1 | 1168.5 | 861.75 | 0.22273 | 0.37122 | 0.26053 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | Existing | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 1.0264 | 0.080693 | 1.1878 | Cap-Tons/1000 sf | 1102.95 | 1838.25 | 1432.95 | 0.29099 | 0.48498 | 0.33004 | 0 | 0 | 0 | 1102.95 | 1838.25 | 1432.95 | 0.29099 | 0.48498 | 0.33004 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | Existing | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.67965 | 0.05343 | 0.78651 | Cap-Tons/1000 sf | 927.1865 | 1545.3109 | 1161.6865 | 0.32128 | 0.53547 | 0.35818 | 0 | 0 | 0 | 927.1865 | 1545.3109 | 1161.6865 | 0.32128 | 0.53547 | 0.35818 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | Existing | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.34638 | 0.025246 | 0.37163 | Cap-Tons/1000 sf | 860.55 | 1434.25 | 1074.05 | 0.28064 | 0.46773 | 0.31969 | 0 | 0 | 0 | 860.55 | 1434.25 | 1074.05 | 0.28064 | 0.46773 | 0.31969 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | Existing | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.34652 | 0.027242 | 0.40101 | Cap-Tons/1000 sf | 912 | 1520 | 1168.5 | 0.27752 | 0.46254 | 0.32012 | 0 | 0 | 0 | 912 | 1520 | 1168.5 | 0.27752 | 0.46254 | 0.32012 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTS | RETAIL - SMALL | Existing | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.39888 | 0.031358 | 0.46159 | Cap-Tons/1000 sf | 821.55 | 1369.25 | 1030.55 | 0.28122 | 0.46869 | 0.32232 | 0 | 0 | 0 | 821.55 | 1369.25 | 1030.55 | 0.28122 | 0.46869 | 0.32232 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | SCN | STORAGE - CONDITIONED | Existing | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.22128 | 0.017396 | 0.25607 | Cap-Tons/1000 sf | 617.1 | 1028.5 | 820.1 | 0.25029 | 0.41715 | 0.29119 | 0 | 0 | 0 | 617.1 | 1028.5 | 820.1 | 0.25029 | 0.41715 | 0.29119 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ASM | ASSEMBLY | New | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.83582 | 0.065708 | 0.96724 | Cap-Tons/1000 sf | 1121 | 1348.5 | 1348.5 | 0.36785 | 0.4353 | 0.4353 | 0 | 0 | 0 | 1121 | 1348.5 | 1348.5 | 0.36785 | 0.4353 | 0.4353 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | New | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.4818 | 0.037877 | 0.55756 | Cap-Tons/1000 sf | 979 | 1177 | 1177 | 0.35012 | 0.41117 | 0.41117 | 0 | 0 | 0 | 979 | 1177 | 1177 | 0.35012 | 0.41117 | 0.41117 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | New | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.51248 | 0.040289 | 0.59306 | Cap-Tons/1000 sf | 851.8 | 996.25 | 996.25 | 0.24896 | 0.29221 | 0.29221 | 0 | 0 | 0 | 851.8 | 996.25 | 996.25 | 0.24896 | 0.29221 | 0.29221 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | New | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.6128 | 0.048175 | 0.70915 | Cap-Tons/1000 sf | 986.5 | 1244 | 1244 | 0.28464 | 0.35884 | 0.35884 | 0 | 0 | 0 | 986.5 | 1244 | 1244 | 0.28464 | 0.35884 | 0.35884 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | New | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.49429 | 0.038858 | 0.57201 | Cap-Tons/1000 sf | 1034 | 1192.5 | 1192.5 | 0.22578 | 0.26148 | 0.26148 | 0 | 0 | 0 | 1034 | 1192.5 | 1192.5 | 0.22578 | 0.26148 | 0.26148 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EUN | EDUCATION - UNIVERSITY | New | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.51877 | 0.037811 | 0.55658 | Cap-Tons/1000 sf | 1161.25 | 1382.75 | 1382.75 | 0.36728 | 0.42903 | 0.42903 | 0 | 0 | 0 | 1161.25 | 1382.75 | 1382.75 | 0.36728 | 0.42903 | 0.42903 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | GRO | GROCERY | New | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.86635 | 0.063144 | 0.92949 | Cap-Tons/1000 sf | 1258.25 | 1599.25 | 1599.25 | 0.19987 | 0.25742 | 0.25742 | 0 | 0 | 0 | 1258.25 | 1599.25 | 1599.25 | 0.19987 | 0.25742 | 0.25742 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | New | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.71085 | 0.055883 | 0.82262 | Cap-Tons/1000 sf | 1999.25 | 2400.75 | 2400.75 | 0.23912 | 0.28677 | 0.28677 | 0 | 0 | 0 | 1999.25 | 2400.75 | 2400.75 | 0.23912 | 0.28677 | 0.28677 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HTL | LODGING - HOTEL | New | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.4087 | 0.029788 | 0.43849 | Cap-Tons/1000 sf | 1905.25 | 2275.25 | 2275.25 | 0.29822 | 0.35207 | 0.35207 | 0 | 0 | 0 | 1905.25 | 2275.25 | 2275.25 | 0.29822 | 0.35207 | 0.35207 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | MTL | LODGING - MOTEL | New | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.4087 | 0.029788 | 0.43849 | Cap-Tons/1000 sf | 1905.25 | 2275.25 | 2275.25 | 0.29822 | 0.35207 | 0.35207 | 0 | 0 | 0 | 1905.25 | 2275.25 | 2275.25 | 0.29822 | 0.35207 | 0.35207 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | New | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.76674 | 0.055883 | 0.82262 | Cap-Tons/1000 sf | 1481.5 | 1867 | 1867 | 0.18217 | 0.23217 | 0.23217 | 0 | 0 | 0 | 1481.5 | 1867 | 1867 | 0.18217 | 0.23217 | 0.23217 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFL | OFFICE - LARGE | New | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.54446 | 0.039683 | 0.58414 | Cap-Tons/1000 sf | 1277.6599 | 1435.5599 | 1435.5599 | 0.51592 | 0.56862 | 0.56862 | 0 | 0 | 0 | 1277.6599 | 1435.5599 | 1435.5599 | 0.51592 | 0.56862 | 0.56862 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFS | OFFICE - SMALL | New | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.59035 | 0.04641 | 0.68317 | Cap-Tons/1000 sf | 1013.45 | 1168.5 | 1168.5 | 0.38371 | 0.43321 | 0.43321 | 0 | 0 | 0 | 1013.45 | 1168.5 | 1168.5 | 0.38371 | 0.43321 | 0.43321 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | New | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 1.0264 | 0.080693 | 1.1878 | Cap-Tons/1000 sf | 1493.75 | 1838.25 | 1838.25 | 0.29828 | 0.36528 | 0.36528 | 0 | 0 | 0 | 1493.75 | 1838.25 | 1838.25 | 0.29828 | 0.36528 | 0.36528 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | New | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.67965 | 0.05343 | 0.78651 | Cap-Tons/1000 sf | 1292.3109 | 1545.3109 | 1545.3109 | 0.39811 | 0.47231 | 0.47231 | 0 | 0 | 0 | 1292.3109 | 1545.3109 | 1545.3109 | 0.39811 | 0.47231 | 0.47231 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | New | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.34638 | 0.025246 | 0.37163 | Cap-Tons/1000 sf | 1212.25 | 1434.25 | 1434.25 | 0.34664 | 0.40589 | 0.40589 | 0 | 0 | 0 | 1212.25 | 1434.25 | 1434.25 | 0.34664 | 0.40589 | 0.40589 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | New | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.34652 | 0.027242 | 0.40101 | Cap-Tons/1000 sf | 1261.5 | 1520 | 1520 | 0.33555 | 0.39985 | 0.39985 | 0 | 0 | 0 | 1261.5 | 1520 | 1520 | 0.33555 | 0.39985 | 0.39985 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTS | RETAIL - SMALL | New | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.39888 | 0.031358 | 0.46159 | Cap-Tons/1000 sf | 1151.25 | 1369.25 | 1369.25 | 0.39532 | 0.46287 | 0.46287 | 0 | 0 | 0 | 1151.25 | 1369.25 | 1369.25 | 0.39532 | 0.46287 | 0.46287 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | SCN | STORAGE - CONDITIONED | New | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.22128 | 0.017396 | 0.25607 | Cap-Tons/1000 sf | 825 | 1028.5 | 1028.5 | 0.201 | 0.2516 | 0.2516 | 0 | 0 | 0 | 825 | 1028.5 | 1028.5 | 0.201 | 0.2516 | 0.2516 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ASM | ASSEMBLY | Existing | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.83582 | 0.065708 | 0.96724 | Cap-Tons/1000 sf | 809.1 | 1348.5 | 1029.1 | 0.28625 | 0.47708 | 0.3189 | 0 | 0 | 0 | 809.1 | 1348.5 | 1029.1 | 0.28625 | 0.47708 | 0.3189 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | Existing | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.4818 | 0.037877 | 0.55756 | Cap-Tons/1000 sf | 706.2 | 1177 | 907.7 | 0.24945 | 0.41576 | 0.2851 | 0 | 0 | 0 | 706.2 | 1177 | 907.7 | 0.24945 | 0.41576 | 0.2851 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | Existing | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.51248 | 0.040289 | 0.59306 | Cap-Tons/1000 sf | 597.75 | 996.25 | 740.1 | 0.14182 | 0.23636 | 0.17357 | 0 | 0 | 0 | 597.75 | 996.25 | 740.1 | 0.14182 | 0.23636 | 0.17357 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | Existing | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.6128 | 0.048175 | 0.70915 | Cap-Tons/1000 sf | 746.4 | 1244 | 1032.4 | 0.24907 | 0.41512 | 0.30727 | 0 | 0 | 0 | 746.4 | 1244 | 1032.4 | 0.24907 | 0.41512 | 0.30727 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | Existing | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.49429 | 0.038858 | 0.57201 | Cap-Tons/1000 sf | 721 | 1192.5 | 874.75 | 0.1257 | 0.20784 | 0.1491 | 0 | 0 | 0 | 721 | 1192.5 | 874.75 | 0.1257 | 0.20784 | 0.1491 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EUN | EDUCATION - UNIVERSITY | Existing | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.51877 | 0.037811 | 0.55658 | Cap-Tons/1000 sf | 829.65 | 1382.75 | 1051.15 | 0.26058 | 0.4343 | 0.29888 | 0 | 0 | 0 | 829.65 | 1382.75 | 1051.15 | 0.26058 | 0.4343 | 0.29888 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | GRO | GROCERY | Existing | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.86635 | 0.063144 | 0.92949 | Cap-Tons/1000 sf | 959.55 | 1599.25 | 1300.55 | 0.29342 | 0.48903 | 0.34272 | 0 | 0 | 0 | 959.55 | 1599.25 | 1300.55 | 0.29342 | 0.48903 | 0.34272 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | Existing | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.71085 | 0.055883 | 0.82262 | Cap-Tons/1000 sf | 1440.45 | 2400.75 | 1831.95 | 0.25403 | 0.42339 | 0.29578 | 0 | 0 | 0 | 1440.45 | 2400.75 | 1831.95 | 0.25403 | 0.42339 | 0.29578 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HTL | LODGING - HOTEL | Existing | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.4087 | 0.029788 | 0.43849 | Cap-Tons/1000 sf | 1365.15 | 2275.25 | 1736.65 | 0.2819 | 0.46984 | 0.322 | 0 | 0 | 0 | 1365.15 | 2275.25 | 1736.65 | 0.2819 | 0.46984 | 0.322 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFS | OFFICE - SMALL | Existing | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.59035 | 0.04641 | 0.68317 | Cap-Tons/1000 sf | 701.1 | 1168.5 | 855.05 | 0.28545 | 0.47575 | 0.3289 | 0 | 0 | 0 | 701.1 | 1168.5 | 855.05 | 0.28545 | 0.47575 | 0.3289 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | Existing | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 1.0264 | 0.080693 | 1.1878 | Cap-Tons/1000 sf | 1102.95 | 1838.25 | 1430.95 | 0.30266 | 0.50444 | 0.34296 | 0 | 0 | 0 | 1102.95 | 1838.25 | 1430.95 | 0.30266 | 0.50444 | 0.34296 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | Existing | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.67965 | 0.05343 | 0.78651 | Cap-Tons/1000 sf | 927.1865 | 1545.3109 | 1161.6865 | 0.3499 | 0.58317 | 0.38335 | 0 | 0 | 0 | 927.1865 | 1545.3109 | 1161.6865 | 0.3499 | 0.58317 | 0.38335 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | Existing | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.34638 | 0.025246 | 0.37163 | Cap-Tons/1000 sf | 860.55 | 1434.25 | 1074.55 | 0.2747 | 0.45784 | 0.31425 | 0 | 0 | 0 | 860.55 | 1434.25 | 1074.55 | 0.2747 | 0.45784 | 0.31425 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | Existing | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.34652 | 0.027242 | 0.40101 | Cap-Tons/1000 sf | 912 | 1520 | 1167.5 | 0.28759 | 0.47932 | 0.33119 | 0 | 0 | 0 | 912 | 1520 | 1167.5 | 0.28759 | 0.47932 | 0.33119 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTS | RETAIL - SMALL | Existing | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.39888 | 0.031358 | 0.46159 | Cap-Tons/1000 sf | 821.55 | 1369.25 | 1030.05 | 0.28378 | 0.47297 | 0.32358 | 0 | 0 | 0 | 821.55 | 1369.25 | 1030.05 | 0.28378 | 0.47297 | 0.32358 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.4818 | 0.037877 | 0.55756 | Cap-Tons/1000 sf | 706.2 | 1177 | 917.7 | 0.13341 | 0.22235 | 0.17826 | 0 | 0 | 0 | 706.2 | 1177 | 917.7 | 0.13341 | 0.22235 | 0.17826 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.51248 | 0.040289 | 0.59306 | Cap-Tons/1000 sf | 597.75 | 996.25 | 756.25 | 0.17206 | 0.28677 | 0.21666 | 0 | 0 | 0 | 597.75 | 996.25 | 756.25 | 0.17206 | 0.28677 | 0.21666 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.6128 | 0.048175 | 0.70915 | Cap-Tons/1000 sf | 746.4 | 1244 | 1047.4 | 0.24091 | 0.40151 | 0.30141 | 0 | 0 | 0 | 746.4 | 1244 | 1047.4 | 0.24091 | 0.40151 | 0.30141 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | SCN | STORAGE - CONDITIONED | Existing | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.22128 | 0.017396 | 0.25607 | Cap-Tons/1000 sf | 617.1 | 1028.5 | 819.6 | 0.27061 | 0.45102 | 0.31451 | 0 | 0 | 0 | 617.1 | 1028.5 | 819.6 | 0.27061 | 0.45102 | 0.31451 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ASM | ASSEMBLY | New | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.83582 | 0.065708 | 0.96724 | Cap-Tons/1000 sf | 1110.5 | 1348.5 | 1348.5 | 0.12005 | 0.14965 | 0.14965 | 0 | 0 | 0 | 1110.5 | 1348.5 | 1348.5 | 0.12005 | 0.14965 | 0.14965 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | New | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.4818 | 0.037877 | 0.55756 | Cap-Tons/1000 sf | 977.5 | 1177 | 1177 | 0.12678 | 0.15373 | 0.15373 | 0 | 0 | 0 | 977.5 | 1177 | 1177 | 0.12678 | 0.15373 | 0.15373 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | New | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.51248 | 0.040289 | 0.59306 | Cap-Tons/1000 sf | 863.2 | 996.25 | 996.25 | 0.061861 | 0.071496 | 0.071496 | 0 | 0 | 0 | 863.2 | 996.25 | 996.25 | 0.061861 | 0.071496 | 0.071496 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | New | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.6128 | 0.048175 | 0.70915 | Cap-Tons/1000 sf | 1022.5 | 1244 | 1244 | 0.23592 | 0.28692 | 0.28692 | 0 | 0 | 0 | 1022.5 | 1244 | 1244 | 0.23592 | 0.28692 | 0.28692 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | New | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.49429 | 0.038858 | 0.57201 | Cap-Tons/1000 sf | 1042.5 | 1192.5 | 1192.5 | 0.052194 | 0.059914 | 0.059914 | 0 | 0 | 0 | 1042.5 | 1192.5 | 1192.5 | 0.052194 | 0.059914 | 0.059914 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EUN | EDUCATION - UNIVERSITY | New | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.51877 | 0.037811 | 0.55658 | Cap-Tons/1000 sf | 1162.75 | 1382.75 | 1382.75 | 0.19571 | 0.23061 | 0.23061 | 0 | 0 | 0 | 1162.75 | 1382.75 | 1382.75 | 0.19571 | 0.23061 | 0.23061 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | GRO | GROCERY | New | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.86635 | 0.063144 | 0.92949 | Cap-Tons/1000 sf | 1253.75 | 1599.25 | 1599.25 | 0.18469 | 0.23884 | 0.23884 | 0 | 0 | 0 | 1253.75 | 1599.25 | 1599.25 | 0.18469 | 0.23884 | 0.23884 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | New | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.71085 | 0.055883 | 0.82262 | Cap-Tons/1000 sf | 1996.25 | 2400.75 | 2400.75 | 0.23672 | 0.28037 | 0.28037 | 0 | 0 | 0 | 1996.25 | 2400.75 | 2400.75 | 0.23672 | 0.28037 | 0.28037 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HTL | LODGING - HOTEL | New | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.4087 | 0.029788 | 0.43849 | Cap-Tons/1000 sf | 1902.75 | 2275.25 | 2275.25 | 0.22718 | 0.26873 | 0.26873 | 0 | 0 | 0 | 1902.75 | 2275.25 | 2275.25 | 0.22718 | 0.26873 | 0.26873 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | MTL | LODGING - MOTEL | New | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.4087 | 0.029788 | 0.43849 | Cap-Tons/1000 sf | 1902.75 | 2275.25 | 2275.25 | 0.22718 | 0.26873 | 0.26873 | 0 | 0 | 0 | 1902.75 | 2275.25 | 2275.25 | 0.22718 | 0.26873 | 0.26873 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | New | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.76674 | 0.055883 | 0.82262 | Cap-Tons/1000 sf | 1481.5 | 1867 | 1867 | 0.18531 | 0.23031 | 0.23031 | 0 | 0 | 0 | 1481.5 | 1867 | 1867 | 0.18531 | 0.23031 | 0.23031 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFL | OFFICE - LARGE | New | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.54446 | 0.039683 | 0.58414 | Cap-Tons/1000 sf | 1281.0599 | 1435.5599 | 1435.5599 | 0.38657 | 0.42567 | 0.42567 | 0 | 0 | 0 | 1281.0599 | 1435.5599 | 1435.5599 | 0.38657 | 0.42567 | 0.42567 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFS | OFFICE - SMALL | New | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.59035 | 0.04641 | 0.68317 | Cap-Tons/1000 sf | 1014.8 | 1168.5 | 1168.5 | 0.29708 | 0.33673 | 0.33673 | 0 | 0 | 0 | 1014.8 | 1168.5 | 1168.5 | 0.29708 | 0.33673 | 0.33673 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | New | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.34652 | 0.027242 | 0.40101 | Cap-Tons/1000 sf | 1254.5 | 1520 | 1520 | 0.19844 | 0.23899 | 0.23899 | 0 | 0 | 0 | 1254.5 | 1520 | 1520 | 0.19844 | 0.23899 | 0.23899 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTS | RETAIL - SMALL | New | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.39888 | 0.031358 | 0.46159 | Cap-Tons/1000 sf | 1152.75 | 1369.25 | 1369.25 | 0.2354 | 0.27715 | 0.27715 | 0 | 0 | 0 | 1152.75 | 1369.25 | 1369.25 | 0.2354 | 0.27715 | 0.27715 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | SCN | STORAGE - CONDITIONED | New | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.22128 | 0.017396 | 0.25607 | Cap-Tons/1000 sf | 821.5 | 1028.5 | 1028.5 | 0.16687 | 0.20777 | 0.20777 | 0 | 0 | 0 | 821.5 | 1028.5 | 1028.5 | 0.16687 | 0.20777 | 0.20777 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ASM | ASSEMBLY | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.83582 | 0.065708 | 0.96724 | Cap-Tons/1000 sf | 809.1 | 1348.5 | 1026.6 | 0.27813 | 0.46355 | 0.30953 | 0 | 0 | 0 | 809.1 | 1348.5 | 1026.6 | 0.27813 | 0.46355 | 0.30953 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.49429 | 0.038858 | 0.57201 | Cap-Tons/1000 sf | 715.5 | 1192.5 | 895 | 0.18281 | 0.30468 | 0.22616 | 0 | 0 | 0 | 715.5 | 1192.5 | 895 | 0.18281 | 0.30468 | 0.22616 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EUN | EDUCATION - UNIVERSITY | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.51877 | 0.037811 | 0.55658 | Cap-Tons/1000 sf | 829.65 | 1382.75 | 1057.65 | 0.12397 | 0.20662 | 0.16052 | 0 | 0 | 0 | 829.65 | 1382.75 | 1057.65 | 0.12397 | 0.20662 | 0.16052 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | GRO | GROCERY | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.86635 | 0.063144 | 0.92949 | Cap-Tons/1000 sf | 959.55 | 1599.25 | 1298.55 | 0.2768 | 0.46133 | 0.3262 | 0 | 0 | 0 | 959.55 | 1599.25 | 1298.55 | 0.2768 | 0.46133 | 0.3262 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.71085 | 0.055883 | 0.82262 | Cap-Tons/1000 sf | 1440.45 | 2400.75 | 1838.45 | 0.23884 | 0.39807 | 0.27894 | 0 | 0 | 0 | 1440.45 | 2400.75 | 1838.45 | 0.23884 | 0.39807 | 0.27894 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HTL | LODGING - HOTEL | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.4087 | 0.029788 | 0.43849 | Cap-Tons/1000 sf | 1365.15 | 2275.25 | 1739.65 | 0.27305 | 0.45509 | 0.3117 | 0 | 0 | 0 | 1365.15 | 2275.25 | 1739.65 | 0.27305 | 0.45509 | 0.3117 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | MTL | LODGING - MOTEL | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.4087 | 0.029788 | 0.43849 | Cap-Tons/1000 sf | 1365.15 | 2275.25 | 1739.65 | 0.27305 | 0.45509 | 0.3117 | 0 | 0 | 0 | 1365.15 | 2275.25 | 1739.65 | 0.27305 | 0.45509 | 0.3117 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | GRO | GROCERY | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.86635 | 0.063144 | 0.92949 | Cap-Tons/1000 sf | 978.55 | 1599.25 | 1331.05 | 0.33646 | 0.54967 | 0.38731 | 0 | 0 | 0 | 978.55 | 1599.25 | 1331.05 | 0.33646 | 0.54967 | 0.38731 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.71085 | 0.055883 | 0.82262 | Cap-Tons/1000 sf | 1440.45 | 2400.75 | 1834.95 | 0.28136 | 0.46893 | 0.33106 | 0 | 0 | 0 | 1440.45 | 2400.75 | 1834.95 | 0.28136 | 0.46893 | 0.33106 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HTL | LODGING - HOTEL | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.4087 | 0.029788 | 0.43849 | Cap-Tons/1000 sf | 1365.15 | 2275.25 | 1733.65 | 0.3298 | 0.54966 | 0.38525 | 0 | 0 | 0 | 1365.15 | 2275.25 | 1733.65 | 0.3298 | 0.54966 | 0.38525 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.76674 | 0.055883 | 0.82262 | Cap-Tons/1000 sf | 1120.2 | 1867 | 1505.2 | 0.23607 | 0.39345 | 0.27637 | 0 | 0 | 0 | 1120.2 | 1867 | 1505.2 | 0.23607 | 0.39345 | 0.27637 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFL | OFFICE - LARGE | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.54446 | 0.039683 | 0.58414 | Cap-Tons/1000 sf | 861.336 | 1435.5599 | 1027.886 | 0.2503 | 0.41717 | 0.288 | 0 | 0 | 0 | 861.336 | 1435.5599 | 1027.886 | 0.2503 | 0.41717 | 0.288 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFS | OFFICE - SMALL | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.59035 | 0.04641 | 0.68317 | Cap-Tons/1000 sf | 701.1 | 1168.5 | 860.5 | 0.23038 | 0.38397 | 0.26933 | 0 | 0 | 0 | 701.1 | 1168.5 | 860.5 | 0.23038 | 0.38397 | 0.26933 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 1.0264 | 0.080693 | 1.1878 | Cap-Tons/1000 sf | 1102.95 | 1838.25 | 1428.45 | 0.28627 | 0.47712 | 0.32242 | 0 | 0 | 0 | 1102.95 | 1838.25 | 1428.45 | 0.28627 | 0.47712 | 0.32242 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.67965 | 0.05343 | 0.78651 | Cap-Tons/1000 sf | 927.1865 | 1545.3109 | 1156.6865 | 0.32157 | 0.53595 | 0.35337 | 0 | 0 | 0 | 927.1865 | 1545.3109 | 1156.6865 | 0.32157 | 0.53595 | 0.35337 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.34638 | 0.025246 | 0.37163 | Cap-Tons/1000 sf | 860.55 | 1434.25 | 1072.05 | 0.26583 | 0.44305 | 0.29763 | 0 | 0 | 0 | 860.55 | 1434.25 | 1072.05 | 0.26583 | 0.44305 | 0.29763 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.34652 | 0.027242 | 0.40101 | Cap-Tons/1000 sf | 912 | 1520 | 1166.5 | 0.26748 | 0.44581 | 0.30803 | 0 | 0 | 0 | 912 | 1520 | 1166.5 | 0.26748 | 0.44581 | 0.30803 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTS | RETAIL - SMALL | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.39888 | 0.031358 | 0.46159 | Cap-Tons/1000 sf | 821.55 | 1369.25 | 1028.05 | 0.26911 | 0.44851 | 0.30431 | 0 | 0 | 0 | 821.55 | 1369.25 | 1028.05 | 0.26911 | 0.44851 | 0.30431 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | SCN | STORAGE - CONDITIONED | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.22128 | 0.017396 | 0.25607 | Cap-Tons/1000 sf | 617.1 | 1028.5 | 818.6 | 0.24659 | 0.41098 | 0.28439 | 0 | 0 | 0 | 617.1 | 1028.5 | 818.6 | 0.24659 | 0.41098 | 0.28439 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ASM | ASSEMBLY | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.83582 | 0.065708 | 0.96724 | Cap-Tons/1000 sf | 1114 | 1348.5 | 1348.5 | 0.11182 | 0.13797 | 0.13797 | 0 | 0 | 0 | 1114 | 1348.5 | 1348.5 | 0.11182 | 0.13797 | 0.13797 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.4818 | 0.037877 | 0.55756 | Cap-Tons/1000 sf | 979 | 1177 | 1177 | 0.099029 | 0.12068 | 0.12068 | 0 | 0 | 0 | 979 | 1177 | 1177 | 0.099029 | 0.12068 | 0.12068 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.51248 | 0.040289 | 0.59306 | Cap-Tons/1000 sf | 847.75 | 996.25 | 996.25 | 0.23974 | 0.28349 | 0.28349 | 0 | 0 | 0 | 847.75 | 996.25 | 996.25 | 0.23974 | 0.28349 | 0.28349 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.6128 | 0.048175 | 0.70915 | Cap-Tons/1000 sf | 989 | 1244 | 1244 | 0.23422 | 0.29452 | 0.29452 | 0 | 0 | 0 | 989 | 1244 | 1244 | 0.23422 | 0.29452 | 0.29452 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.49429 | 0.038858 | 0.57201 | Cap-Tons/1000 sf | 1028 | 1192.5 | 1192.5 | 0.19487 | 0.22662 | 0.22662 | 0 | 0 | 0 | 1028 | 1192.5 | 1192.5 | 0.19487 | 0.22662 | 0.22662 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EUN | EDUCATION - UNIVERSITY | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.51877 | 0.037811 | 0.55658 | Cap-Tons/1000 sf | 1159.25 | 1382.75 | 1382.75 | 0.19883 | 0.23543 | 0.23543 | 0 | 0 | 0 | 1159.25 | 1382.75 | 1382.75 | 0.19883 | 0.23543 | 0.23543 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | GRO | GROCERY | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.86635 | 0.063144 | 0.92949 | Cap-Tons/1000 sf | 1256.25 | 1599.25 | 1599.25 | 0.18386 | 0.23721 | 0.23721 | 0 | 0 | 0 | 1256.25 | 1599.25 | 1599.25 | 0.18386 | 0.23721 | 0.23721 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.71085 | 0.055883 | 0.82262 | Cap-Tons/1000 sf | 1994.25 | 2400.75 | 2400.75 | 0.23033 | 0.27358 | 0.27358 | 0 | 0 | 0 | 1994.25 | 2400.75 | 2400.75 | 0.23033 | 0.27358 | 0.27358 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HTL | LODGING - HOTEL | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.4087 | 0.029788 | 0.43849 | Cap-Tons/1000 sf | 1903.25 | 2275.25 | 2275.25 | 0.23419 | 0.27629 | 0.27629 | 0 | 0 | 0 | 1903.25 | 2275.25 | 2275.25 | 0.23419 | 0.27629 | 0.27629 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | MTL | LODGING - MOTEL | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.4087 | 0.029788 | 0.43849 | Cap-Tons/1000 sf | 1903.25 | 2275.25 | 2275.25 | 0.23419 | 0.27629 | 0.27629 | 0 | 0 | 0 | 1903.25 | 2275.25 | 2275.25 | 0.23419 | 0.27629 | 0.27629 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.76674 | 0.055883 | 0.82262 | Cap-Tons/1000 sf | 1478.5 | 1867 | 1867 | 0.18436 | 0.22936 | 0.22936 | 0 | 0 | 0 | 1478.5 | 1867 | 1867 | 0.18436 | 0.22936 | 0.22936 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFL | OFFICE - LARGE | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.54446 | 0.039683 | 0.58414 | Cap-Tons/1000 sf | 1279.0099 | 1435.5599 | 1435.5599 | 0.3696 | 0.409 | 0.409 | 0 | 0 | 0 | 1279.0099 | 1435.5599 | 1435.5599 | 0.3696 | 0.409 | 0.409 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFS | OFFICE - SMALL | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.59035 | 0.04641 | 0.68317 | Cap-Tons/1000 sf | 1013 | 1168.5 | 1168.5 | 0.31747 | 0.35982 | 0.35982 | 0 | 0 | 0 | 1013 | 1168.5 | 1168.5 | 0.31747 | 0.35982 | 0.35982 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 1.0264 | 0.080693 | 1.1878 | Cap-Tons/1000 sf | 1490.75 | 1838.25 | 1838.25 | 0.14443 | 0.17873 | 0.17873 | 0 | 0 | 0 | 1490.75 | 1838.25 | 1838.25 | 0.14443 | 0.17873 | 0.17873 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.67965 | 0.05343 | 0.78651 | Cap-Tons/1000 sf | 1298.8109 | 1545.3109 | 1545.3109 | 0.14493 | 0.17408 | 0.17408 | 0 | 0 | 0 | 1298.8109 | 1545.3109 | 1545.3109 | 0.14493 | 0.17408 | 0.17408 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.34638 | 0.025246 | 0.37163 | Cap-Tons/1000 sf | 1215.25 | 1434.25 | 1434.25 | 0.20963 | 0.24653 | 0.24653 | 0 | 0 | 0 | 1215.25 | 1434.25 | 1434.25 | 0.20963 | 0.24653 | 0.24653 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.34652 | 0.027242 | 0.40101 | Cap-Tons/1000 sf | 1260.5 | 1520 | 1520 | 0.18914 | 0.22684 | 0.22684 | 0 | 0 | 0 | 1260.5 | 1520 | 1520 | 0.18914 | 0.22684 | 0.22684 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTS | RETAIL - SMALL | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.39888 | 0.031358 | 0.46159 | Cap-Tons/1000 sf | 1156.25 | 1369.25 | 1369.25 | 0.24144 | 0.28289 | 0.28289 | 0 | 0 | 0 | 1156.25 | 1369.25 | 1369.25 | 0.24144 | 0.28289 | 0.28289 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | SCN | STORAGE - CONDITIONED | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.22128 | 0.017396 | 0.25607 | Cap-Tons/1000 sf | 823 | 1028.5 | 1028.5 | 0.16205 | 0.2012 | 0.2012 | 0 | 0 | 0 | 823 | 1028.5 | 1028.5 | 0.16205 | 0.2012 | 0.2012 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ASM | ASSEMBLY | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.83582 | 0.065708 | 0.96724 | Cap-Tons/1000 sf | 809.1 | 1348.5 | 1041.6 | 0.37057 | 0.61762 | 0.43322 | 0 | 0 | 0 | 809.1 | 1348.5 | 1041.6 | 0.37057 | 0.61762 | 0.43322 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.4818 | 0.037877 | 0.55756 | Cap-Tons/1000 sf | 706.2 | 1177 | 930.7 | 0.22178 | 0.36963 | 0.26298 | 0 | 0 | 0 | 706.2 | 1177 | 930.7 | 0.22178 | 0.36963 | 0.26298 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.51248 | 0.040289 | 0.59306 | Cap-Tons/1000 sf | 617.45 | 996.25 | 769.25 | 0.12346 | 0.19884 | 0.14411 | 0 | 0 | 0 | 617.45 | 996.25 | 769.25 | 0.12346 | 0.19884 | 0.14411 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.6128 | 0.048175 | 0.70915 | Cap-Tons/1000 sf | 746.4 | 1244 | 1062.4 | 0.28401 | 0.47335 | 0.35191 | 0 | 0 | 0 | 746.4 | 1244 | 1062.4 | 0.28401 | 0.47335 | 0.35191 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.49429 | 0.038858 | 0.57201 | Cap-Tons/1000 sf | 762.5 | 1192.5 | 927 | 0.13801 | 0.21524 | 0.15796 | 0 | 0 | 0 | 762.5 | 1192.5 | 927 | 0.13801 | 0.21524 | 0.15796 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EUN | EDUCATION - UNIVERSITY | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.51877 | 0.037811 | 0.55658 | Cap-Tons/1000 sf | 829.65 | 1382.75 | 1069.65 | 0.25091 | 0.41818 | 0.29776 | 0 | 0 | 0 | 829.65 | 1382.75 | 1069.65 | 0.25091 | 0.41818 | 0.29776 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | MTL | LODGING - MOTEL | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.4087 | 0.029788 | 0.43849 | Cap-Tons/1000 sf | 1365.15 | 2275.25 | 1733.65 | 0.3298 | 0.54966 | 0.38525 | 0 | 0 | 0 | 1365.15 | 2275.25 | 1733.65 | 0.3298 | 0.54966 | 0.38525 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.76674 | 0.055883 | 0.82262 | Cap-Tons/1000 sf | 1120.2 | 1867 | 1503.7 | 0.29607 | 0.49345 | 0.34657 | 0 | 0 | 0 | 1120.2 | 1867 | 1503.7 | 0.29607 | 0.49345 | 0.34657 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFL | OFFICE - LARGE | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.54446 | 0.039683 | 0.58414 | Cap-Tons/1000 sf | 861.336 | 1435.5599 | 1042.336 | 0.32522 | 0.54204 | 0.37662 | 0 | 0 | 0 | 861.336 | 1435.5599 | 1042.336 | 0.32522 | 0.54204 | 0.37662 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFS | OFFICE - SMALL | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.59035 | 0.04641 | 0.68317 | Cap-Tons/1000 sf | 701.1 | 1168.5 | 863.25 | 0.30506 | 0.50843 | 0.35701 | 0 | 0 | 0 | 701.1 | 1168.5 | 863.25 | 0.30506 | 0.50843 | 0.35701 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 1.0264 | 0.080693 | 1.1878 | Cap-Tons/1000 sf | 1102.95 | 1838.25 | 1451.45 | 0.36925 | 0.61542 | 0.42615 | 0 | 0 | 0 | 1102.95 | 1838.25 | 1451.45 | 0.36925 | 0.61542 | 0.42615 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.67965 | 0.05343 | 0.78651 | Cap-Tons/1000 sf | 927.1865 | 1545.3109 | 1173.6865 | 0.47641 | 0.79402 | 0.54431 | 0 | 0 | 0 | 927.1865 | 1545.3109 | 1173.6865 | 0.47641 | 0.79402 | 0.54431 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.34638 | 0.025246 | 0.37163 | Cap-Tons/1000 sf | 860.55 | 1434.25 | 1084.55 | 0.3758 | 0.62633 | 0.42705 | 0 | 0 | 0 | 860.55 | 1434.25 | 1084.55 | 0.3758 | 0.62633 | 0.42705 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.34652 | 0.027242 | 0.40101 | Cap-Tons/1000 sf | 912 | 1520 | 1170 | 0.38422 | 0.64036 | 0.44407 | 0 | 0 | 0 | 912 | 1520 | 1170 | 0.38422 | 0.64036 | 0.44407 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTS | RETAIL - SMALL | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.39888 | 0.031358 | 0.46159 | Cap-Tons/1000 sf | 821.55 | 1369.25 | 1044.05 | 0.36978 | 0.6163 | 0.42508 | 0 | 0 | 0 | 821.55 | 1369.25 | 1044.05 | 0.36978 | 0.6163 | 0.42508 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | SCN | STORAGE - CONDITIONED | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.22128 | 0.017396 | 0.25607 | Cap-Tons/1000 sf | 622 | 1028.5 | 846 | 0.31231 | 0.5161 | 0.36591 | 0 | 0 | 0 | 622 | 1028.5 | 846 | 0.31231 | 0.5161 | 0.36591 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ASM | ASSEMBLY | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.83582 | 0.065708 | 0.96724 | Cap-Tons/1000 sf | 1115 | 1348.5 | 1348.5 | 0.34371 | 0.40741 | 0.40741 | 0 | 0 | 0 | 1115 | 1348.5 | 1348.5 | 0.34371 | 0.40741 | 0.40741 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.4818 | 0.037877 | 0.55756 | Cap-Tons/1000 sf | 967 | 1177 | 1177 | 0.21929 | 0.26269 | 0.26269 | 0 | 0 | 0 | 967 | 1177 | 1177 | 0.21929 | 0.26269 | 0.26269 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.51248 | 0.040289 | 0.59306 | Cap-Tons/1000 sf | 856.9 | 996.25 | 996.25 | 0 | 0 | 0 | 0 | 0 | 0 | 856.9 | 996.25 | 996.25 | 0 | 0 | 0 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.6128 | 0.048175 | 0.70915 | Cap-Tons/1000 sf | 990.5 | 1244 | 1244 | 0.16824 | 0.21124 | 0.21124 | 0 | 0 | 0 | 990.5 | 1244 | 1244 | 0.16824 | 0.21124 | 0.21124 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.49429 | 0.038858 | 0.57201 | Cap-Tons/1000 sf | 1041.5 | 1192.5 | 1192.5 | 0 | 0 | 0 | 0 | 0 | 0 | 1041.5 | 1192.5 | 1192.5 | 0 | 0 | 0 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EUN | EDUCATION - UNIVERSITY | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.51877 | 0.037811 | 0.55658 | Cap-Tons/1000 sf | 1159.25 | 1382.75 | 1382.75 | 0.23499 | 0.27574 | 0.27574 | 0 | 0 | 0 | 1159.25 | 1382.75 | 1382.75 | 0.23499 | 0.27574 | 0.27574 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | GRO | GROCERY | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.86635 | 0.063144 | 0.92949 | Cap-Tons/1000 sf | 1247.25 | 1599.25 | 1599.25 | 0.17771 | 0.23116 | 0.23116 | 0 | 0 | 0 | 1247.25 | 1599.25 | 1599.25 | 0.17771 | 0.23116 | 0.23116 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.71085 | 0.055883 | 0.82262 | Cap-Tons/1000 sf | 2004.25 | 2400.75 | 2400.75 | 0.2377 | 0.28465 | 0.28465 | 0 | 0 | 0 | 2004.25 | 2400.75 | 2400.75 | 0.2377 | 0.28465 | 0.28465 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HTL | LODGING - HOTEL | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.4087 | 0.029788 | 0.43849 | Cap-Tons/1000 sf | 1917.75 | 2275.25 | 2275.25 | 0.28874 | 0.33924 | 0.33924 | 0 | 0 | 0 | 1917.75 | 2275.25 | 2275.25 | 0.28874 | 0.33924 | 0.33924 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | MTL | LODGING - MOTEL | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.4087 | 0.029788 | 0.43849 | Cap-Tons/1000 sf | 1917.75 | 2275.25 | 2275.25 | 0.28874 | 0.33924 | 0.33924 | 0 | 0 | 0 | 1917.75 | 2275.25 | 2275.25 | 0.28874 | 0.33924 | 0.33924 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.76674 | 0.055883 | 0.82262 | Cap-Tons/1000 sf | 1484 | 1867 | 1867 | 0.17439 | 0.21969 | 0.21969 | 0 | 0 | 0 | 1484 | 1867 | 1867 | 0.17439 | 0.21969 | 0.21969 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFL | OFFICE - LARGE | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.54446 | 0.039683 | 0.58414 | Cap-Tons/1000 sf | 1274.7099 | 1435.5599 | 1435.5599 | 0.46424 | 0.51664 | 0.51664 | 0 | 0 | 0 | 1274.7099 | 1435.5599 | 1435.5599 | 0.46424 | 0.51664 | 0.51664 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFS | OFFICE - SMALL | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.59035 | 0.04641 | 0.68317 | Cap-Tons/1000 sf | 1012.65 | 1168.5 | 1168.5 | 0.34998 | 0.40053 | 0.40053 | 0 | 0 | 0 | 1012.65 | 1168.5 | 1168.5 | 0.34998 | 0.40053 | 0.40053 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 1.0264 | 0.080693 | 1.1878 | Cap-Tons/1000 sf | 1482.75 | 1838.25 | 1838.25 | 0.21259 | 0.26304 | 0.26304 | 0 | 0 | 0 | 1482.75 | 1838.25 | 1838.25 | 0.21259 | 0.26304 | 0.26304 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.67965 | 0.05343 | 0.78651 | Cap-Tons/1000 sf | 1305.3109 | 1545.3109 | 1545.3109 | 0.35952 | 0.42447 | 0.42447 | 0 | 0 | 0 | 1305.3109 | 1545.3109 | 1545.3109 | 0.35952 | 0.42447 | 0.42447 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.34638 | 0.025246 | 0.37163 | Cap-Tons/1000 sf | 1207.25 | 1434.25 | 1434.25 | 0.21897 | 0.25672 | 0.25672 | 0 | 0 | 0 | 1207.25 | 1434.25 | 1434.25 | 0.21897 | 0.25672 | 0.25672 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.34652 | 0.027242 | 0.40101 | Cap-Tons/1000 sf | 1257.5 | 1520 | 1520 | 0.23638 | 0.28363 | 0.28363 | 0 | 0 | 0 | 1257.5 | 1520 | 1520 | 0.23638 | 0.28363 | 0.28363 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.54701 | 0.037166 | 0.62134 | Cap-Tons/1000 sf | 706.2 | 1177 | 887.75 | 0.26282 | 0.43804 | 0.30752 | 0 | 0 | 0 | 706.2 | 1177 | 887.75 | 0.26282 | 0.43804 | 0.30752 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.621 | 0.042193 | 0.70538 | Cap-Tons/1000 sf | 602.95 | 996.25 | 724.1 | 0.32976 | 0.54453 | 0.37531 | 0 | 0 | 0 | 602.95 | 996.25 | 724.1 | 0.32976 | 0.54453 | 0.37531 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.79463 | 0.050555 | 0.84519 | Cap-Tons/1000 sf | 746.4 | 1244 | 1018.9 | 0.24168 | 0.4028 | 0.27933 | 0 | 0 | 0 | 746.4 | 1244 | 1018.9 | 0.24168 | 0.4028 | 0.27933 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.61214 | 0.041591 | 0.69532 | Cap-Tons/1000 sf | 762.5 | 1192.5 | 890 | 0.46208 | 0.71883 | 0.51018 | 0 | 0 | 0 | 762.5 | 1192.5 | 890 | 0.46208 | 0.71883 | 0.51018 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EUN | EDUCATION - UNIVERSITY | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.58484 | 0.037208 | 0.62204 | Cap-Tons/1000 sf | 829.65 | 1382.75 | 1039.3 | 0.26981 | 0.44968 | 0.31831 | 0 | 0 | 0 | 829.65 | 1382.75 | 1039.3 | 0.26981 | 0.44968 | 0.31831 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | GRO | GROCERY | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 1.0397 | 0.066148 | 1.1059 | Cap-Tons/1000 sf | 1013.25 | 1599.25 | 1366.75 | 0.30831 | 0.48981 | 0.35611 | 0 | 0 | 0 | 1013.25 | 1599.25 | 1366.75 | 0.30831 | 0.48981 | 0.35611 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.77621 | 0.052738 | 0.88169 | Cap-Tons/1000 sf | 1440.45 | 2400.75 | 1824.45 | 0.24276 | 0.40461 | 0.28971 | 0 | 0 | 0 | 1440.45 | 2400.75 | 1824.45 | 0.24276 | 0.40461 | 0.28971 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HTL | LODGING - HOTEL | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.46549 | 0.029615 | 0.49511 | Cap-Tons/1000 sf | 1365.15 | 2275.25 | 1730.65 | 0.2755 | 0.45917 | 0.3256 | 0 | 0 | 0 | 1365.15 | 2275.25 | 1730.65 | 0.2755 | 0.45917 | 0.3256 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | MTL | LODGING - MOTEL | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.46549 | 0.029615 | 0.49511 | Cap-Tons/1000 sf | 1365.15 | 2275.25 | 1730.65 | 0.2755 | 0.45917 | 0.3256 | 0 | 0 | 0 | 1365.15 | 2275.25 | 1730.65 | 0.2755 | 0.45917 | 0.3256 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.82895 | 0.052738 | 0.88169 | Cap-Tons/1000 sf | 1120.2 | 1867 | 1489.7 | 0.26021 | 0.43369 | 0.30711 | 0 | 0 | 0 | 1120.2 | 1867 | 1489.7 | 0.26021 | 0.43369 | 0.30711 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFL | OFFICE - LARGE | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.61708 | 0.039259 | 0.65634 | Cap-Tons/1000 sf | 861.336 | 1435.5599 | 1020.636 | 0.2805 | 0.46749 | 0.3299 | 0 | 0 | 0 | 861.336 | 1435.5599 | 1020.636 | 0.2805 | 0.46749 | 0.3299 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFS | OFFICE - SMALL | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.65556 | 0.044541 | 0.74464 | Cap-Tons/1000 sf | 701.1 | 1168.5 | 851.65 | 0.25947 | 0.43246 | 0.30867 | 0 | 0 | 0 | 701.1 | 1168.5 | 851.65 | 0.25947 | 0.43246 | 0.30867 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 1.143 | 0.077662 | 1.2984 | Cap-Tons/1000 sf | 1102.95 | 1838.25 | 1425.45 | 0.27702 | 0.46171 | 0.32332 | 0 | 0 | 0 | 1102.95 | 1838.25 | 1425.45 | 0.27702 | 0.46171 | 0.32332 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.77022 | 0.052331 | 0.87488 | Cap-Tons/1000 sf | 973.2487 | 1545.3109 | 1194.2487 | 0.31675 | 0.50048 | 0.3584 | 0 | 0 | 0 | 973.2487 | 1545.3109 | 1194.2487 | 0.31675 | 0.50048 | 0.3584 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.37551 | 0.02389 | 0.3994 | Cap-Tons/1000 sf | 860.55 | 1434.25 | 1074.5 | 0.30837 | 0.51395 | 0.35927 | 0 | 0 | 0 | 860.55 | 1434.25 | 1074.5 | 0.30837 | 0.51395 | 0.35927 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.40936 | 0.027814 | 0.46499 | Cap-Tons/1000 sf | 912 | 1520 | 1152.5 | 0.31188 | 0.51981 | 0.36813 | 0 | 0 | 0 | 912 | 1520 | 1152.5 | 0.31188 | 0.51981 | 0.36813 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTS | RETAIL - SMALL | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.45321 | 0.030792 | 0.51479 | Cap-Tons/1000 sf | 821.55 | 1369.25 | 1034.55 | 0.29458 | 0.49096 | 0.34498 | 0 | 0 | 0 | 821.55 | 1369.25 | 1034.55 | 0.29458 | 0.49096 | 0.34498 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | SCN | STORAGE - CONDITIONED | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.24791 | 0.016844 | 0.2816 | Cap-Tons/1000 sf | 673 | 1028.5 | 863 | 0.18349 | 0.2801 | 0.22629 | 0 | 0 | 0 | 673 | 1028.5 | 863 | 0.18349 | 0.2801 | 0.22629 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ASM | ASSEMBLY | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.93897 | 0.063797 | 1.0666 | Cap-Tons/1000 sf | 1188.45 | 1348.5 | 1348.5 | 0.52549 | 0.57679 | 0.57679 | 0 | 0 | 0 | 1188.45 | 1348.5 | 1348.5 | 0.52549 | 0.57679 | 0.57679 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.54701 | 0.037166 | 0.62134 | Cap-Tons/1000 sf | 989.5 | 1177 | 1177 | 0.322 | 0.37345 | 0.37345 | 0 | 0 | 0 | 989.5 | 1177 | 1177 | 0.322 | 0.37345 | 0.37345 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.621 | 0.042193 | 0.70538 | Cap-Tons/1000 sf | 873.45 | 996.25 | 996.25 | 0.39759 | 0.44749 | 0.44749 | 0 | 0 | 0 | 873.45 | 996.25 | 996.25 | 0.39759 | 0.44749 | 0.44749 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.79463 | 0.050555 | 0.84519 | Cap-Tons/1000 sf | 1063.5 | 1244 | 1244 | 0.24183 | 0.28263 | 0.28263 | 0 | 0 | 0 | 1063.5 | 1244 | 1244 | 0.24183 | 0.28263 | 0.28263 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.61214 | 0.041591 | 0.69532 | Cap-Tons/1000 sf | 1066.6 | 1192.5 | 1192.5 | 0.46856 | 0.51851 | 0.51851 | 0 | 0 | 0 | 1066.6 | 1192.5 | 1192.5 | 0.46856 | 0.51851 | 0.51851 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EUN | EDUCATION - UNIVERSITY | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.58484 | 0.037208 | 0.62204 | Cap-Tons/1000 sf | 1178.55 | 1382.75 | 1382.75 | 0.45568 | 0.50878 | 0.50878 | 0 | 0 | 0 | 1178.55 | 1382.75 | 1382.75 | 0.45568 | 0.50878 | 0.50878 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | GRO | GROCERY | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 1.0397 | 0.066148 | 1.1059 | Cap-Tons/1000 sf | 1250.75 | 1599.25 | 1599.25 | 0.17986 | 0.23391 | 0.23391 | 0 | 0 | 0 | 1250.75 | 1599.25 | 1599.25 | 0.17986 | 0.23391 | 0.23391 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.77621 | 0.052738 | 0.88169 | Cap-Tons/1000 sf | 2013.75 | 2400.75 | 2400.75 | 0.27622 | 0.32512 | 0.32512 | 0 | 0 | 0 | 2013.75 | 2400.75 | 2400.75 | 0.27622 | 0.32512 | 0.32512 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HTL | LODGING - HOTEL | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.46549 | 0.029615 | 0.49511 | Cap-Tons/1000 sf | 1927.25 | 2275.25 | 2275.25 | 0.31601 | 0.36706 | 0.36706 | 0 | 0 | 0 | 1927.25 | 2275.25 | 2275.25 | 0.31601 | 0.36706 | 0.36706 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | MTL | LODGING - MOTEL | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.46549 | 0.029615 | 0.49511 | Cap-Tons/1000 sf | 1927.25 | 2275.25 | 2275.25 | 0.31601 | 0.36706 | 0.36706 | 0 | 0 | 0 | 1927.25 | 2275.25 | 2275.25 | 0.31601 | 0.36706 | 0.36706 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.82895 | 0.052738 | 0.88169 | Cap-Tons/1000 sf | 1501.5 | 1867 | 1867 | 0.19782 | 0.24487 | 0.24487 | 0 | 0 | 0 | 1501.5 | 1867 | 1867 | 0.19782 | 0.24487 | 0.24487 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFL | OFFICE - LARGE | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.61708 | 0.039259 | 0.65634 | Cap-Tons/1000 sf | 1283.9099 | 1435.5599 | 1435.5599 | 0.57036 | 0.62036 | 0.62036 | 0 | 0 | 0 | 1283.9099 | 1435.5599 | 1435.5599 | 0.57036 | 0.62036 | 0.62036 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFS | OFFICE - SMALL | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.65556 | 0.044541 | 0.74464 | Cap-Tons/1000 sf | 1019.1 | 1168.5 | 1168.5 | 0.43325 | 0.4862 | 0.4862 | 0 | 0 | 0 | 1019.1 | 1168.5 | 1168.5 | 0.43325 | 0.4862 | 0.4862 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 1.143 | 0.077662 | 1.2984 | Cap-Tons/1000 sf | 1509.25 | 1838.25 | 1838.25 | 0.24163 | 0.29288 | 0.29288 | 0 | 0 | 0 | 1509.25 | 1838.25 | 1838.25 | 0.24163 | 0.29288 | 0.29288 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.77022 | 0.052331 | 0.87488 | Cap-Tons/1000 sf | 1348.3109 | 1545.3109 | 1545.3109 | 0.39378 | 0.44393 | 0.44393 | 0 | 0 | 0 | 1348.3109 | 1545.3109 | 1545.3109 | 0.39378 | 0.44393 | 0.44393 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.37551 | 0.02389 | 0.3994 | Cap-Tons/1000 sf | 1226.65 | 1434.25 | 1434.25 | 0.36708 | 0.41588 | 0.41588 | 0 | 0 | 0 | 1226.65 | 1434.25 | 1434.25 | 0.36708 | 0.41588 | 0.41588 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.40936 | 0.027814 | 0.46499 | Cap-Tons/1000 sf | 1283.5 | 1520 | 1520 | 0.40148 | 0.45943 | 0.45943 | 0 | 0 | 0 | 1283.5 | 1520 | 1520 | 0.40148 | 0.45943 | 0.45943 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTS | RETAIL - SMALL | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.45321 | 0.030792 | 0.51479 | Cap-Tons/1000 sf | 1159.75 | 1369.25 | 1369.25 | 0.32984 | 0.38139 | 0.38139 | 0 | 0 | 0 | 1159.75 | 1369.25 | 1369.25 | 0.32984 | 0.38139 | 0.38139 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | SCN | STORAGE - CONDITIONED | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.24791 | 0.016844 | 0.2816 | Cap-Tons/1000 sf | 838 | 1028.5 | 1028.5 | 0.21404 | 0.26464 | 0.26464 | 0 | 0 | 0 | 838 | 1028.5 | 1028.5 | 0.21404 | 0.26464 | 0.26464 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ASM | ASSEMBLY | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.93897 | 0.063797 | 1.0666 | Cap-Tons/1000 sf | 809.1 | 1348.5 | 1028.1 | 0.26181 | 0.43634 | 0.31036 | 0 | 0 | 0 | 809.1 | 1348.5 | 1028.1 | 0.26181 | 0.43634 | 0.31036 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.54701 | 0.037166 | 0.62134 | Cap-Tons/1000 sf | 706.2 | 1177 | 891.4 | 0.16449 | 0.27416 | 0.20139 | 0 | 0 | 0 | 706.2 | 1177 | 891.4 | 0.16449 | 0.27416 | 0.20139 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.621 | 0.042193 | 0.70538 | Cap-Tons/1000 sf | 597.75 | 996.25 | 722.5 | 0.041867 | 0.069778 | 0.051917 | 0 | 0 | 0 | 597.75 | 996.25 | 722.5 | 0.041867 | 0.069778 | 0.051917 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.79463 | 0.050555 | 0.84519 | Cap-Tons/1000 sf | 746.4 | 1244 | 975.9 | 0.18875 | 0.31458 | 0.24605 | 0 | 0 | 0 | 746.4 | 1244 | 975.9 | 0.18875 | 0.31458 | 0.24605 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.61214 | 0.041591 | 0.69532 | Cap-Tons/1000 sf | 725.5 | 1192.5 | 858.5 | 0.024121 | 0.039621 | 0.028721 | 0 | 0 | 0 | 725.5 | 1192.5 | 858.5 | 0.024121 | 0.039621 | 0.028721 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EUN | EDUCATION - UNIVERSITY | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.58484 | 0.037208 | 0.62204 | Cap-Tons/1000 sf | 829.65 | 1382.75 | 1050.15 | 0.17408 | 0.29013 | 0.21608 | 0 | 0 | 0 | 829.65 | 1382.75 | 1050.15 | 0.17408 | 0.29013 | 0.21608 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | GRO | GROCERY | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 1.0397 | 0.066148 | 1.1059 | Cap-Tons/1000 sf | 959.55 | 1599.25 | 1300.55 | 0.28157 | 0.46928 | 0.33022 | 0 | 0 | 0 | 959.55 | 1599.25 | 1300.55 | 0.28157 | 0.46928 | 0.33022 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.77621 | 0.052738 | 0.88169 | Cap-Tons/1000 sf | 1440.45 | 2400.75 | 1836.45 | 0.21709 | 0.36181 | 0.26569 | 0 | 0 | 0 | 1440.45 | 2400.75 | 1836.45 | 0.21709 | 0.36181 | 0.26569 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HTL | LODGING - HOTEL | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.46549 | 0.029615 | 0.49511 | Cap-Tons/1000 sf | 1365.15 | 2275.25 | 1748.15 | 0.24203 | 0.40338 | 0.29423 | 0 | 0 | 0 | 1365.15 | 2275.25 | 1748.15 | 0.24203 | 0.40338 | 0.29423 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | MTL | LODGING - MOTEL | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.46549 | 0.029615 | 0.49511 | Cap-Tons/1000 sf | 1365.15 | 2275.25 | 1748.15 | 0.24203 | 0.40338 | 0.29423 | 0 | 0 | 0 | 1365.15 | 2275.25 | 1748.15 | 0.24203 | 0.40338 | 0.29423 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.82895 | 0.052738 | 0.88169 | Cap-Tons/1000 sf | 1120.2 | 1867 | 1501.2 | 0.2229 | 0.37149 | 0.27305 | 0 | 0 | 0 | 1120.2 | 1867 | 1501.2 | 0.2229 | 0.37149 | 0.27305 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFL | OFFICE - LARGE | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.61708 | 0.039259 | 0.65634 | Cap-Tons/1000 sf | 861.336 | 1435.5599 | 1024.586 | 0.26952 | 0.4492 | 0.32042 | 0 | 0 | 0 | 861.336 | 1435.5599 | 1024.586 | 0.26952 | 0.4492 | 0.32042 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFS | OFFICE - SMALL | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.65556 | 0.044541 | 0.74464 | Cap-Tons/1000 sf | 701.1 | 1168.5 | 857.65 | 0.24216 | 0.40361 | 0.29386 | 0 | 0 | 0 | 701.1 | 1168.5 | 857.65 | 0.24216 | 0.40361 | 0.29386 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 1.143 | 0.077662 | 1.2984 | Cap-Tons/1000 sf | 1102.95 | 1838.25 | 1435.95 | 0.24973 | 0.41622 | 0.30068 | 0 | 0 | 0 | 1102.95 | 1838.25 | 1435.95 | 0.24973 | 0.41622 | 0.30068 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.77022 | 0.052331 | 0.87488 | Cap-Tons/1000 sf | 927.1865 | 1545.3109 | 1155.1865 | 0.30397 | 0.50661 | 0.35437 | 0 | 0 | 0 | 927.1865 | 1545.3109 | 1155.1865 | 0.30397 | 0.50661 | 0.35437 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.37551 | 0.02389 | 0.3994 | Cap-Tons/1000 sf | 860.55 | 1434.25 | 1086.05 | 0.2414 | 0.40233 | 0.2926 | 0 | 0 | 0 | 860.55 | 1434.25 | 1086.05 | 0.2414 | 0.40233 | 0.2926 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.40936 | 0.027814 | 0.46499 | Cap-Tons/1000 sf | 912 | 1520 | 1179.5 | 0.24133 | 0.40222 | 0.29288 | 0 | 0 | 0 | 912 | 1520 | 1179.5 | 0.24133 | 0.40222 | 0.29288 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTS | RETAIL - SMALL | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.45321 | 0.030792 | 0.51479 | Cap-Tons/1000 sf | 821.55 | 1369.25 | 1042.55 | 0.24365 | 0.40608 | 0.2957 | 0 | 0 | 0 | 821.55 | 1369.25 | 1042.55 | 0.24365 | 0.40608 | 0.2957 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | SCN | STORAGE - CONDITIONED | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.24791 | 0.016844 | 0.2816 | Cap-Tons/1000 sf | 621 | 1028.5 | 819.5 | 0.28057 | 0.46434 | 0.33162 | 0 | 0 | 0 | 621 | 1028.5 | 819.5 | 0.28057 | 0.46434 | 0.33162 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ASM | ASSEMBLY | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.93897 | 0.063797 | 1.0666 | Cap-Tons/1000 sf | 1130.5 | 1348.5 | 1348.5 | 0.3048 | 0.3527 | 0.3527 | 0 | 0 | 0 | 1130.5 | 1348.5 | 1348.5 | 0.3048 | 0.3527 | 0.3527 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.54701 | 0.037166 | 0.62134 | Cap-Tons/1000 sf | 987.5 | 1177 | 1177 | 0.25815 | 0.303 | 0.303 | 0 | 0 | 0 | 987.5 | 1177 | 1177 | 0.25815 | 0.303 | 0.303 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.621 | 0.042193 | 0.70538 | Cap-Tons/1000 sf | 868.8 | 996.25 | 996.25 | 0.35093 | 0.39883 | 0.39883 | 0 | 0 | 0 | 868.8 | 996.25 | 996.25 | 0.35093 | 0.39883 | 0.39883 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.79463 | 0.050555 | 0.84519 | Cap-Tons/1000 sf | 1072 | 1244 | 1244 | 0.35249 | 0.40859 | 0.40859 | 0 | 0 | 0 | 1072 | 1244 | 1244 | 0.35249 | 0.40859 | 0.40859 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.61214 | 0.041591 | 0.69532 | Cap-Tons/1000 sf | 1057 | 1192.5 | 1192.5 | 0.40567 | 0.45417 | 0.45417 | 0 | 0 | 0 | 1057 | 1192.5 | 1192.5 | 0.40567 | 0.45417 | 0.45417 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EUN | EDUCATION - UNIVERSITY | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.58484 | 0.037208 | 0.62204 | Cap-Tons/1000 sf | 1170.75 | 1382.75 | 1382.75 | 0.35189 | 0.40089 | 0.40089 | 0 | 0 | 0 | 1170.75 | 1382.75 | 1382.75 | 0.35189 | 0.40089 | 0.40089 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | GRO | GROCERY | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 1.0397 | 0.066148 | 1.1059 | Cap-Tons/1000 sf | 1266.75 | 1599.25 | 1599.25 | 0.19598 | 0.25108 | 0.25108 | 0 | 0 | 0 | 1266.75 | 1599.25 | 1599.25 | 0.19598 | 0.25108 | 0.25108 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.77621 | 0.052738 | 0.88169 | Cap-Tons/1000 sf | 1999.75 | 2400.75 | 2400.75 | 0.25512 | 0.30107 | 0.30107 | 0 | 0 | 0 | 1999.75 | 2400.75 | 2400.75 | 0.25512 | 0.30107 | 0.30107 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HTL | LODGING - HOTEL | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.46549 | 0.029615 | 0.49511 | Cap-Tons/1000 sf | 1894.75 | 2275.25 | 2275.25 | 0.2816 | 0.32975 | 0.32975 | 0 | 0 | 0 | 1894.75 | 2275.25 | 2275.25 | 0.2816 | 0.32975 | 0.32975 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | MTL | LODGING - MOTEL | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.46549 | 0.029615 | 0.49511 | Cap-Tons/1000 sf | 1894.75 | 2275.25 | 2275.25 | 0.2816 | 0.32975 | 0.32975 | 0 | 0 | 0 | 1894.75 | 2275.25 | 2275.25 | 0.2816 | 0.32975 | 0.32975 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.82895 | 0.052738 | 0.88169 | Cap-Tons/1000 sf | 1487 | 1867 | 1867 | 0.2017 | 0.24985 | 0.24985 | 0 | 0 | 0 | 1487 | 1867 | 1867 | 0.2017 | 0.24985 | 0.24985 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFL | OFFICE - LARGE | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.61708 | 0.039259 | 0.65634 | Cap-Tons/1000 sf | 1281.2099 | 1435.5599 | 1435.5599 | 0.53841 | 0.58751 | 0.58751 | 0 | 0 | 0 | 1281.2099 | 1435.5599 | 1435.5599 | 0.53841 | 0.58751 | 0.58751 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFS | OFFICE - SMALL | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.65556 | 0.044541 | 0.74464 | Cap-Tons/1000 sf | 1012.35 | 1168.5 | 1168.5 | 0.42986 | 0.48141 | 0.48141 | 0 | 0 | 0 | 1012.35 | 1168.5 | 1168.5 | 0.42986 | 0.48141 | 0.48141 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 1.143 | 0.077662 | 1.2984 | Cap-Tons/1000 sf | 1496.75 | 1838.25 | 1838.25 | 0.22205 | 0.271 | 0.271 | 0 | 0 | 0 | 1496.75 | 1838.25 | 1838.25 | 0.22205 | 0.271 | 0.271 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.77022 | 0.052331 | 0.87488 | Cap-Tons/1000 sf | 1313.8109 | 1545.3109 | 1545.3109 | 0.38381 | 0.43906 | 0.43906 | 0 | 0 | 0 | 1313.8109 | 1545.3109 | 1545.3109 | 0.38381 | 0.43906 | 0.43906 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.37551 | 0.02389 | 0.3994 | Cap-Tons/1000 sf | 1206.75 | 1434.25 | 1434.25 | 0.28707 | 0.33402 | 0.33402 | 0 | 0 | 0 | 1206.75 | 1434.25 | 1434.25 | 0.28707 | 0.33402 | 0.33402 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.40936 | 0.027814 | 0.46499 | Cap-Tons/1000 sf | 1253.5 | 1520 | 1520 | 0.24849 | 0.29684 | 0.29684 | 0 | 0 | 0 | 1253.5 | 1520 | 1520 | 0.24849 | 0.29684 | 0.29684 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTS | RETAIL - SMALL | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.45321 | 0.030792 | 0.51479 | Cap-Tons/1000 sf | 1148.25 | 1369.25 | 1369.25 | 0.3011 | 0.35085 | 0.35085 | 0 | 0 | 0 | 1148.25 | 1369.25 | 1369.25 | 0.3011 | 0.35085 | 0.35085 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | SCN | STORAGE - CONDITIONED | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.24791 | 0.016844 | 0.2816 | Cap-Tons/1000 sf | 828.5 | 1028.5 | 1028.5 | 0.20809 | 0.25624 | 0.25624 | 0 | 0 | 0 | 828.5 | 1028.5 | 1028.5 | 0.20809 | 0.25624 | 0.25624 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ASM | ASSEMBLY | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.93897 | 0.063797 | 1.0666 | Cap-Tons/1000 sf | 809.1 | 1348.5 | 1026.6 | 0.27402 | 0.4567 | 0.31467 | 0 | 0 | 0 | 809.1 | 1348.5 | 1026.6 | 0.27402 | 0.4567 | 0.31467 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.54701 | 0.037166 | 0.62134 | Cap-Tons/1000 sf | 706.2 | 1177 | 894.35 | 0.2513 | 0.41883 | 0.29085 | 0 | 0 | 0 | 706.2 | 1177 | 894.35 | 0.2513 | 0.41883 | 0.29085 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.621 | 0.042193 | 0.70538 | Cap-Tons/1000 sf | 597.75 | 996.25 | 728.6 | 0.34314 | 0.57191 | 0.38414 | 0 | 0 | 0 | 597.75 | 996.25 | 728.6 | 0.34314 | 0.57191 | 0.38414 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.79463 | 0.050555 | 0.84519 | Cap-Tons/1000 sf | 746.4 | 1244 | 987.4 | 0.36314 | 0.60523 | 0.41994 | 0 | 0 | 0 | 746.4 | 1244 | 987.4 | 0.36314 | 0.60523 | 0.41994 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.61214 | 0.041591 | 0.69532 | Cap-Tons/1000 sf | 715.5 | 1192.5 | 853.7 | 0.41792 | 0.69653 | 0.45997 | 0 | 0 | 0 | 715.5 | 1192.5 | 853.7 | 0.41792 | 0.69653 | 0.45997 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EUN | EDUCATION - UNIVERSITY | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.58484 | 0.037208 | 0.62204 | Cap-Tons/1000 sf | 829.65 | 1382.75 | 1052.15 | 0.25478 | 0.42464 | 0.29773 | 0 | 0 | 0 | 829.65 | 1382.75 | 1052.15 | 0.25478 | 0.42464 | 0.29773 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | GRO | GROCERY | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 1.0397 | 0.066148 | 1.1059 | Cap-Tons/1000 sf | 959.55 | 1599.25 | 1297.05 | 0.27973 | 0.46622 | 0.32873 | 0 | 0 | 0 | 959.55 | 1599.25 | 1297.05 | 0.27973 | 0.46622 | 0.32873 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.77621 | 0.052738 | 0.88169 | Cap-Tons/1000 sf | 1440.45 | 2400.75 | 1833.95 | 0.23254 | 0.38756 | 0.27564 | 0 | 0 | 0 | 1440.45 | 2400.75 | 1833.95 | 0.23254 | 0.38756 | 0.27564 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HTL | LODGING - HOTEL | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.46549 | 0.029615 | 0.49511 | Cap-Tons/1000 sf | 1365.15 | 2275.25 | 1748.65 | 0.24914 | 0.41524 | 0.29349 | 0 | 0 | 0 | 1365.15 | 2275.25 | 1748.65 | 0.24914 | 0.41524 | 0.29349 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | MTL | LODGING - MOTEL | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.46549 | 0.029615 | 0.49511 | Cap-Tons/1000 sf | 1365.15 | 2275.25 | 1748.65 | 0.24914 | 0.41524 | 0.29349 | 0 | 0 | 0 | 1365.15 | 2275.25 | 1748.65 | 0.24914 | 0.41524 | 0.29349 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.82895 | 0.052738 | 0.88169 | Cap-Tons/1000 sf | 1120.2 | 1867 | 1501.2 | 0.24103 | 0.40171 | 0.28668 | 0 | 0 | 0 | 1120.2 | 1867 | 1501.2 | 0.24103 | 0.40171 | 0.28668 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFL | OFFICE - LARGE | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.61708 | 0.039259 | 0.65634 | Cap-Tons/1000 sf | 861.336 | 1435.5599 | 1024.536 | 0.29815 | 0.49692 | 0.34375 | 0 | 0 | 0 | 861.336 | 1435.5599 | 1024.536 | 0.29815 | 0.49692 | 0.34375 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFS | OFFICE - SMALL | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.65556 | 0.044541 | 0.74464 | Cap-Tons/1000 sf | 701.1 | 1168.5 | 858.35 | 0.26223 | 0.43706 | 0.30988 | 0 | 0 | 0 | 701.1 | 1168.5 | 858.35 | 0.26223 | 0.43706 | 0.30988 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 1.143 | 0.077662 | 1.2984 | Cap-Tons/1000 sf | 1102.95 | 1838.25 | 1433.95 | 0.26562 | 0.44269 | 0.30687 | 0 | 0 | 0 | 1102.95 | 1838.25 | 1433.95 | 0.26562 | 0.44269 | 0.30687 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.77022 | 0.052331 | 0.87488 | Cap-Tons/1000 sf | 927.1865 | 1545.3109 | 1161.6865 | 0.30977 | 0.51628 | 0.35142 | 0 | 0 | 0 | 927.1865 | 1545.3109 | 1161.6865 | 0.30977 | 0.51628 | 0.35142 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.37551 | 0.02389 | 0.3994 | Cap-Tons/1000 sf | 860.55 | 1434.25 | 1083.55 | 0.24304 | 0.40507 | 0.28559 | 0 | 0 | 0 | 860.55 | 1434.25 | 1083.55 | 0.24304 | 0.40507 | 0.28559 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.40936 | 0.027814 | 0.46499 | Cap-Tons/1000 sf | 912 | 1520 | 1177.5 | 0.24736 | 0.41227 | 0.29126 | 0 | 0 | 0 | 912 | 1520 | 1177.5 | 0.24736 | 0.41227 | 0.29126 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTS | RETAIL - SMALL | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.45321 | 0.030792 | 0.51479 | Cap-Tons/1000 sf | 821.55 | 1369.25 | 1039.55 | 0.24676 | 0.41127 | 0.29056 | 0 | 0 | 0 | 821.55 | 1369.25 | 1039.55 | 0.24676 | 0.41127 | 0.29056 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | SCN | STORAGE - CONDITIONED | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.24791 | 0.016844 | 0.2816 | Cap-Tons/1000 sf | 617.1 | 1028.5 | 816.6 | 0.28885 | 0.48142 | 0.3339 | 0 | 0 | 0 | 617.1 | 1028.5 | 816.6 | 0.28885 | 0.48142 | 0.3339 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ASM | ASSEMBLY | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.93897 | 0.063797 | 1.0666 | Cap-Tons/1000 sf | 1120 | 1348.5 | 1348.5 | 0.35657 | 0.41327 | 0.41327 | 0 | 0 | 0 | 1120 | 1348.5 | 1348.5 | 0.35657 | 0.41327 | 0.41327 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.54701 | 0.037166 | 0.62134 | Cap-Tons/1000 sf | 991.5 | 1177 | 1177 | 0.22236 | 0.25991 | 0.25991 | 0 | 0 | 0 | 991.5 | 1177 | 1177 | 0.22236 | 0.25991 | 0.25991 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.621 | 0.042193 | 0.70538 | Cap-Tons/1000 sf | 866.45 | 996.25 | 996.25 | 0.30338 | 0.34653 | 0.34653 | 0 | 0 | 0 | 866.45 | 996.25 | 996.25 | 0.30338 | 0.34653 | 0.34653 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.79463 | 0.050555 | 0.84519 | Cap-Tons/1000 sf | 1071 | 1244 | 1244 | 0.32072 | 0.37222 | 0.37222 | 0 | 0 | 0 | 1071 | 1244 | 1244 | 0.32072 | 0.37222 | 0.37222 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.61214 | 0.041591 | 0.69532 | Cap-Tons/1000 sf | 1056.05 | 1192.5 | 1192.5 | 0.34256 | 0.38491 | 0.38491 | 0 | 0 | 0 | 1056.05 | 1192.5 | 1192.5 | 0.34256 | 0.38491 | 0.38491 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EUN | EDUCATION - UNIVERSITY | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.58484 | 0.037208 | 0.62204 | Cap-Tons/1000 sf | 1165.25 | 1382.75 | 1382.75 | 0.2705 | 0.3112 | 0.3112 | 0 | 0 | 0 | 1165.25 | 1382.75 | 1382.75 | 0.2705 | 0.3112 | 0.3112 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | MTL | LODGING - MOTEL | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.46549 | 0.029615 | 0.49511 | Cap-Tons/1000 sf | 1889.75 | 2275.25 | 2275.25 | 0.24957 | 0.29402 | 0.29402 | 0 | 0 | 0 | 1889.75 | 2275.25 | 2275.25 | 0.24957 | 0.29402 | 0.29402 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.82895 | 0.052738 | 0.88169 | Cap-Tons/1000 sf | 1482 | 1867 | 1867 | 0.18025 | 0.22325 | 0.22325 | 0 | 0 | 0 | 1482 | 1867 | 1867 | 0.18025 | 0.22325 | 0.22325 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFL | OFFICE - LARGE | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.61708 | 0.039259 | 0.65634 | Cap-Tons/1000 sf | 1282.8099 | 1435.5599 | 1435.5599 | 0.43919 | 0.48019 | 0.48019 | 0 | 0 | 0 | 1282.8099 | 1435.5599 | 1435.5599 | 0.43919 | 0.48019 | 0.48019 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFS | OFFICE - SMALL | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.65556 | 0.044541 | 0.74464 | Cap-Tons/1000 sf | 1011.6 | 1168.5 | 1168.5 | 0.36615 | 0.41215 | 0.41215 | 0 | 0 | 0 | 1011.6 | 1168.5 | 1168.5 | 0.36615 | 0.41215 | 0.41215 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 1.143 | 0.077662 | 1.2984 | Cap-Tons/1000 sf | 1491.75 | 1838.25 | 1838.25 | 0.20178 | 0.24748 | 0.24748 | 0 | 0 | 0 | 1491.75 | 1838.25 | 1838.25 | 0.20178 | 0.24748 | 0.24748 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTS | RETAIL - SMALL | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.45321 | 0.030792 | 0.51479 | Cap-Tons/1000 sf | 1147.75 | 1369.25 | 1369.25 | 0.20833 | 0.24473 | 0.24473 | 0 | 0 | 0 | 1147.75 | 1369.25 | 1369.25 | 0.20833 | 0.24473 | 0.24473 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | SCN | STORAGE - CONDITIONED | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.24791 | 0.016844 | 0.2816 | Cap-Tons/1000 sf | 826 | 1028.5 | 1028.5 | 0.17122 | 0.21172 | 0.21172 | 0 | 0 | 0 | 826 | 1028.5 | 1028.5 | 0.17122 | 0.21172 | 0.21172 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ASM | ASSEMBLY | Existing | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 0.93897 | 0.063797 | 1.0666 | Cap-Tons/1000 sf | 809.1 | 1348.5 | 1033.6 | 0.27779 | 0.46299 | 0.31004 | 0 | 0 | 0 | 809.1 | 1348.5 | 1033.6 | 0.27779 | 0.46299 | 0.31004 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | Existing | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 0.54701 | 0.037166 | 0.62134 | Cap-Tons/1000 sf | 706.2 | 1177 | 898.7 | 0.1879 | 0.31316 | 0.21595 | 0 | 0 | 0 | 706.2 | 1177 | 898.7 | 0.1879 | 0.31316 | 0.21595 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | Existing | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 0.621 | 0.042193 | 0.70538 | Cap-Tons/1000 sf | 597.75 | 996.25 | 731.9 | 0.14919 | 0.24866 | 0.18614 | 0 | 0 | 0 | 597.75 | 996.25 | 731.9 | 0.14919 | 0.24866 | 0.18614 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | Existing | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 0.79463 | 0.050555 | 0.84519 | Cap-Tons/1000 sf | 746.4 | 1244 | 1000.4 | 0.23583 | 0.39305 | 0.29653 | 0 | 0 | 0 | 746.4 | 1244 | 1000.4 | 0.23583 | 0.39305 | 0.29653 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | Existing | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 0.61214 | 0.041591 | 0.69532 | Cap-Tons/1000 sf | 715.5 | 1192.5 | 857.65 | 0.1496 | 0.24934 | 0.1809 | 0 | 0 | 0 | 715.5 | 1192.5 | 857.65 | 0.1496 | 0.24934 | 0.1809 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EUN | EDUCATION - UNIVERSITY | Existing | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 0.58484 | 0.037208 | 0.62204 | Cap-Tons/1000 sf | 829.65 | 1382.75 | 1053.15 | 0.20105 | 0.33509 | 0.23545 | 0 | 0 | 0 | 829.65 | 1382.75 | 1053.15 | 0.20105 | 0.33509 | 0.23545 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | GRO | GROCERY | Existing | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 1.0397 | 0.066148 | 1.1059 | Cap-Tons/1000 sf | 959.55 | 1599.25 | 1295.55 | 0.29855 | 0.49758 | 0.34705 | 0 | 0 | 0 | 959.55 | 1599.25 | 1295.55 | 0.29855 | 0.49758 | 0.34705 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | Existing | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 0.77621 | 0.052738 | 0.88169 | Cap-Tons/1000 sf | 1440.45 | 2400.75 | 1835.45 | 0.23883 | 0.39805 | 0.27943 | 0 | 0 | 0 | 1440.45 | 2400.75 | 1835.45 | 0.23883 | 0.39805 | 0.27943 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HTL | LODGING - HOTEL | Existing | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 0.46549 | 0.029615 | 0.49511 | Cap-Tons/1000 sf | 1365.15 | 2275.25 | 1748.15 | 0.25619 | 0.42699 | 0.29684 | 0 | 0 | 0 | 1365.15 | 2275.25 | 1748.15 | 0.25619 | 0.42699 | 0.29684 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | MTL | LODGING - MOTEL | Existing | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 0.46549 | 0.029615 | 0.49511 | Cap-Tons/1000 sf | 1365.15 | 2275.25 | 1748.15 | 0.25619 | 0.42699 | 0.29684 | 0 | 0 | 0 | 1365.15 | 2275.25 | 1748.15 | 0.25619 | 0.42699 | 0.29684 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | Existing | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 0.82895 | 0.052738 | 0.88169 | Cap-Tons/1000 sf | 1120.2 | 1867 | 1505.7 | 0.24326 | 0.40543 | 0.28496 | 0 | 0 | 0 | 1120.2 | 1867 | 1505.7 | 0.24326 | 0.40543 | 0.28496 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFL | OFFICE - LARGE | Existing | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 0.61708 | 0.039259 | 0.65634 | Cap-Tons/1000 sf | 861.336 | 1435.5599 | 1023.136 | 0.29277 | 0.48795 | 0.33412 | 0 | 0 | 0 | 861.336 | 1435.5599 | 1023.136 | 0.29277 | 0.48795 | 0.33412 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFS | OFFICE - SMALL | Existing | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 0.65556 | 0.044541 | 0.74464 | Cap-Tons/1000 sf | 701.1 | 1168.5 | 856.45 | 0.26437 | 0.44062 | 0.30652 | 0 | 0 | 0 | 701.1 | 1168.5 | 856.45 | 0.26437 | 0.44062 | 0.30652 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | Existing | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 1.143 | 0.077662 | 1.2984 | Cap-Tons/1000 sf | 1102.95 | 1838.25 | 1433.45 | 0.2728 | 0.45467 | 0.31015 | 0 | 0 | 0 | 1102.95 | 1838.25 | 1433.45 | 0.2728 | 0.45467 | 0.31015 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | Existing | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 0.77022 | 0.052331 | 0.87488 | Cap-Tons/1000 sf | 927.1865 | 1545.3109 | 1163.6865 | 0.31423 | 0.52372 | 0.34598 | 0 | 0 | 0 | 927.1865 | 1545.3109 | 1163.6865 | 0.31423 | 0.52372 | 0.34598 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | Existing | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 0.37551 | 0.02389 | 0.3994 | Cap-Tons/1000 sf | 860.55 | 1434.25 | 1080.05 | 0.25945 | 0.43241 | 0.29575 | 0 | 0 | 0 | 860.55 | 1434.25 | 1080.05 | 0.25945 | 0.43241 | 0.29575 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | Existing | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 0.40936 | 0.027814 | 0.46499 | Cap-Tons/1000 sf | 912 | 1520 | 1171 | 0.26101 | 0.43502 | 0.29796 | 0 | 0 | 0 | 912 | 1520 | 1171 | 0.26101 | 0.43502 | 0.29796 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTS | RETAIL - SMALL | Existing | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 0.45321 | 0.030792 | 0.51479 | Cap-Tons/1000 sf | 821.55 | 1369.25 | 1034.55 | 0.25864 | 0.43106 | 0.29654 | 0 | 0 | 0 | 821.55 | 1369.25 | 1034.55 | 0.25864 | 0.43106 | 0.29654 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | SCN | STORAGE - CONDITIONED | Existing | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 0.24791 | 0.016844 | 0.2816 | Cap-Tons/1000 sf | 617.1 | 1028.5 | 816.1 | 0.28563 | 0.47605 | 0.32438 | 0 | 0 | 0 | 617.1 | 1028.5 | 816.1 | 0.28563 | 0.47605 | 0.32438 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ASM | ASSEMBLY | New | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 0.93897 | 0.063797 | 1.0666 | Cap-Tons/1000 sf | 1109 | 1348.5 | 1348.5 | 0.12663 | 0.15508 | 0.15508 | 0 | 0 | 0 | 1109 | 1348.5 | 1348.5 | 0.12663 | 0.15508 | 0.15508 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | New | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 0.54701 | 0.037166 | 0.62134 | Cap-Tons/1000 sf | 989 | 1177 | 1177 | 0.17843 | 0.20963 | 0.20963 | 0 | 0 | 0 | 989 | 1177 | 1177 | 0.17843 | 0.20963 | 0.20963 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | New | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 0.621 | 0.042193 | 0.70538 | Cap-Tons/1000 sf | 867.95 | 996.25 | 996.25 | 0.20325 | 0.2333 | 0.2333 | 0 | 0 | 0 | 867.95 | 996.25 | 996.25 | 0.20325 | 0.2333 | 0.2333 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | New | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 0.79463 | 0.050555 | 0.84519 | Cap-Tons/1000 sf | 1062.5 | 1244 | 1244 | 0.28021 | 0.32791 | 0.32791 | 0 | 0 | 0 | 1062.5 | 1244 | 1244 | 0.28021 | 0.32791 | 0.32791 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | New | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 0.61214 | 0.041591 | 0.69532 | Cap-Tons/1000 sf | 1055.1 | 1192.5 | 1192.5 | 0.25074 | 0.28279 | 0.28279 | 0 | 0 | 0 | 1055.1 | 1192.5 | 1192.5 | 0.25074 | 0.28279 | 0.28279 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EUN | EDUCATION - UNIVERSITY | New | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 0.58484 | 0.037208 | 0.62204 | Cap-Tons/1000 sf | 1162.75 | 1382.75 | 1382.75 | 0.2205 | 0.25725 | 0.25725 | 0 | 0 | 0 | 1162.75 | 1382.75 | 1382.75 | 0.2205 | 0.25725 | 0.25725 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | GRO | GROCERY | New | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 1.0397 | 0.066148 | 1.1059 | Cap-Tons/1000 sf | 1263.75 | 1599.25 | 1599.25 | 0.17786 | 0.22831 | 0.22831 | 0 | 0 | 0 | 1263.75 | 1599.25 | 1599.25 | 0.17786 | 0.22831 | 0.22831 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | New | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 0.77621 | 0.052738 | 0.88169 | Cap-Tons/1000 sf | 1999.75 | 2400.75 | 2400.75 | 0.22558 | 0.26633 | 0.26633 | 0 | 0 | 0 | 1999.75 | 2400.75 | 2400.75 | 0.22558 | 0.26633 | 0.26633 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HTL | LODGING - HOTEL | New | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 0.46549 | 0.029615 | 0.49511 | Cap-Tons/1000 sf | 1890.25 | 2275.25 | 2275.25 | 0.23001 | 0.27176 | 0.27176 | 0 | 0 | 0 | 1890.25 | 2275.25 | 2275.25 | 0.23001 | 0.27176 | 0.27176 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | MTL | LODGING - MOTEL | New | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 0.46549 | 0.029615 | 0.49511 | Cap-Tons/1000 sf | 1890.25 | 2275.25 | 2275.25 | 0.23001 | 0.27176 | 0.27176 | 0 | 0 | 0 | 1890.25 | 2275.25 | 2275.25 | 0.23001 | 0.27176 | 0.27176 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | New | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 0.82895 | 0.052738 | 0.88169 | Cap-Tons/1000 sf | 1478 | 1867 | 1867 | 0.1698 | 0.21175 | 0.21175 | 0 | 0 | 0 | 1478 | 1867 | 1867 | 0.1698 | 0.21175 | 0.21175 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFL | OFFICE - LARGE | New | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 0.61708 | 0.039259 | 0.65634 | Cap-Tons/1000 sf | 1280.2599 | 1435.5599 | 1435.5599 | 0.39712 | 0.43702 | 0.43702 | 0 | 0 | 0 | 1280.2599 | 1435.5599 | 1435.5599 | 0.39712 | 0.43702 | 0.43702 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | New | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 0.37551 | 0.02389 | 0.3994 | Cap-Tons/1000 sf | 1210.25 | 1434.25 | 1434.25 | 0.1982 | 0.23245 | 0.23245 | 0 | 0 | 0 | 1210.25 | 1434.25 | 1434.25 | 0.1982 | 0.23245 | 0.23245 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | New | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 0.40936 | 0.027814 | 0.46499 | Cap-Tons/1000 sf | 1252 | 1520 | 1520 | 0.1741 | 0.21015 | 0.21015 | 0 | 0 | 0 | 1252 | 1520 | 1520 | 0.1741 | 0.21015 | 0.21015 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTS | RETAIL - SMALL | New | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 0.45321 | 0.030792 | 0.51479 | Cap-Tons/1000 sf | 1151.75 | 1369.25 | 1369.25 | 0.21234 | 0.24854 | 0.24854 | 0 | 0 | 0 | 1151.75 | 1369.25 | 1369.25 | 0.21234 | 0.24854 | 0.24854 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | SCN | STORAGE - CONDITIONED | New | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 0.24791 | 0.016844 | 0.2816 | Cap-Tons/1000 sf | 824.5 | 1028.5 | 1028.5 | 0.16136 | 0.20071 | 0.20071 | 0 | 0 | 0 | 824.5 | 1028.5 | 1028.5 | 0.16136 | 0.20071 | 0.20071 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ASM | ASSEMBLY | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.93897 | 0.063797 | 1.0666 | Cap-Tons/1000 sf | 809.1 | 1348.5 | 1027.6 | 0.23071 | 0.38452 | 0.25496 | 0 | 0 | 0 | 809.1 | 1348.5 | 1027.6 | 0.23071 | 0.38452 | 0.25496 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.54701 | 0.037166 | 0.62134 | Cap-Tons/1000 sf | 706.2 | 1177 | 895.2 | 0.22197 | 0.36996 | 0.25172 | 0 | 0 | 0 | 706.2 | 1177 | 895.2 | 0.22197 | 0.36996 | 0.25172 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.621 | 0.042193 | 0.70538 | Cap-Tons/1000 sf | 597.75 | 996.25 | 732.25 | 0.14598 | 0.2433 | 0.18118 | 0 | 0 | 0 | 597.75 | 996.25 | 732.25 | 0.14598 | 0.2433 | 0.18118 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.79463 | 0.050555 | 0.84519 | Cap-Tons/1000 sf | 746.4 | 1244 | 1004.4 | 0.23412 | 0.39021 | 0.29392 | 0 | 0 | 0 | 746.4 | 1244 | 1004.4 | 0.23412 | 0.39021 | 0.29392 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.61214 | 0.041591 | 0.69532 | Cap-Tons/1000 sf | 728 | 1192.5 | 871.7 | 0.15789 | 0.2585 | 0.18974 | 0 | 0 | 0 | 728 | 1192.5 | 871.7 | 0.15789 | 0.2585 | 0.18974 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EUN | EDUCATION - UNIVERSITY | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.58484 | 0.037208 | 0.62204 | Cap-Tons/1000 sf | 829.65 | 1382.75 | 1048.15 | 0.22712 | 0.37854 | 0.26162 | 0 | 0 | 0 | 829.65 | 1382.75 | 1048.15 | 0.22712 | 0.37854 | 0.26162 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | GRO | GROCERY | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 1.0397 | 0.066148 | 1.1059 | Cap-Tons/1000 sf | 959.55 | 1599.25 | 1295.55 | 0.2798 | 0.46634 | 0.32905 | 0 | 0 | 0 | 959.55 | 1599.25 | 1295.55 | 0.2798 | 0.46634 | 0.32905 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.77621 | 0.052738 | 0.88169 | Cap-Tons/1000 sf | 1440.45 | 2400.75 | 1831.45 | 0.2285 | 0.38084 | 0.26745 | 0 | 0 | 0 | 1440.45 | 2400.75 | 1831.45 | 0.2285 | 0.38084 | 0.26745 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HTL | LODGING - HOTEL | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.46549 | 0.029615 | 0.49511 | Cap-Tons/1000 sf | 1365.15 | 2275.25 | 1741.15 | 0.23897 | 0.39828 | 0.27682 | 0 | 0 | 0 | 1365.15 | 2275.25 | 1741.15 | 0.23897 | 0.39828 | 0.27682 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | MTL | LODGING - MOTEL | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.46549 | 0.029615 | 0.49511 | Cap-Tons/1000 sf | 1365.15 | 2275.25 | 1741.15 | 0.23897 | 0.39828 | 0.27682 | 0 | 0 | 0 | 1365.15 | 2275.25 | 1741.15 | 0.23897 | 0.39828 | 0.27682 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.82895 | 0.052738 | 0.88169 | Cap-Tons/1000 sf | 1120.2 | 1867 | 1501.2 | 0.22879 | 0.38132 | 0.26994 | 0 | 0 | 0 | 1120.2 | 1867 | 1501.2 | 0.22879 | 0.38132 | 0.26994 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFL | OFFICE - LARGE | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.61708 | 0.039259 | 0.65634 | Cap-Tons/1000 sf | 861.336 | 1435.5599 | 1021.286 | 0.28374 | 0.4729 | 0.32169 | 0 | 0 | 0 | 861.336 | 1435.5599 | 1021.286 | 0.28374 | 0.4729 | 0.32169 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFS | OFFICE - SMALL | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.65556 | 0.044541 | 0.74464 | Cap-Tons/1000 sf | 701.1 | 1168.5 | 854.85 | 0.25397 | 0.42328 | 0.29367 | 0 | 0 | 0 | 701.1 | 1168.5 | 854.85 | 0.25397 | 0.42328 | 0.29367 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 1.143 | 0.077662 | 1.2984 | Cap-Tons/1000 sf | 1102.95 | 1838.25 | 1428.95 | 0.24517 | 0.40862 | 0.27487 | 0 | 0 | 0 | 1102.95 | 1838.25 | 1428.95 | 0.24517 | 0.40862 | 0.27487 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.77022 | 0.052331 | 0.87488 | Cap-Tons/1000 sf | 927.1865 | 1545.3109 | 1158.6865 | 0.27318 | 0.4553 | 0.29548 | 0 | 0 | 0 | 927.1865 | 1545.3109 | 1158.6865 | 0.27318 | 0.4553 | 0.29548 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.37551 | 0.02389 | 0.3994 | Cap-Tons/1000 sf | 860.55 | 1434.25 | 1073.55 | 0.22793 | 0.37988 | 0.25813 | 0 | 0 | 0 | 860.55 | 1434.25 | 1073.55 | 0.22793 | 0.37988 | 0.25813 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.40936 | 0.027814 | 0.46499 | Cap-Tons/1000 sf | 912 | 1520 | 1166.5 | 0.22976 | 0.38294 | 0.26116 | 0 | 0 | 0 | 912 | 1520 | 1166.5 | 0.22976 | 0.38294 | 0.26116 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTS | RETAIL - SMALL | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.45321 | 0.030792 | 0.51479 | Cap-Tons/1000 sf | 821.55 | 1369.25 | 1030.05 | 0.22891 | 0.38152 | 0.26171 | 0 | 0 | 0 | 821.55 | 1369.25 | 1030.05 | 0.22891 | 0.38152 | 0.26171 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | SCN | STORAGE - CONDITIONED | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.24791 | 0.016844 | 0.2816 | Cap-Tons/1000 sf | 618 | 1028.5 | 814.5 | 0.2268 | 0.37737 | 0.26605 | 0 | 0 | 0 | 618 | 1028.5 | 814.5 | 0.2268 | 0.37737 | 0.26605 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ASM | ASSEMBLY | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.93897 | 0.063797 | 1.0666 | Cap-Tons/1000 sf | 1116 | 1348.5 | 1348.5 | 0.32417 | 0.38292 | 0.38292 | 0 | 0 | 0 | 1116 | 1348.5 | 1348.5 | 0.32417 | 0.38292 | 0.38292 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.54701 | 0.037166 | 0.62134 | Cap-Tons/1000 sf | 989 | 1177 | 1177 | 0.13542 | 0.16367 | 0.16367 | 0 | 0 | 0 | 989 | 1177 | 1177 | 0.13542 | 0.16367 | 0.16367 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.621 | 0.042193 | 0.70538 | Cap-Tons/1000 sf | 865.95 | 996.25 | 996.25 | 0.27078 | 0.31058 | 0.31058 | 0 | 0 | 0 | 865.95 | 996.25 | 996.25 | 0.27078 | 0.31058 | 0.31058 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.79463 | 0.050555 | 0.84519 | Cap-Tons/1000 sf | 1049.5 | 1244 | 1244 | 0.26252 | 0.31102 | 0.31102 | 0 | 0 | 0 | 1049.5 | 1244 | 1244 | 0.26252 | 0.31102 | 0.31102 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.61214 | 0.041591 | 0.69532 | Cap-Tons/1000 sf | 1052.95 | 1192.5 | 1192.5 | 0.30295 | 0.34225 | 0.34225 | 0 | 0 | 0 | 1052.95 | 1192.5 | 1192.5 | 0.30295 | 0.34225 | 0.34225 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EUN | EDUCATION - UNIVERSITY | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.58484 | 0.037208 | 0.62204 | Cap-Tons/1000 sf | 1164.25 | 1382.75 | 1382.75 | 0.18568 | 0.21783 | 0.21783 | 0 | 0 | 0 | 1164.25 | 1382.75 | 1382.75 | 0.18568 | 0.21783 | 0.21783 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | GRO | GROCERY | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 1.0397 | 0.066148 | 1.1059 | Cap-Tons/1000 sf | 1261.25 | 1599.25 | 1599.25 | 0.20361 | 0.26096 | 0.26096 | 0 | 0 | 0 | 1261.25 | 1599.25 | 1599.25 | 0.20361 | 0.26096 | 0.26096 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.77621 | 0.052738 | 0.88169 | Cap-Tons/1000 sf | 1997.25 | 2400.75 | 2400.75 | 0.21733 | 0.25688 | 0.25688 | 0 | 0 | 0 | 1997.25 | 2400.75 | 2400.75 | 0.21733 | 0.25688 | 0.25688 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HTL | LODGING - HOTEL | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.46549 | 0.029615 | 0.49511 | Cap-Tons/1000 sf | 1893.75 | 2275.25 | 2275.25 | 0.23134 | 0.27339 | 0.27339 | 0 | 0 | 0 | 1893.75 | 2275.25 | 2275.25 | 0.23134 | 0.27339 | 0.27339 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | MTL | LODGING - MOTEL | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.46549 | 0.029615 | 0.49511 | Cap-Tons/1000 sf | 1893.75 | 2275.25 | 2275.25 | 0.23134 | 0.27339 | 0.27339 | 0 | 0 | 0 | 1893.75 | 2275.25 | 2275.25 | 0.23134 | 0.27339 | 0.27339 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.82895 | 0.052738 | 0.88169 | Cap-Tons/1000 sf | 1481 | 1867 | 1867 | 0.15399 | 0.19244 | 0.19244 | 0 | 0 | 0 | 1481 | 1867 | 1867 | 0.15399 | 0.19244 | 0.19244 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFL | OFFICE - LARGE | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.61708 | 0.039259 | 0.65634 | Cap-Tons/1000 sf | 1281.3599 | 1435.5599 | 1435.5599 | 0.3441 | 0.3797 | 0.3797 | 0 | 0 | 0 | 1281.3599 | 1435.5599 | 1435.5599 | 0.3441 | 0.3797 | 0.3797 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFS | OFFICE - SMALL | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.65556 | 0.044541 | 0.74464 | Cap-Tons/1000 sf | 1014.7 | 1168.5 | 1168.5 | 0.3258 | 0.3659 | 0.3659 | 0 | 0 | 0 | 1014.7 | 1168.5 | 1168.5 | 0.3258 | 0.3659 | 0.3659 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 1.143 | 0.077662 | 1.2984 | Cap-Tons/1000 sf | 1492.25 | 1838.25 | 1838.25 | 0.18454 | 0.22734 | 0.22734 | 0 | 0 | 0 | 1492.25 | 1838.25 | 1838.25 | 0.18454 | 0.22734 | 0.22734 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.77022 | 0.052331 | 0.87488 | Cap-Tons/1000 sf | 1294.8109 | 1545.3109 | 1545.3109 | 0.30961 | 0.36546 | 0.36546 | 0 | 0 | 0 | 1294.8109 | 1545.3109 | 1545.3109 | 0.30961 | 0.36546 | 0.36546 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.37551 | 0.02389 | 0.3994 | Cap-Tons/1000 sf | 1215.25 | 1434.25 | 1434.25 | 0.1369 | 0.16285 | 0.16285 | 0 | 0 | 0 | 1215.25 | 1434.25 | 1434.25 | 0.1369 | 0.16285 | 0.16285 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.40936 | 0.027814 | 0.46499 | Cap-Tons/1000 sf | 1256.5 | 1520 | 1520 | 0.16235 | 0.1959 | 0.1959 | 0 | 0 | 0 | 1256.5 | 1520 | 1520 | 0.16235 | 0.1959 | 0.1959 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTS | RETAIL - SMALL | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.45321 | 0.030792 | 0.51479 | Cap-Tons/1000 sf | 1153.75 | 1369.25 | 1369.25 | 0.16278 | 0.19258 | 0.19258 | 0 | 0 | 0 | 1153.75 | 1369.25 | 1369.25 | 0.16278 | 0.19258 | 0.19258 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | SCN | STORAGE - CONDITIONED | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.24791 | 0.016844 | 0.2816 | Cap-Tons/1000 sf | 826.5 | 1028.5 | 1028.5 | 0.090048 | 0.11688 | 0.11688 | 0 | 0 | 0 | 826.5 | 1028.5 | 1028.5 | 0.090048 | 0.11688 | 0.11688 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ASM | ASSEMBLY | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.93897 | 0.063797 | 1.0666 | Cap-Tons/1000 sf | 809.1 | 1348.5 | 1027.1 | 0.26725 | 0.44542 | 0.29875 | 0 | 0 | 0 | 809.1 | 1348.5 | 1027.1 | 0.26725 | 0.44542 | 0.29875 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.54701 | 0.037166 | 0.62134 | Cap-Tons/1000 sf | 706.2 | 1177 | 915.7 | 0.13588 | 0.22647 | 0.18098 | 0 | 0 | 0 | 706.2 | 1177 | 915.7 | 0.13588 | 0.22647 | 0.18098 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.621 | 0.042193 | 0.70538 | Cap-Tons/1000 sf | 597.75 | 996.25 | 755.75 | 0.1722 | 0.287 | 0.2168 | 0 | 0 | 0 | 597.75 | 996.25 | 755.75 | 0.1722 | 0.287 | 0.2168 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.79463 | 0.050555 | 0.84519 | Cap-Tons/1000 sf | 746.4 | 1244 | 1045.9 | 0.23877 | 0.39795 | 0.29937 | 0 | 0 | 0 | 746.4 | 1244 | 1045.9 | 0.23877 | 0.39795 | 0.29937 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.61214 | 0.041591 | 0.69532 | Cap-Tons/1000 sf | 715.5 | 1192.5 | 894.5 | 0.18237 | 0.30395 | 0.22562 | 0 | 0 | 0 | 715.5 | 1192.5 | 894.5 | 0.18237 | 0.30395 | 0.22562 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EUN | EDUCATION - UNIVERSITY | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.58484 | 0.037208 | 0.62204 | Cap-Tons/1000 sf | 829.65 | 1382.75 | 1055.65 | 0.12377 | 0.20628 | 0.16042 | 0 | 0 | 0 | 829.65 | 1382.75 | 1055.65 | 0.12377 | 0.20628 | 0.16042 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | GRO | GROCERY | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 1.0397 | 0.066148 | 1.1059 | Cap-Tons/1000 sf | 959.55 | 1599.25 | 1298.55 | 0.2729 | 0.45483 | 0.32225 | 0 | 0 | 0 | 959.55 | 1599.25 | 1298.55 | 0.2729 | 0.45483 | 0.32225 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.77621 | 0.052738 | 0.88169 | Cap-Tons/1000 sf | 1440.45 | 2400.75 | 1838.45 | 0.23315 | 0.38858 | 0.2733 | 0 | 0 | 0 | 1440.45 | 2400.75 | 1838.45 | 0.23315 | 0.38858 | 0.2733 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HTL | LODGING - HOTEL | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.46549 | 0.029615 | 0.49511 | Cap-Tons/1000 sf | 1365.15 | 2275.25 | 1738.65 | 0.26249 | 0.43749 | 0.30119 | 0 | 0 | 0 | 1365.15 | 2275.25 | 1738.65 | 0.26249 | 0.43749 | 0.30119 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | MTL | LODGING - MOTEL | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.46549 | 0.029615 | 0.49511 | Cap-Tons/1000 sf | 1365.15 | 2275.25 | 1738.65 | 0.26249 | 0.43749 | 0.30119 | 0 | 0 | 0 | 1365.15 | 2275.25 | 1738.65 | 0.26249 | 0.43749 | 0.30119 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.82895 | 0.052738 | 0.88169 | Cap-Tons/1000 sf | 1120.2 | 1867 | 1505.2 | 0.22938 | 0.38229 | 0.26973 | 0 | 0 | 0 | 1120.2 | 1867 | 1505.2 | 0.22938 | 0.38229 | 0.26973 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFL | OFFICE - LARGE | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.61708 | 0.039259 | 0.65634 | Cap-Tons/1000 sf | 861.336 | 1435.5599 | 1028.486 | 0.24985 | 0.41642 | 0.2877 | 0 | 0 | 0 | 861.336 | 1435.5599 | 1028.486 | 0.24985 | 0.41642 | 0.2877 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFS | OFFICE - SMALL | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.65556 | 0.044541 | 0.74464 | Cap-Tons/1000 sf | 701.1 | 1168.5 | 860.5 | 0.23164 | 0.38607 | 0.27064 | 0 | 0 | 0 | 701.1 | 1168.5 | 860.5 | 0.23164 | 0.38607 | 0.27064 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 1.143 | 0.077662 | 1.2984 | Cap-Tons/1000 sf | 1102.95 | 1838.25 | 1429.95 | 0.2643 | 0.4405 | 0.30005 | 0 | 0 | 0 | 1102.95 | 1838.25 | 1429.95 | 0.2643 | 0.4405 | 0.30005 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.77022 | 0.052331 | 0.87488 | Cap-Tons/1000 sf | 927.1865 | 1545.3109 | 1156.6865 | 0.29891 | 0.49819 | 0.33071 | 0 | 0 | 0 | 927.1865 | 1545.3109 | 1156.6865 | 0.29891 | 0.49819 | 0.33071 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.37551 | 0.02389 | 0.3994 | Cap-Tons/1000 sf | 860.55 | 1434.25 | 1071.55 | 0.25892 | 0.43153 | 0.29032 | 0 | 0 | 0 | 860.55 | 1434.25 | 1071.55 | 0.25892 | 0.43153 | 0.29032 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.40936 | 0.027814 | 0.46499 | Cap-Tons/1000 sf | 912 | 1520 | 1165.5 | 0.26036 | 0.43394 | 0.30006 | 0 | 0 | 0 | 912 | 1520 | 1165.5 | 0.26036 | 0.43394 | 0.30006 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTS | RETAIL - SMALL | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.45321 | 0.030792 | 0.51479 | Cap-Tons/1000 sf | 821.55 | 1369.25 | 1028.05 | 0.26152 | 0.43586 | 0.29642 | 0 | 0 | 0 | 821.55 | 1369.25 | 1028.05 | 0.26152 | 0.43586 | 0.29642 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | SCN | STORAGE - CONDITIONED | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.24791 | 0.016844 | 0.2816 | Cap-Tons/1000 sf | 617.1 | 1028.5 | 818.1 | 0.23362 | 0.38937 | 0.27142 | 0 | 0 | 0 | 617.1 | 1028.5 | 818.1 | 0.23362 | 0.38937 | 0.27142 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ASM | ASSEMBLY | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.93897 | 0.063797 | 1.0666 | Cap-Tons/1000 sf | 1114 | 1348.5 | 1348.5 | 0.11182 | 0.13797 | 0.13797 | 0 | 0 | 0 | 1114 | 1348.5 | 1348.5 | 0.11182 | 0.13797 | 0.13797 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.54701 | 0.037166 | 0.62134 | Cap-Tons/1000 sf | 979 | 1177 | 1177 | 0.099029 | 0.12068 | 0.12068 | 0 | 0 | 0 | 979 | 1177 | 1177 | 0.099029 | 0.12068 | 0.12068 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.621 | 0.042193 | 0.70538 | Cap-Tons/1000 sf | 847.75 | 996.25 | 996.25 | 0.23974 | 0.28349 | 0.28349 | 0 | 0 | 0 | 847.75 | 996.25 | 996.25 | 0.23974 | 0.28349 | 0.28349 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | GRO | GROCERY | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 1.0397 | 0.066148 | 1.1059 | Cap-Tons/1000 sf | 1256.25 | 1599.25 | 1599.25 | 0.18386 | 0.23721 | 0.23721 | 0 | 0 | 0 | 1256.25 | 1599.25 | 1599.25 | 0.18386 | 0.23721 | 0.23721 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.77621 | 0.052738 | 0.88169 | Cap-Tons/1000 sf | 1994.25 | 2400.75 | 2400.75 | 0.23033 | 0.27358 | 0.27358 | 0 | 0 | 0 | 1994.25 | 2400.75 | 2400.75 | 0.23033 | 0.27358 | 0.27358 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HTL | LODGING - HOTEL | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.46549 | 0.029615 | 0.49511 | Cap-Tons/1000 sf | 1903.25 | 2275.25 | 2275.25 | 0.23419 | 0.27629 | 0.27629 | 0 | 0 | 0 | 1903.25 | 2275.25 | 2275.25 | 0.23419 | 0.27629 | 0.27629 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | MTL | LODGING - MOTEL | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.46549 | 0.029615 | 0.49511 | Cap-Tons/1000 sf | 1903.25 | 2275.25 | 2275.25 | 0.23419 | 0.27629 | 0.27629 | 0 | 0 | 0 | 1903.25 | 2275.25 | 2275.25 | 0.23419 | 0.27629 | 0.27629 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.82895 | 0.052738 | 0.88169 | Cap-Tons/1000 sf | 1478.5 | 1867 | 1867 | 0.18436 | 0.22936 | 0.22936 | 0 | 0 | 0 | 1478.5 | 1867 | 1867 | 0.18436 | 0.22936 | 0.22936 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFL | OFFICE - LARGE | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.61708 | 0.039259 | 0.65634 | Cap-Tons/1000 sf | 1279.0099 | 1435.5599 | 1435.5599 | 0.3696 | 0.409 | 0.409 | 0 | 0 | 0 | 1279.0099 | 1435.5599 | 1435.5599 | 0.3696 | 0.409 | 0.409 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFS | OFFICE - SMALL | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.65556 | 0.044541 | 0.74464 | Cap-Tons/1000 sf | 1013 | 1168.5 | 1168.5 | 0.31747 | 0.35982 | 0.35982 | 0 | 0 | 0 | 1013 | 1168.5 | 1168.5 | 0.31747 | 0.35982 | 0.35982 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 1.143 | 0.077662 | 1.2984 | Cap-Tons/1000 sf | 1490.75 | 1838.25 | 1838.25 | 0.14443 | 0.17873 | 0.17873 | 0 | 0 | 0 | 1490.75 | 1838.25 | 1838.25 | 0.14443 | 0.17873 | 0.17873 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.77022 | 0.052331 | 0.87488 | Cap-Tons/1000 sf | 1298.8109 | 1545.3109 | 1545.3109 | 0.14493 | 0.17408 | 0.17408 | 0 | 0 | 0 | 1298.8109 | 1545.3109 | 1545.3109 | 0.14493 | 0.17408 | 0.17408 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.37551 | 0.02389 | 0.3994 | Cap-Tons/1000 sf | 1215.25 | 1434.25 | 1434.25 | 0.20963 | 0.24653 | 0.24653 | 0 | 0 | 0 | 1215.25 | 1434.25 | 1434.25 | 0.20963 | 0.24653 | 0.24653 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.40936 | 0.027814 | 0.46499 | Cap-Tons/1000 sf | 1260.5 | 1520 | 1520 | 0.18914 | 0.22684 | 0.22684 | 0 | 0 | 0 | 1260.5 | 1520 | 1520 | 0.18914 | 0.22684 | 0.22684 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTS | RETAIL - SMALL | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.45321 | 0.030792 | 0.51479 | Cap-Tons/1000 sf | 1156.25 | 1369.25 | 1369.25 | 0.24144 | 0.28289 | 0.28289 | 0 | 0 | 0 | 1156.25 | 1369.25 | 1369.25 | 0.24144 | 0.28289 | 0.28289 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | SCN | STORAGE - CONDITIONED | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.24791 | 0.016844 | 0.2816 | Cap-Tons/1000 sf | 823 | 1028.5 | 1028.5 | 0.16205 | 0.2012 | 0.2012 | 0 | 0 | 0 | 823 | 1028.5 | 1028.5 | 0.16205 | 0.2012 | 0.2012 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ASM | ASSEMBLY | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.93897 | 0.063797 | 1.0666 | Cap-Tons/1000 sf | 809.1 | 1348.5 | 1038.1 | 0.27489 | 0.45816 | 0.32659 | 0 | 0 | 0 | 809.1 | 1348.5 | 1038.1 | 0.27489 | 0.45816 | 0.32659 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.54701 | 0.037166 | 0.62134 | Cap-Tons/1000 sf | 706.2 | 1177 | 915.7 | 0.18251 | 0.30419 | 0.20826 | 0 | 0 | 0 | 706.2 | 1177 | 915.7 | 0.18251 | 0.30419 | 0.20826 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.621 | 0.042193 | 0.70538 | Cap-Tons/1000 sf | 597.75 | 996.25 | 753.25 | 0.18708 | 0.31181 | 0.23468 | 0 | 0 | 0 | 597.75 | 996.25 | 753.25 | 0.18708 | 0.31181 | 0.23468 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.79463 | 0.050555 | 0.84519 | Cap-Tons/1000 sf | 746.4 | 1244 | 1049.9 | 0.24696 | 0.41161 | 0.31356 | 0 | 0 | 0 | 746.4 | 1244 | 1049.9 | 0.24696 | 0.41161 | 0.31356 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.61214 | 0.041591 | 0.69532 | Cap-Tons/1000 sf | 715.5 | 1192.5 | 887.5 | 0.20004 | 0.33341 | 0.24519 | 0 | 0 | 0 | 715.5 | 1192.5 | 887.5 | 0.20004 | 0.33341 | 0.24519 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EUN | EDUCATION - UNIVERSITY | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.58484 | 0.037208 | 0.62204 | Cap-Tons/1000 sf | 829.65 | 1382.75 | 1057.15 | 0.20288 | 0.33813 | 0.23478 | 0 | 0 | 0 | 829.65 | 1382.75 | 1057.15 | 0.20288 | 0.33813 | 0.23478 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | GRO | GROCERY | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 1.0397 | 0.066148 | 1.1059 | Cap-Tons/1000 sf | 959.55 | 1599.25 | 1298.55 | 0.27763 | 0.46271 | 0.33023 | 0 | 0 | 0 | 959.55 | 1599.25 | 1298.55 | 0.27763 | 0.46271 | 0.33023 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.77621 | 0.052738 | 0.88169 | Cap-Tons/1000 sf | 1440.45 | 2400.75 | 1836.95 | 0.25687 | 0.42812 | 0.29752 | 0 | 0 | 0 | 1440.45 | 2400.75 | 1836.95 | 0.25687 | 0.42812 | 0.29752 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HTL | LODGING - HOTEL | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.46549 | 0.029615 | 0.49511 | Cap-Tons/1000 sf | 1365.15 | 2275.25 | 1746.15 | 0.26657 | 0.44428 | 0.30852 | 0 | 0 | 0 | 1365.15 | 2275.25 | 1746.15 | 0.26657 | 0.44428 | 0.30852 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | MTL | LODGING - MOTEL | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.46549 | 0.029615 | 0.49511 | Cap-Tons/1000 sf | 1365.15 | 2275.25 | 1746.15 | 0.26657 | 0.44428 | 0.30852 | 0 | 0 | 0 | 1365.15 | 2275.25 | 1746.15 | 0.26657 | 0.44428 | 0.30852 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.82895 | 0.052738 | 0.88169 | Cap-Tons/1000 sf | 1120.2 | 1867 | 1503.2 | 0.24848 | 0.41414 | 0.28778 | 0 | 0 | 0 | 1120.2 | 1867 | 1503.2 | 0.24848 | 0.41414 | 0.28778 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFL | OFFICE - LARGE | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.61708 | 0.039259 | 0.65634 | Cap-Tons/1000 sf | 861.336 | 1435.5599 | 1031.536 | 0.28463 | 0.47439 | 0.33033 | 0 | 0 | 0 | 861.336 | 1435.5599 | 1031.536 | 0.28463 | 0.47439 | 0.33033 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFS | OFFICE - SMALL | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.65556 | 0.044541 | 0.74464 | Cap-Tons/1000 sf | 701.1 | 1168.5 | 861.65 | 0.25811 | 0.43019 | 0.30616 | 0 | 0 | 0 | 701.1 | 1168.5 | 861.65 | 0.25811 | 0.43019 | 0.30616 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 1.143 | 0.077662 | 1.2984 | Cap-Tons/1000 sf | 1102.95 | 1838.25 | 1432.95 | 0.27303 | 0.45505 | 0.31573 | 0 | 0 | 0 | 1102.95 | 1838.25 | 1432.95 | 0.27303 | 0.45505 | 0.31573 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.77022 | 0.052331 | 0.87488 | Cap-Tons/1000 sf | 927.1865 | 1545.3109 | 1166.6865 | 0.31011 | 0.51684 | 0.36061 | 0 | 0 | 0 | 927.1865 | 1545.3109 | 1166.6865 | 0.31011 | 0.51684 | 0.36061 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.37551 | 0.02389 | 0.3994 | Cap-Tons/1000 sf | 860.55 | 1434.25 | 1071.05 | 0.27336 | 0.4556 | 0.30816 | 0 | 0 | 0 | 860.55 | 1434.25 | 1071.05 | 0.27336 | 0.4556 | 0.30816 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.40936 | 0.027814 | 0.46499 | Cap-Tons/1000 sf | 912 | 1520 | 1168 | 0.2747 | 0.45783 | 0.31665 | 0 | 0 | 0 | 912 | 1520 | 1168 | 0.2747 | 0.45783 | 0.31665 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTS | RETAIL - SMALL | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.45321 | 0.030792 | 0.51479 | Cap-Tons/1000 sf | 821.55 | 1369.25 | 1027.55 | 0.26527 | 0.44211 | 0.30037 | 0 | 0 | 0 | 821.55 | 1369.25 | 1027.55 | 0.26527 | 0.44211 | 0.30037 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | SCN | STORAGE - CONDITIONED | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.24791 | 0.016844 | 0.2816 | Cap-Tons/1000 sf | 617.1 | 1028.5 | 819.1 | 0.24355 | 0.40591 | 0.28205 | 0 | 0 | 0 | 617.1 | 1028.5 | 819.1 | 0.24355 | 0.40591 | 0.28205 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ASM | ASSEMBLY | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.93897 | 0.063797 | 1.0666 | Cap-Tons/1000 sf | 1095.5 | 1348.5 | 1348.5 | 0.36121 | 0.43741 | 0.43741 | 0 | 0 | 0 | 1095.5 | 1348.5 | 1348.5 | 0.36121 | 0.43741 | 0.43741 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.54701 | 0.037166 | 0.62134 | Cap-Tons/1000 sf | 974.5 | 1177 | 1177 | 0.38359 | 0.44914 | 0.44914 | 0 | 0 | 0 | 974.5 | 1177 | 1177 | 0.38359 | 0.44914 | 0.44914 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.621 | 0.042193 | 0.70538 | Cap-Tons/1000 sf | 851.25 | 996.25 | 996.25 | 0.42953 | 0.49608 | 0.49608 | 0 | 0 | 0 | 851.25 | 996.25 | 996.25 | 0.42953 | 0.49608 | 0.49608 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.79463 | 0.050555 | 0.84519 | Cap-Tons/1000 sf | 993 | 1244 | 1244 | 0.29073 | 0.36413 | 0.36413 | 0 | 0 | 0 | 993 | 1244 | 1244 | 0.29073 | 0.36413 | 0.36413 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.61214 | 0.041591 | 0.69532 | Cap-Tons/1000 sf | 1035.5 | 1192.5 | 1192.5 | 0.48358 | 0.54958 | 0.54958 | 0 | 0 | 0 | 1035.5 | 1192.5 | 1192.5 | 0.48358 | 0.54958 | 0.54958 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EUN | EDUCATION - UNIVERSITY | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.58484 | 0.037208 | 0.62204 | Cap-Tons/1000 sf | 1157.25 | 1382.75 | 1382.75 | 0.34398 | 0.40153 | 0.40153 | 0 | 0 | 0 | 1157.25 | 1382.75 | 1382.75 | 0.34398 | 0.40153 | 0.40153 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | GRO | GROCERY | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 1.0397 | 0.066148 | 1.1059 | Cap-Tons/1000 sf | 1256.25 | 1599.25 | 1599.25 | 0.19212 | 0.24782 | 0.24782 | 0 | 0 | 0 | 1256.25 | 1599.25 | 1599.25 | 0.19212 | 0.24782 | 0.24782 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.77621 | 0.052738 | 0.88169 | Cap-Tons/1000 sf | 1998.75 | 2400.75 | 2400.75 | 0.18904 | 0.22699 | 0.22699 | 0 | 0 | 0 | 1998.75 | 2400.75 | 2400.75 | 0.18904 | 0.22699 | 0.22699 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HTL | LODGING - HOTEL | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.46549 | 0.029615 | 0.49511 | Cap-Tons/1000 sf | 1896.25 | 2275.25 | 2275.25 | 0.21456 | 0.25581 | 0.25581 | 0 | 0 | 0 | 1896.25 | 2275.25 | 2275.25 | 0.21456 | 0.25581 | 0.25581 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | MTL | LODGING - MOTEL | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.46549 | 0.029615 | 0.49511 | Cap-Tons/1000 sf | 1896.25 | 2275.25 | 2275.25 | 0.21456 | 0.25581 | 0.25581 | 0 | 0 | 0 | 1896.25 | 2275.25 | 2275.25 | 0.21456 | 0.25581 | 0.25581 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.82895 | 0.052738 | 0.88169 | Cap-Tons/1000 sf | 1485 | 1867 | 1867 | 0.13865 | 0.18025 | 0.18025 | 0 | 0 | 0 | 1485 | 1867 | 1867 | 0.13865 | 0.18025 | 0.18025 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFL | OFFICE - LARGE | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.61708 | 0.039259 | 0.65634 | Cap-Tons/1000 sf | 1275.1099 | 1435.5599 | 1435.5599 | 0.48515 | 0.5356 | 0.5356 | 0 | 0 | 0 | 1275.1099 | 1435.5599 | 1435.5599 | 0.48515 | 0.5356 | 0.5356 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFS | OFFICE - SMALL | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.65556 | 0.044541 | 0.74464 | Cap-Tons/1000 sf | 1010.05 | 1168.5 | 1168.5 | 0.36752 | 0.41557 | 0.41557 | 0 | 0 | 0 | 1010.05 | 1168.5 | 1168.5 | 0.36752 | 0.41557 | 0.41557 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 1.143 | 0.077662 | 1.2984 | Cap-Tons/1000 sf | 1489.75 | 1838.25 | 1838.25 | 0.32066 | 0.39231 | 0.39231 | 0 | 0 | 0 | 1489.75 | 1838.25 | 1838.25 | 0.32066 | 0.39231 | 0.39231 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.77022 | 0.052331 | 0.87488 | Cap-Tons/1000 sf | 1289.8109 | 1545.3109 | 1545.3109 | 0.37865 | 0.44985 | 0.44985 | 0 | 0 | 0 | 1289.8109 | 1545.3109 | 1545.3109 | 0.37865 | 0.44985 | 0.44985 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.37551 | 0.02389 | 0.3994 | Cap-Tons/1000 sf | 1214.25 | 1434.25 | 1434.25 | 0.37527 | 0.43682 | 0.43682 | 0 | 0 | 0 | 1214.25 | 1434.25 | 1434.25 | 0.37527 | 0.43682 | 0.43682 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.40936 | 0.027814 | 0.46499 | Cap-Tons/1000 sf | 1257.5 | 1520 | 1520 | 0.20587 | 0.25207 | 0.25207 | 0 | 0 | 0 | 1257.5 | 1520 | 1520 | 0.20587 | 0.25207 | 0.25207 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTS | RETAIL - SMALL | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.45321 | 0.030792 | 0.51479 | Cap-Tons/1000 sf | 1157.75 | 1369.25 | 1369.25 | 0.35417 | 0.41392 | 0.41392 | 0 | 0 | 0 | 1157.75 | 1369.25 | 1369.25 | 0.35417 | 0.41392 | 0.41392 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | SCN | STORAGE - CONDITIONED | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.24791 | 0.016844 | 0.2816 | Cap-Tons/1000 sf | 825 | 1028.5 | 1028.5 | 0.14598 | 0.18888 | 0.18888 | 0 | 0 | 0 | 825 | 1028.5 | 1028.5 | 0.14598 | 0.18888 | 0.18888 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ASM | ASSEMBLY | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.93897 | 0.063797 | 1.0666 | Cap-Tons/1000 sf | 809.1 | 1348.5 | 1027.6 | 0.19828 | 0.33047 | 0.22773 | 0 | 0 | 0 | 809.1 | 1348.5 | 1027.6 | 0.19828 | 0.33047 | 0.22773 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.54701 | 0.037166 | 0.62134 | Cap-Tons/1000 sf | 706.2 | 1177 | 928.7 | 0.15004 | 0.25007 | 0.17884 | 0 | 0 | 0 | 706.2 | 1177 | 928.7 | 0.15004 | 0.25007 | 0.17884 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.621 | 0.042193 | 0.70538 | Cap-Tons/1000 sf | 597.75 | 996.25 | 772.25 | 0.14285 | 0.23809 | 0.1906 | 0 | 0 | 0 | 597.75 | 996.25 | 772.25 | 0.14285 | 0.23809 | 0.1906 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.79463 | 0.050555 | 0.84519 | Cap-Tons/1000 sf | 746.4 | 1244 | 1050.9 | 0.18756 | 0.3126 | 0.25126 | 0 | 0 | 0 | 746.4 | 1244 | 1050.9 | 0.18756 | 0.3126 | 0.25126 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.61214 | 0.041591 | 0.69532 | Cap-Tons/1000 sf | 715.5 | 1192.5 | 929.5 | 0.13965 | 0.23275 | 0.1858 | 0 | 0 | 0 | 715.5 | 1192.5 | 929.5 | 0.13965 | 0.23275 | 0.1858 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EUN | EDUCATION - UNIVERSITY | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.58484 | 0.037208 | 0.62204 | Cap-Tons/1000 sf | 829.65 | 1382.75 | 1066.65 | 0.17198 | 0.28664 | 0.20528 | 0 | 0 | 0 | 829.65 | 1382.75 | 1066.65 | 0.17198 | 0.28664 | 0.20528 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | GRO | GROCERY | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 1.0397 | 0.066148 | 1.1059 | Cap-Tons/1000 sf | 959.55 | 1599.25 | 1291.05 | 0.21135 | 0.35224 | 0.26195 | 0 | 0 | 0 | 959.55 | 1599.25 | 1291.05 | 0.21135 | 0.35224 | 0.26195 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.77621 | 0.052738 | 0.88169 | Cap-Tons/1000 sf | 1440.45 | 2400.75 | 1845.45 | 0.21745 | 0.36242 | 0.2576 | 0 | 0 | 0 | 1440.45 | 2400.75 | 1845.45 | 0.21745 | 0.36242 | 0.2576 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HTL | LODGING - HOTEL | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.46549 | 0.029615 | 0.49511 | Cap-Tons/1000 sf | 1365.15 | 2275.25 | 1755.65 | 0.21695 | 0.36158 | 0.256 | 0 | 0 | 0 | 1365.15 | 2275.25 | 1755.65 | 0.21695 | 0.36158 | 0.256 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | MTL | LODGING - MOTEL | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.46549 | 0.029615 | 0.49511 | Cap-Tons/1000 sf | 1365.15 | 2275.25 | 1755.65 | 0.21695 | 0.36158 | 0.256 | 0 | 0 | 0 | 1365.15 | 2275.25 | 1755.65 | 0.21695 | 0.36158 | 0.256 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.82895 | 0.052738 | 0.88169 | Cap-Tons/1000 sf | 1120.2 | 1867 | 1509.2 | 0.19161 | 0.31934 | 0.23191 | 0 | 0 | 0 | 1120.2 | 1867 | 1509.2 | 0.19161 | 0.31934 | 0.23191 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFL | OFFICE - LARGE | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.61708 | 0.039259 | 0.65634 | Cap-Tons/1000 sf | 861.336 | 1435.5599 | 1045.836 | 0.24203 | 0.40338 | 0.28248 | 0 | 0 | 0 | 861.336 | 1435.5599 | 1045.836 | 0.24203 | 0.40338 | 0.28248 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFS | OFFICE - SMALL | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.65556 | 0.044541 | 0.74464 | Cap-Tons/1000 sf | 701.1 | 1168.5 | 875.6 | 0.21442 | 0.35736 | 0.25972 | 0 | 0 | 0 | 701.1 | 1168.5 | 875.6 | 0.21442 | 0.35736 | 0.25972 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 1.143 | 0.077662 | 1.2984 | Cap-Tons/1000 sf | 1102.95 | 1838.25 | 1430.45 | 0.21086 | 0.35143 | 0.24546 | 0 | 0 | 0 | 1102.95 | 1838.25 | 1430.45 | 0.21086 | 0.35143 | 0.24546 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.77022 | 0.052331 | 0.87488 | Cap-Tons/1000 sf | 927.1865 | 1545.3109 | 1155.6865 | 0.23373 | 0.38955 | 0.26348 | 0 | 0 | 0 | 927.1865 | 1545.3109 | 1155.6865 | 0.23373 | 0.38955 | 0.26348 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.37551 | 0.02389 | 0.3994 | Cap-Tons/1000 sf | 860.55 | 1434.25 | 1073.55 | 0.21206 | 0.35344 | 0.24326 | 0 | 0 | 0 | 860.55 | 1434.25 | 1073.55 | 0.21206 | 0.35344 | 0.24326 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.40936 | 0.027814 | 0.46499 | Cap-Tons/1000 sf | 912 | 1520 | 1165 | 0.21049 | 0.35082 | 0.24764 | 0 | 0 | 0 | 912 | 1520 | 1165 | 0.21049 | 0.35082 | 0.24764 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTS | RETAIL - SMALL | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.45321 | 0.030792 | 0.51479 | Cap-Tons/1000 sf | 821.55 | 1369.25 | 1031.55 | 0.20862 | 0.3477 | 0.24042 | 0 | 0 | 0 | 821.55 | 1369.25 | 1031.55 | 0.20862 | 0.3477 | 0.24042 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | SCN | STORAGE - CONDITIONED | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.24791 | 0.016844 | 0.2816 | Cap-Tons/1000 sf | 617.1 | 1028.5 | 810.6 | 0.18882 | 0.31469 | 0.22557 | 0 | 0 | 0 | 617.1 | 1028.5 | 810.6 | 0.18882 | 0.31469 | 0.22557 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ASM | ASSEMBLY | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.93897 | 0.063797 | 1.0666 | Cap-Tons/1000 sf | 1111.5 | 1348.5 | 1348.5 | 0.37598 | 0.44563 | 0.44563 | 0 | 0 | 0 | 1111.5 | 1348.5 | 1348.5 | 0.37598 | 0.44563 | 0.44563 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.54701 | 0.037166 | 0.62134 | Cap-Tons/1000 sf | 978.5 | 1177 | 1177 | 0.3813 | 0.44605 | 0.44605 | 0 | 0 | 0 | 978.5 | 1177 | 1177 | 0.3813 | 0.44605 | 0.44605 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.621 | 0.042193 | 0.70538 | Cap-Tons/1000 sf | 828.75 | 996.25 | 996.25 | 0.33589 | 0.39854 | 0.39854 | 0 | 0 | 0 | 828.75 | 996.25 | 996.25 | 0.33589 | 0.39854 | 0.39854 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.79463 | 0.050555 | 0.84519 | Cap-Tons/1000 sf | 965 | 1244 | 1244 | 0.24202 | 0.31192 | 0.31192 | 0 | 0 | 0 | 965 | 1244 | 1244 | 0.24202 | 0.31192 | 0.31192 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.61214 | 0.041591 | 0.69532 | Cap-Tons/1000 sf | 993.5 | 1192.5 | 1192.5 | 0.34908 | 0.41198 | 0.41198 | 0 | 0 | 0 | 993.5 | 1192.5 | 1192.5 | 0.34908 | 0.41198 | 0.41198 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EUN | EDUCATION - UNIVERSITY | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.58484 | 0.037208 | 0.62204 | Cap-Tons/1000 sf | 1155.25 | 1382.75 | 1382.75 | 0.27632 | 0.32622 | 0.32622 | 0 | 0 | 0 | 1155.25 | 1382.75 | 1382.75 | 0.27632 | 0.32622 | 0.32622 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | GRO | GROCERY | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 1.0397 | 0.066148 | 1.1059 | Cap-Tons/1000 sf | 1263.25 | 1599.25 | 1599.25 | 0.2148 | 0.2734 | 0.2734 | 0 | 0 | 0 | 1263.25 | 1599.25 | 1599.25 | 0.2148 | 0.2734 | 0.2734 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.77621 | 0.052738 | 0.88169 | Cap-Tons/1000 sf | 1984.75 | 2400.75 | 2400.75 | 0.22829 | 0.27344 | 0.27344 | 0 | 0 | 0 | 1984.75 | 2400.75 | 2400.75 | 0.22829 | 0.27344 | 0.27344 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HTL | LODGING - HOTEL | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.46549 | 0.029615 | 0.49511 | Cap-Tons/1000 sf | 1872.25 | 2275.25 | 2275.25 | 0.25472 | 0.30502 | 0.30502 | 0 | 0 | 0 | 1872.25 | 2275.25 | 2275.25 | 0.25472 | 0.30502 | 0.30502 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | MTL | LODGING - MOTEL | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.46549 | 0.029615 | 0.49511 | Cap-Tons/1000 sf | 1872.25 | 2275.25 | 2275.25 | 0.25472 | 0.30502 | 0.30502 | 0 | 0 | 0 | 1872.25 | 2275.25 | 2275.25 | 0.25472 | 0.30502 | 0.30502 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.82895 | 0.052738 | 0.88169 | Cap-Tons/1000 sf | 1459.5 | 1867 | 1867 | 0.18505 | 0.23515 | 0.23515 | 0 | 0 | 0 | 1459.5 | 1867 | 1867 | 0.18505 | 0.23515 | 0.23515 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFL | OFFICE - LARGE | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.61708 | 0.039259 | 0.65634 | Cap-Tons/1000 sf | 1269.5599 | 1435.5599 | 1435.5599 | 0.45158 | 0.50313 | 0.50313 | 0 | 0 | 0 | 1269.5599 | 1435.5599 | 1435.5599 | 0.45158 | 0.50313 | 0.50313 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFS | OFFICE - SMALL | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.65556 | 0.044541 | 0.74464 | Cap-Tons/1000 sf | 1004 | 1168.5 | 1168.5 | 0.35982 | 0.41062 | 0.41062 | 0 | 0 | 0 | 1004 | 1168.5 | 1168.5 | 0.35982 | 0.41062 | 0.41062 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 1.143 | 0.077662 | 1.2984 | Cap-Tons/1000 sf | 1497.75 | 1838.25 | 1838.25 | 0.2833 | 0.34555 | 0.34555 | 0 | 0 | 0 | 1497.75 | 1838.25 | 1838.25 | 0.2833 | 0.34555 | 0.34555 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.77022 | 0.052331 | 0.87488 | Cap-Tons/1000 sf | 1304.3109 | 1545.3109 | 1545.3109 | 0.404 | 0.47255 | 0.47255 | 0 | 0 | 0 | 1304.3109 | 1545.3109 | 1545.3109 | 0.404 | 0.47255 | 0.47255 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.37551 | 0.02389 | 0.3994 | Cap-Tons/1000 sf | 1204.75 | 1434.25 | 1434.25 | 0.20968 | 0.25178 | 0.25178 | 0 | 0 | 0 | 1204.75 | 1434.25 | 1434.25 | 0.20968 | 0.25178 | 0.25178 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.40936 | 0.027814 | 0.46499 | Cap-Tons/1000 sf | 1256 | 1520 | 1520 | 0.30443 | 0.36483 | 0.36483 | 0 | 0 | 0 | 1256 | 1520 | 1520 | 0.30443 | 0.36483 | 0.36483 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTS | RETAIL - SMALL | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.45321 | 0.030792 | 0.51479 | Cap-Tons/1000 sf | 1153.75 | 1369.25 | 1369.25 | 0.26834 | 0.31669 | 0.31669 | 0 | 0 | 0 | 1153.75 | 1369.25 | 1369.25 | 0.26834 | 0.31669 | 0.31669 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | SCN | STORAGE - CONDITIONED | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.24791 | 0.016844 | 0.2816 | Cap-Tons/1000 sf | 829 | 1028.5 | 1028.5 | 0.1749 | 0.2202 | 0.2202 | 0 | 0 | 0 | 829 | 1028.5 | 1028.5 | 0.1749 | 0.2202 | 0.2202 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ASM | ASSEMBLY | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.93897 | 0.063797 | 1.0666 | Cap-Tons/1000 sf | 809.1 | 1348.5 | 1040.6 | 0.34961 | 0.58269 | 0.41291 | 0 | 0 | 0 | 809.1 | 1348.5 | 1040.6 | 0.34961 | 0.58269 | 0.41291 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.54701 | 0.037166 | 0.62134 | Cap-Tons/1000 sf | 706.2 | 1177 | 928.2 | 0.20952 | 0.3492 | 0.25132 | 0 | 0 | 0 | 706.2 | 1177 | 928.2 | 0.20952 | 0.3492 | 0.25132 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.621 | 0.042193 | 0.70538 | Cap-Tons/1000 sf | 622.95 | 996.25 | 773.4 | 0.11606 | 0.18522 | 0.13501 | 0 | 0 | 0 | 622.95 | 996.25 | 773.4 | 0.11606 | 0.18522 | 0.13501 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.79463 | 0.050555 | 0.84519 | Cap-Tons/1000 sf | 746.4 | 1244 | 1060.4 | 0.27606 | 0.4601 | 0.34376 | 0 | 0 | 0 | 746.4 | 1244 | 1060.4 | 0.27606 | 0.4601 | 0.34376 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.61214 | 0.041591 | 0.69532 | Cap-Tons/1000 sf | 768 | 1192.5 | 932 | 0.12989 | 0.2011 | 0.14839 | 0 | 0 | 0 | 768 | 1192.5 | 932 | 0.12989 | 0.2011 | 0.14839 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EUN | EDUCATION - UNIVERSITY | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.58484 | 0.037208 | 0.62204 | Cap-Tons/1000 sf | 829.65 | 1382.75 | 1067.15 | 0.23599 | 0.39331 | 0.28204 | 0 | 0 | 0 | 829.65 | 1382.75 | 1067.15 | 0.23599 | 0.39331 | 0.28204 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | GRO | GROCERY | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 1.0397 | 0.066148 | 1.1059 | Cap-Tons/1000 sf | 987.05 | 1599.25 | 1339.05 | 0.32591 | 0.52788 | 0.37651 | 0 | 0 | 0 | 987.05 | 1599.25 | 1339.05 | 0.32591 | 0.52788 | 0.37651 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.77621 | 0.052738 | 0.88169 | Cap-Tons/1000 sf | 1440.45 | 2400.75 | 1834.95 | 0.27231 | 0.45385 | 0.32201 | 0 | 0 | 0 | 1440.45 | 2400.75 | 1834.95 | 0.27231 | 0.45385 | 0.32201 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HTL | LODGING - HOTEL | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.46549 | 0.029615 | 0.49511 | Cap-Tons/1000 sf | 1365.15 | 2275.25 | 1733.65 | 0.32132 | 0.53554 | 0.37687 | 0 | 0 | 0 | 1365.15 | 2275.25 | 1733.65 | 0.32132 | 0.53554 | 0.37687 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | MTL | LODGING - MOTEL | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.46549 | 0.029615 | 0.49511 | Cap-Tons/1000 sf | 1365.15 | 2275.25 | 1733.65 | 0.32132 | 0.53554 | 0.37687 | 0 | 0 | 0 | 1365.15 | 2275.25 | 1733.65 | 0.32132 | 0.53554 | 0.37687 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.82895 | 0.052738 | 0.88169 | Cap-Tons/1000 sf | 1120.2 | 1867 | 1503.2 | 0.28256 | 0.47094 | 0.33296 | 0 | 0 | 0 | 1120.2 | 1867 | 1503.2 | 0.28256 | 0.47094 | 0.33296 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFL | OFFICE - LARGE | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.61708 | 0.039259 | 0.65634 | Cap-Tons/1000 sf | 861.336 | 1435.5599 | 1041.336 | 0.31591 | 0.52652 | 0.36746 | 0 | 0 | 0 | 861.336 | 1435.5599 | 1041.336 | 0.31591 | 0.52652 | 0.36746 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFS | OFFICE - SMALL | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.65556 | 0.044541 | 0.74464 | Cap-Tons/1000 sf | 701.1 | 1168.5 | 863 | 0.29823 | 0.49705 | 0.35028 | 0 | 0 | 0 | 701.1 | 1168.5 | 863 | 0.29823 | 0.49705 | 0.35028 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 1.143 | 0.077662 | 1.2984 | Cap-Tons/1000 sf | 1103.45 | 1838.25 | 1451.45 | 0.33503 | 0.55811 | 0.39278 | 0 | 0 | 0 | 1103.45 | 1838.25 | 1451.45 | 0.33503 | 0.55811 | 0.39278 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.77022 | 0.052331 | 0.87488 | Cap-Tons/1000 sf | 956.2487 | 1545.3109 | 1199.2487 | 0.44995 | 0.7264 | 0.51915 | 0 | 0 | 0 | 956.2487 | 1545.3109 | 1199.2487 | 0.44995 | 0.7264 | 0.51915 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 1.2308 | 0.068392 | 1.3676 | Cap-Tons/1000 sf | 1102.95 | 1838.25 | 1435.95 | 0.2561 | 0.42683 | 0.307 | 0 | 0 | 0 | 1102.95 | 1838.25 | 1435.95 | 0.2561 | 0.42683 | 0.307 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.81237 | 0.04514 | 0.90265 | Cap-Tons/1000 sf | 927.1865 | 1545.3109 | 1156.1865 | 0.31223 | 0.52039 | 0.36263 | 0 | 0 | 0 | 927.1865 | 1545.3109 | 1156.1865 | 0.31223 | 0.52039 | 0.36263 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.37152 | 0.019557 | 0.39108 | Cap-Tons/1000 sf | 860.55 | 1434.25 | 1086.55 | 0.23716 | 0.39527 | 0.28836 | 0 | 0 | 0 | 860.55 | 1434.25 | 1086.55 | 0.23716 | 0.39527 | 0.28836 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.37551 | 0.02389 | 0.3994 | Cap-Tons/1000 sf | 860.55 | 1434.25 | 1085.05 | 0.35846 | 0.59743 | 0.40976 | 0 | 0 | 0 | 860.55 | 1434.25 | 1085.05 | 0.35846 | 0.59743 | 0.40976 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.40936 | 0.027814 | 0.46499 | Cap-Tons/1000 sf | 912 | 1520 | 1169.5 | 0.3615 | 0.60249 | 0.4204 | 0 | 0 | 0 | 912 | 1520 | 1169.5 | 0.3615 | 0.60249 | 0.4204 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTS | RETAIL - SMALL | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.45321 | 0.030792 | 0.51479 | Cap-Tons/1000 sf | 821.55 | 1369.25 | 1044.05 | 0.35292 | 0.5882 | 0.40832 | 0 | 0 | 0 | 821.55 | 1369.25 | 1044.05 | 0.35292 | 0.5882 | 0.40832 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | SCN | STORAGE - CONDITIONED | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.24791 | 0.016844 | 0.2816 | Cap-Tons/1000 sf | 638 | 1028.5 | 856.5 | 0.29381 | 0.47259 | 0.34656 | 0 | 0 | 0 | 638 | 1028.5 | 856.5 | 0.29381 | 0.47259 | 0.34656 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.79463 | 0.050555 | 0.84519 | Cap-Tons/1000 sf | 990.5 | 1244 | 1244 | 0.16824 | 0.21124 | 0.21124 | 0 | 0 | 0 | 990.5 | 1244 | 1244 | 0.16824 | 0.21124 | 0.21124 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.61214 | 0.041591 | 0.69532 | Cap-Tons/1000 sf | 1041.5 | 1192.5 | 1192.5 | 0 | 0 | 0 | 0 | 0 | 0 | 1041.5 | 1192.5 | 1192.5 | 0 | 0 | 0 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EUN | EDUCATION - UNIVERSITY | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.58484 | 0.037208 | 0.62204 | Cap-Tons/1000 sf | 1159.25 | 1382.75 | 1382.75 | 0.23499 | 0.27574 | 0.27574 | 0 | 0 | 0 | 1159.25 | 1382.75 | 1382.75 | 0.23499 | 0.27574 | 0.27574 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | GRO | GROCERY | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 1.0397 | 0.066148 | 1.1059 | Cap-Tons/1000 sf | 1247.25 | 1599.25 | 1599.25 | 0.17771 | 0.23116 | 0.23116 | 0 | 0 | 0 | 1247.25 | 1599.25 | 1599.25 | 0.17771 | 0.23116 | 0.23116 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.77621 | 0.052738 | 0.88169 | Cap-Tons/1000 sf | 2004.25 | 2400.75 | 2400.75 | 0.2377 | 0.28465 | 0.28465 | 0 | 0 | 0 | 2004.25 | 2400.75 | 2400.75 | 0.2377 | 0.28465 | 0.28465 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HTL | LODGING - HOTEL | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.46549 | 0.029615 | 0.49511 | Cap-Tons/1000 sf | 1917.75 | 2275.25 | 2275.25 | 0.28874 | 0.33924 | 0.33924 | 0 | 0 | 0 | 1917.75 | 2275.25 | 2275.25 | 0.28874 | 0.33924 | 0.33924 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | MTL | LODGING - MOTEL | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.46549 | 0.029615 | 0.49511 | Cap-Tons/1000 sf | 1917.75 | 2275.25 | 2275.25 | 0.28874 | 0.33924 | 0.33924 | 0 | 0 | 0 | 1917.75 | 2275.25 | 2275.25 | 0.28874 | 0.33924 | 0.33924 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.82895 | 0.052738 | 0.88169 | Cap-Tons/1000 sf | 1484 | 1867 | 1867 | 0.17439 | 0.21969 | 0.21969 | 0 | 0 | 0 | 1484 | 1867 | 1867 | 0.17439 | 0.21969 | 0.21969 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFL | OFFICE - LARGE | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.61708 | 0.039259 | 0.65634 | Cap-Tons/1000 sf | 1274.7099 | 1435.5599 | 1435.5599 | 0.46424 | 0.51664 | 0.51664 | 0 | 0 | 0 | 1274.7099 | 1435.5599 | 1435.5599 | 0.46424 | 0.51664 | 0.51664 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFS | OFFICE - SMALL | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.65556 | 0.044541 | 0.74464 | Cap-Tons/1000 sf | 1012.65 | 1168.5 | 1168.5 | 0.34998 | 0.40053 | 0.40053 | 0 | 0 | 0 | 1012.65 | 1168.5 | 1168.5 | 0.34998 | 0.40053 | 0.40053 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 1.143 | 0.077662 | 1.2984 | Cap-Tons/1000 sf | 1482.75 | 1838.25 | 1838.25 | 0.21259 | 0.26304 | 0.26304 | 0 | 0 | 0 | 1482.75 | 1838.25 | 1838.25 | 0.21259 | 0.26304 | 0.26304 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.77022 | 0.052331 | 0.87488 | Cap-Tons/1000 sf | 1305.3109 | 1545.3109 | 1545.3109 | 0.35952 | 0.42447 | 0.42447 | 0 | 0 | 0 | 1305.3109 | 1545.3109 | 1545.3109 | 0.35952 | 0.42447 | 0.42447 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.37551 | 0.02389 | 0.3994 | Cap-Tons/1000 sf | 1207.25 | 1434.25 | 1434.25 | 0.21897 | 0.25672 | 0.25672 | 0 | 0 | 0 | 1207.25 | 1434.25 | 1434.25 | 0.21897 | 0.25672 | 0.25672 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.40936 | 0.027814 | 0.46499 | Cap-Tons/1000 sf | 1257.5 | 1520 | 1520 | 0.23638 | 0.28363 | 0.28363 | 0 | 0 | 0 | 1257.5 | 1520 | 1520 | 0.23638 | 0.28363 | 0.28363 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTS | RETAIL - SMALL | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.45321 | 0.030792 | 0.51479 | Cap-Tons/1000 sf | 1143.75 | 1369.25 | 1369.25 | 0.23052 | 0.27342 | 0.27342 | 0 | 0 | 0 | 1143.75 | 1369.25 | 1369.25 | 0.23052 | 0.27342 | 0.27342 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | SCN | STORAGE - CONDITIONED | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.24791 | 0.016844 | 0.2816 | Cap-Tons/1000 sf | 822 | 1028.5 | 1028.5 | 0.17193 | 0.21578 | 0.21578 | 0 | 0 | 0 | 822 | 1028.5 | 1028.5 | 0.17193 | 0.21578 | 0.21578 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ASM | ASSEMBLY | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.94349 | 0.052426 | 1.0483 | Cap-Tons/1000 sf | 809.1 | 1348.5 | 1026.6 | 0.25182 | 0.4197 | 0.30067 | 0 | 0 | 0 | 809.1 | 1348.5 | 1026.6 | 0.25182 | 0.4197 | 0.30067 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.54668 | 0.030377 | 0.60743 | Cap-Tons/1000 sf | 706.2 | 1177 | 891.3 | 0.16256 | 0.27094 | 0.19966 | 0 | 0 | 0 | 706.2 | 1177 | 891.3 | 0.16256 | 0.27094 | 0.19966 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.66214 | 0.036793 | 0.73573 | Cap-Tons/1000 sf | 597.75 | 996.25 | 722.35 | 0.039957 | 0.066595 | 0.049322 | 0 | 0 | 0 | 597.75 | 996.25 | 722.35 | 0.039957 | 0.066595 | 0.049322 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.82639 | 0.043502 | 0.86989 | Cap-Tons/1000 sf | 746.4 | 1244 | 971.9 | 0.18485 | 0.30809 | 0.24145 | 0 | 0 | 0 | 746.4 | 1244 | 971.9 | 0.18485 | 0.30809 | 0.24145 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.64424 | 0.035798 | 0.71584 | Cap-Tons/1000 sf | 738 | 1192.5 | 870.55 | 0.022686 | 0.036605 | 0.026851 | 0 | 0 | 0 | 738 | 1192.5 | 870.55 | 0.022686 | 0.036605 | 0.026851 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EUN | EDUCATION - UNIVERSITY | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.58045 | 0.030556 | 0.61101 | Cap-Tons/1000 sf | 829.65 | 1382.75 | 1050.15 | 0.17017 | 0.28362 | 0.21197 | 0 | 0 | 0 | 829.65 | 1382.75 | 1050.15 | 0.17017 | 0.28362 | 0.21197 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | GRO | GROCERY | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 1.0681 | 0.056226 | 1.1243 | Cap-Tons/1000 sf | 967.55 | 1599.25 | 1308.55 | 0.27173 | 0.44924 | 0.31908 | 0 | 0 | 0 | 967.55 | 1599.25 | 1308.55 | 0.27173 | 0.44924 | 0.31908 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.78906 | 0.043846 | 0.87675 | Cap-Tons/1000 sf | 1440.45 | 2400.75 | 1836.95 | 0.21454 | 0.35757 | 0.26319 | 0 | 0 | 0 | 1440.45 | 2400.75 | 1836.95 | 0.21454 | 0.35757 | 0.26319 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HTL | LODGING - HOTEL | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.46601 | 0.024532 | 0.49055 | Cap-Tons/1000 sf | 1365.15 | 2275.25 | 1748.65 | 0.23234 | 0.38723 | 0.28444 | 0 | 0 | 0 | 1365.15 | 2275.25 | 1748.65 | 0.23234 | 0.38723 | 0.28444 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | MTL | LODGING - MOTEL | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.46601 | 0.024532 | 0.49055 | Cap-Tons/1000 sf | 1365.15 | 2275.25 | 1748.65 | 0.23234 | 0.38723 | 0.28444 | 0 | 0 | 0 | 1365.15 | 2275.25 | 1748.65 | 0.23234 | 0.38723 | 0.28444 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.83291 | 0.043846 | 0.87675 | Cap-Tons/1000 sf | 1120.2 | 1867 | 1501.2 | 0.22023 | 0.36705 | 0.27038 | 0 | 0 | 0 | 1120.2 | 1867 | 1501.2 | 0.22023 | 0.36705 | 0.27038 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFL | OFFICE - LARGE | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.60844 | 0.032029 | 0.64047 | Cap-Tons/1000 sf | 861.336 | 1435.5599 | 1024.686 | 0.26322 | 0.43869 | 0.31432 | 0 | 0 | 0 | 861.336 | 1435.5599 | 1024.686 | 0.26322 | 0.43869 | 0.31432 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFS | OFFICE - SMALL | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.69988 | 0.03889 | 0.77766 | Cap-Tons/1000 sf | 701.1 | 1168.5 | 857.65 | 0.24355 | 0.40592 | 0.29525 | 0 | 0 | 0 | 701.1 | 1168.5 | 857.65 | 0.24355 | 0.40592 | 0.29525 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.42671 | 0.023711 | 0.47413 | Cap-Tons/1000 sf | 912 | 1520 | 1179 | 0.2366 | 0.39433 | 0.2879 | 0 | 0 | 0 | 912 | 1520 | 1179 | 0.2366 | 0.39433 | 0.2879 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTS | RETAIL - SMALL | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.46376 | 0.02577 | 0.5153 | Cap-Tons/1000 sf | 821.55 | 1369.25 | 1042.55 | 0.23916 | 0.39861 | 0.29116 | 0 | 0 | 0 | 821.55 | 1369.25 | 1042.55 | 0.23916 | 0.39861 | 0.29116 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | SCN | STORAGE - CONDITIONED | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.25401 | 0.014114 | 0.28224 | Cap-Tons/1000 sf | 628.5 | 1028.5 | 826.5 | 0.2685 | 0.43849 | 0.3199 | 0 | 0 | 0 | 628.5 | 1028.5 | 826.5 | 0.2685 | 0.43849 | 0.3199 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | Existing | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.81237 | 0.04514 | 0.90265 | Cap-Tons/1000 sf | 927.1865 | 1545.3109 | 1138.0365 | 0.33226 | 0.55376 | 0.37966 | 0 | 0 | 0 | 927.1865 | 1545.3109 | 1138.0365 | 0.33226 | 0.55376 | 0.37966 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | Existing | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.37152 | 0.019557 | 0.39108 | Cap-Tons/1000 sf | 860.55 | 1434.25 | 1074.35 | 0.23515 | 0.39191 | 0.28655 | 0 | 0 | 0 | 860.55 | 1434.25 | 1074.35 | 0.23515 | 0.39191 | 0.28655 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | Existing | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.42671 | 0.023711 | 0.47413 | Cap-Tons/1000 sf | 912 | 1520 | 1169 | 0.24009 | 0.40014 | 0.29324 | 0 | 0 | 0 | 912 | 1520 | 1169 | 0.24009 | 0.40014 | 0.29324 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.37152 | 0.019557 | 0.39108 | Cap-Tons/1000 sf | 860.55 | 1434.25 | 1083.55 | 0.23851 | 0.39751 | 0.28111 | 0 | 0 | 0 | 860.55 | 1434.25 | 1083.55 | 0.23851 | 0.39751 | 0.28111 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.42671 | 0.023711 | 0.47413 | Cap-Tons/1000 sf | 912 | 1520 | 1177 | 0.24152 | 0.40254 | 0.28512 | 0 | 0 | 0 | 912 | 1520 | 1177 | 0.24152 | 0.40254 | 0.28512 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTS | RETAIL - SMALL | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.46376 | 0.02577 | 0.5153 | Cap-Tons/1000 sf | 821.55 | 1369.25 | 1039.55 | 0.24152 | 0.40254 | 0.28522 | 0 | 0 | 0 | 821.55 | 1369.25 | 1039.55 | 0.24152 | 0.40254 | 0.28522 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 1.2308 | 0.068392 | 1.3676 | Cap-Tons/1000 sf | 1102.95 | 1838.25 | 1427.95 | 0.27475 | 0.45792 | 0.30525 | 0 | 0 | 0 | 1102.95 | 1838.25 | 1427.95 | 0.27475 | 0.45792 | 0.30525 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.81237 | 0.04514 | 0.90265 | Cap-Tons/1000 sf | 927.1865 | 1545.3109 | 1158.1865 | 0.30766 | 0.51276 | 0.33076 | 0 | 0 | 0 | 927.1865 | 1545.3109 | 1158.1865 | 0.30766 | 0.51276 | 0.33076 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.37152 | 0.019557 | 0.39108 | Cap-Tons/1000 sf | 860.55 | 1434.25 | 1073.55 | 0.24092 | 0.40153 | 0.27132 | 0 | 0 | 0 | 860.55 | 1434.25 | 1073.55 | 0.24092 | 0.40153 | 0.27132 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EUN | EDUCATION - UNIVERSITY | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.58045 | 0.030556 | 0.61101 | Cap-Tons/1000 sf | 829.65 | 1382.75 | 1057.65 | 0.20317 | 0.33862 | 0.23512 | 0 | 0 | 0 | 829.65 | 1382.75 | 1057.65 | 0.20317 | 0.33862 | 0.23512 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | GRO | GROCERY | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 1.0681 | 0.056226 | 1.1243 | Cap-Tons/1000 sf | 959.55 | 1599.25 | 1298.55 | 0.27406 | 0.45677 | 0.32656 | 0 | 0 | 0 | 959.55 | 1599.25 | 1298.55 | 0.27406 | 0.45677 | 0.32656 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.78906 | 0.043846 | 0.87675 | Cap-Tons/1000 sf | 1440.45 | 2400.75 | 1836.95 | 0.26122 | 0.43536 | 0.30197 | 0 | 0 | 0 | 1440.45 | 2400.75 | 1836.95 | 0.26122 | 0.43536 | 0.30197 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ASM | ASSEMBLY | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.94349 | 0.052426 | 1.0483 | Cap-Tons/1000 sf | 1130.5 | 1348.5 | 1348.5 | 0.3048 | 0.3527 | 0.3527 | 0 | 0 | 0 | 1130.5 | 1348.5 | 1348.5 | 0.3048 | 0.3527 | 0.3527 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.54668 | 0.030377 | 0.60743 | Cap-Tons/1000 sf | 987.5 | 1177 | 1177 | 0.25815 | 0.303 | 0.303 | 0 | 0 | 0 | 987.5 | 1177 | 1177 | 0.25815 | 0.303 | 0.303 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.66214 | 0.036793 | 0.73573 | Cap-Tons/1000 sf | 868.8 | 996.25 | 996.25 | 0.35093 | 0.39883 | 0.39883 | 0 | 0 | 0 | 868.8 | 996.25 | 996.25 | 0.35093 | 0.39883 | 0.39883 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.82639 | 0.043502 | 0.86989 | Cap-Tons/1000 sf | 1072 | 1244 | 1244 | 0.35249 | 0.40859 | 0.40859 | 0 | 0 | 0 | 1072 | 1244 | 1244 | 0.35249 | 0.40859 | 0.40859 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.64424 | 0.035798 | 0.71584 | Cap-Tons/1000 sf | 1057 | 1192.5 | 1192.5 | 0.40567 | 0.45417 | 0.45417 | 0 | 0 | 0 | 1057 | 1192.5 | 1192.5 | 0.40567 | 0.45417 | 0.45417 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EUN | EDUCATION - UNIVERSITY | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.58045 | 0.030556 | 0.61101 | Cap-Tons/1000 sf | 1170.75 | 1382.75 | 1382.75 | 0.35189 | 0.40089 | 0.40089 | 0 | 0 | 0 | 1170.75 | 1382.75 | 1382.75 | 0.35189 | 0.40089 | 0.40089 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | GRO | GROCERY | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 1.0681 | 0.056226 | 1.1243 | Cap-Tons/1000 sf | 1266.75 | 1599.25 | 1599.25 | 0.19598 | 0.25108 | 0.25108 | 0 | 0 | 0 | 1266.75 | 1599.25 | 1599.25 | 0.19598 | 0.25108 | 0.25108 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.78906 | 0.043846 | 0.87675 | Cap-Tons/1000 sf | 1999.75 | 2400.75 | 2400.75 | 0.25512 | 0.30107 | 0.30107 | 0 | 0 | 0 | 1999.75 | 2400.75 | 2400.75 | 0.25512 | 0.30107 | 0.30107 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HTL | LODGING - HOTEL | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.46601 | 0.024532 | 0.49055 | Cap-Tons/1000 sf | 1894.75 | 2275.25 | 2275.25 | 0.2816 | 0.32975 | 0.32975 | 0 | 0 | 0 | 1894.75 | 2275.25 | 2275.25 | 0.2816 | 0.32975 | 0.32975 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | MTL | LODGING - MOTEL | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.46601 | 0.024532 | 0.49055 | Cap-Tons/1000 sf | 1894.75 | 2275.25 | 2275.25 | 0.2816 | 0.32975 | 0.32975 | 0 | 0 | 0 | 1894.75 | 2275.25 | 2275.25 | 0.2816 | 0.32975 | 0.32975 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.83291 | 0.043846 | 0.87675 | Cap-Tons/1000 sf | 1487 | 1867 | 1867 | 0.2017 | 0.24985 | 0.24985 | 0 | 0 | 0 | 1487 | 1867 | 1867 | 0.2017 | 0.24985 | 0.24985 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFL | OFFICE - LARGE | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.60844 | 0.032029 | 0.64047 | Cap-Tons/1000 sf | 1281.2099 | 1435.5599 | 1435.5599 | 0.53841 | 0.58751 | 0.58751 | 0 | 0 | 0 | 1281.2099 | 1435.5599 | 1435.5599 | 0.53841 | 0.58751 | 0.58751 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFS | OFFICE - SMALL | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.69988 | 0.03889 | 0.77766 | Cap-Tons/1000 sf | 1012.35 | 1168.5 | 1168.5 | 0.42986 | 0.48141 | 0.48141 | 0 | 0 | 0 | 1012.35 | 1168.5 | 1168.5 | 0.42986 | 0.48141 | 0.48141 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 1.2308 | 0.068392 | 1.3676 | Cap-Tons/1000 sf | 1496.75 | 1838.25 | 1838.25 | 0.22205 | 0.271 | 0.271 | 0 | 0 | 0 | 1496.75 | 1838.25 | 1838.25 | 0.22205 | 0.271 | 0.271 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.81237 | 0.04514 | 0.90265 | Cap-Tons/1000 sf | 1313.8109 | 1545.3109 | 1545.3109 | 0.38381 | 0.43906 | 0.43906 | 0 | 0 | 0 | 1313.8109 | 1545.3109 | 1545.3109 | 0.38381 | 0.43906 | 0.43906 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.37152 | 0.019557 | 0.39108 | Cap-Tons/1000 sf | 1206.75 | 1434.25 | 1434.25 | 0.28707 | 0.33402 | 0.33402 | 0 | 0 | 0 | 1206.75 | 1434.25 | 1434.25 | 0.28707 | 0.33402 | 0.33402 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.42671 | 0.023711 | 0.47413 | Cap-Tons/1000 sf | 1253.5 | 1520 | 1520 | 0.24849 | 0.29684 | 0.29684 | 0 | 0 | 0 | 1253.5 | 1520 | 1520 | 0.24849 | 0.29684 | 0.29684 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTS | RETAIL - SMALL | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.46376 | 0.02577 | 0.5153 | Cap-Tons/1000 sf | 1148.25 | 1369.25 | 1369.25 | 0.3011 | 0.35085 | 0.35085 | 0 | 0 | 0 | 1148.25 | 1369.25 | 1369.25 | 0.3011 | 0.35085 | 0.35085 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | SCN | STORAGE - CONDITIONED | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.25401 | 0.014114 | 0.28224 | Cap-Tons/1000 sf | 828.5 | 1028.5 | 1028.5 | 0.20809 | 0.25624 | 0.25624 | 0 | 0 | 0 | 828.5 | 1028.5 | 1028.5 | 0.20809 | 0.25624 | 0.25624 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ASM | ASSEMBLY | Existing | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.94349 | 0.052426 | 1.0483 | Cap-Tons/1000 sf | 809.1 | 1348.5 | 1007.45 | 0.29219 | 0.48698 | 0.33964 | 0 | 0 | 0 | 809.1 | 1348.5 | 1007.45 | 0.29219 | 0.48698 | 0.33964 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | Existing | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.54668 | 0.030377 | 0.60743 | Cap-Tons/1000 sf | 706.2 | 1177 | 883.25 | 0.23833 | 0.39722 | 0.28633 | 0 | 0 | 0 | 706.2 | 1177 | 883.25 | 0.23833 | 0.39722 | 0.28633 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | Existing | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.66214 | 0.036793 | 0.73573 | Cap-Tons/1000 sf | 597.75 | 996.25 | 715.65 | 0.33969 | 0.56615 | 0.38719 | 0 | 0 | 0 | 597.75 | 996.25 | 715.65 | 0.33969 | 0.56615 | 0.38719 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | Existing | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.82639 | 0.043502 | 0.86989 | Cap-Tons/1000 sf | 762.1 | 1244 | 948.1 | 0.40359 | 0.65671 | 0.46389 | 0 | 0 | 0 | 762.1 | 1244 | 948.1 | 0.40359 | 0.65671 | 0.46389 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | Existing | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.64424 | 0.035798 | 0.71584 | Cap-Tons/1000 sf | 727 | 1192.5 | 853.6 | 0.42367 | 0.69329 | 0.47332 | 0 | 0 | 0 | 727 | 1192.5 | 853.6 | 0.42367 | 0.69329 | 0.47332 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EUN | EDUCATION - UNIVERSITY | Existing | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.58045 | 0.030556 | 0.61101 | Cap-Tons/1000 sf | 829.65 | 1382.75 | 1047.05 | 0.23497 | 0.39162 | 0.28767 | 0 | 0 | 0 | 829.65 | 1382.75 | 1047.05 | 0.23497 | 0.39162 | 0.28767 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | GRO | GROCERY | Existing | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 1.0681 | 0.056226 | 1.1243 | Cap-Tons/1000 sf | 980.55 | 1599.25 | 1325.05 | 0.28792 | 0.47009 | 0.33252 | 0 | 0 | 0 | 980.55 | 1599.25 | 1325.05 | 0.28792 | 0.47009 | 0.33252 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | Existing | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.78906 | 0.043846 | 0.87675 | Cap-Tons/1000 sf | 1440.45 | 2400.75 | 1827.95 | 0.21377 | 0.35628 | 0.26197 | 0 | 0 | 0 | 1440.45 | 2400.75 | 1827.95 | 0.21377 | 0.35628 | 0.26197 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HTL | LODGING - HOTEL | Existing | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.46601 | 0.024532 | 0.49055 | Cap-Tons/1000 sf | 1365.15 | 2275.25 | 1739.65 | 0.22479 | 0.37464 | 0.27794 | 0 | 0 | 0 | 1365.15 | 2275.25 | 1739.65 | 0.22479 | 0.37464 | 0.27794 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | MTL | LODGING - MOTEL | Existing | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.46601 | 0.024532 | 0.49055 | Cap-Tons/1000 sf | 1365.15 | 2275.25 | 1739.65 | 0.22479 | 0.37464 | 0.27794 | 0 | 0 | 0 | 1365.15 | 2275.25 | 1739.65 | 0.22479 | 0.37464 | 0.27794 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | Existing | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.83291 | 0.043846 | 0.87675 | Cap-Tons/1000 sf | 1120.2 | 1867 | 1497.7 | 0.22029 | 0.36715 | 0.26944 | 0 | 0 | 0 | 1120.2 | 1867 | 1497.7 | 0.22029 | 0.36715 | 0.26944 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFL | OFFICE - LARGE | Existing | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.60844 | 0.032029 | 0.64047 | Cap-Tons/1000 sf | 861.336 | 1435.5599 | 1025.886 | 0.26896 | 0.44826 | 0.32121 | 0 | 0 | 0 | 861.336 | 1435.5599 | 1025.886 | 0.26896 | 0.44826 | 0.32121 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFS | OFFICE - SMALL | Existing | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.69988 | 0.03889 | 0.77766 | Cap-Tons/1000 sf | 701.1 | 1168.5 | 854.5 | 0.24381 | 0.40635 | 0.29661 | 0 | 0 | 0 | 701.1 | 1168.5 | 854.5 | 0.24381 | 0.40635 | 0.29661 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | Existing | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 1.2308 | 0.068392 | 1.3676 | Cap-Tons/1000 sf | 1102.95 | 1838.25 | 1427.45 | 0.259 | 0.43166 | 0.30695 | 0 | 0 | 0 | 1102.95 | 1838.25 | 1427.45 | 0.259 | 0.43166 | 0.30695 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTS | RETAIL - SMALL | Existing | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.46376 | 0.02577 | 0.5153 | Cap-Tons/1000 sf | 821.55 | 1369.25 | 1038.05 | 0.2326 | 0.38767 | 0.2843 | 0 | 0 | 0 | 821.55 | 1369.25 | 1038.05 | 0.2326 | 0.38767 | 0.2843 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | New | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.66214 | 0.036793 | 0.73573 | Cap-Tons/1000 sf | 880.1 | 996.25 | 996.25 | 0.42889 | 0.47714 | 0.47714 | 0 | 0 | 0 | 880.1 | 996.25 | 996.25 | 0.42889 | 0.47714 | 0.47714 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | New | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.82639 | 0.043502 | 0.86989 | Cap-Tons/1000 sf | 1098.5 | 1244 | 1244 | 0.38771 | 0.43821 | 0.43821 | 0 | 0 | 0 | 1098.5 | 1244 | 1244 | 0.38771 | 0.43821 | 0.43821 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | New | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.64424 | 0.035798 | 0.71584 | Cap-Tons/1000 sf | 1065 | 1192.5 | 1192.5 | 0.48059 | 0.53109 | 0.53109 | 0 | 0 | 0 | 1065 | 1192.5 | 1192.5 | 0.48059 | 0.53109 | 0.53109 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EUN | EDUCATION - UNIVERSITY | New | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.58045 | 0.030556 | 0.61101 | Cap-Tons/1000 sf | 1179.75 | 1382.75 | 1382.75 | 0.62109 | 0.68109 | 0.68109 | 0 | 0 | 0 | 1179.75 | 1382.75 | 1382.75 | 0.62109 | 0.68109 | 0.68109 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | GRO | GROCERY | New | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 1.0681 | 0.056226 | 1.1243 | Cap-Tons/1000 sf | 1259.75 | 1599.25 | 1599.25 | 0.20494 | 0.26299 | 0.26299 | 0 | 0 | 0 | 1259.75 | 1599.25 | 1599.25 | 0.20494 | 0.26299 | 0.26299 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | New | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.78906 | 0.043846 | 0.87675 | Cap-Tons/1000 sf | 2006.75 | 2400.75 | 2400.75 | 0.27774 | 0.32444 | 0.32444 | 0 | 0 | 0 | 2006.75 | 2400.75 | 2400.75 | 0.27774 | 0.32444 | 0.32444 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HTL | LODGING - HOTEL | New | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.46601 | 0.024532 | 0.49055 | Cap-Tons/1000 sf | 1908.25 | 2275.25 | 2275.25 | 0.35736 | 0.40936 | 0.40936 | 0 | 0 | 0 | 1908.25 | 2275.25 | 2275.25 | 0.35736 | 0.40936 | 0.40936 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | MTL | LODGING - MOTEL | New | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.46601 | 0.024532 | 0.49055 | Cap-Tons/1000 sf | 1908.25 | 2275.25 | 2275.25 | 0.35736 | 0.40936 | 0.40936 | 0 | 0 | 0 | 1908.25 | 2275.25 | 2275.25 | 0.35736 | 0.40936 | 0.40936 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | New | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.83291 | 0.043846 | 0.87675 | Cap-Tons/1000 sf | 1485.5 | 1867 | 1867 | 0.21087 | 0.26072 | 0.26072 | 0 | 0 | 0 | 1485.5 | 1867 | 1867 | 0.21087 | 0.26072 | 0.26072 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFL | OFFICE - LARGE | New | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.60844 | 0.032029 | 0.64047 | Cap-Tons/1000 sf | 1282.2599 | 1435.5599 | 1435.5599 | 0.64218 | 0.69468 | 0.69468 | 0 | 0 | 0 | 1282.2599 | 1435.5599 | 1435.5599 | 0.64218 | 0.69468 | 0.69468 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFS | OFFICE - SMALL | New | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.69988 | 0.03889 | 0.77766 | Cap-Tons/1000 sf | 1018 | 1168.5 | 1168.5 | 0.55018 | 0.60473 | 0.60473 | 0 | 0 | 0 | 1018 | 1168.5 | 1168.5 | 0.55018 | 0.60473 | 0.60473 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | New | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 1.2308 | 0.068392 | 1.3676 | Cap-Tons/1000 sf | 1517.75 | 1838.25 | 1838.25 | 0.2543 | 0.30395 | 0.30395 | 0 | 0 | 0 | 1517.75 | 1838.25 | 1838.25 | 0.2543 | 0.30395 | 0.30395 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | New | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.81237 | 0.04514 | 0.90265 | Cap-Tons/1000 sf | 1340.8109 | 1545.3109 | 1545.3109 | 0.42963 | 0.48353 | 0.48353 | 0 | 0 | 0 | 1340.8109 | 1545.3109 | 1545.3109 | 0.42963 | 0.48353 | 0.48353 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | New | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.37152 | 0.019557 | 0.39108 | Cap-Tons/1000 sf | 1223.65 | 1434.25 | 1434.25 | 0.49559 | 0.54819 | 0.54819 | 0 | 0 | 0 | 1223.65 | 1434.25 | 1434.25 | 0.49559 | 0.54819 | 0.54819 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | New | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.42671 | 0.023711 | 0.47413 | Cap-Tons/1000 sf | 1262.5 | 1520 | 1520 | 0.3085 | 0.3604 | 0.3604 | 0 | 0 | 0 | 1262.5 | 1520 | 1520 | 0.3085 | 0.3604 | 0.3604 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTS | RETAIL - SMALL | New | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.46376 | 0.02577 | 0.5153 | Cap-Tons/1000 sf | 1151.75 | 1369.25 | 1369.25 | 0.33961 | 0.39121 | 0.39121 | 0 | 0 | 0 | 1151.75 | 1369.25 | 1369.25 | 0.33961 | 0.39121 | 0.39121 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | SCN | STORAGE - CONDITIONED | New | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.25401 | 0.014114 | 0.28224 | Cap-Tons/1000 sf | 833.5 | 1028.5 | 1028.5 | 0.23489 | 0.28694 | 0.28694 | 0 | 0 | 0 | 833.5 | 1028.5 | 1028.5 | 0.23489 | 0.28694 | 0.28694 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ASM | ASSEMBLY | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.94349 | 0.052426 | 1.0483 | Cap-Tons/1000 sf | 809.1 | 1348.5 | 1026.6 | 0.25907 | 0.43179 | 0.30012 | 0 | 0 | 0 | 809.1 | 1348.5 | 1026.6 | 0.25907 | 0.43179 | 0.30012 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.54668 | 0.030377 | 0.60743 | Cap-Tons/1000 sf | 706.2 | 1177 | 893.65 | 0.24254 | 0.40423 | 0.28214 | 0 | 0 | 0 | 706.2 | 1177 | 893.65 | 0.24254 | 0.40423 | 0.28214 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.66214 | 0.036793 | 0.73573 | Cap-Tons/1000 sf | 597.75 | 996.25 | 728.7 | 0.3343 | 0.55716 | 0.37525 | 0 | 0 | 0 | 597.75 | 996.25 | 728.7 | 0.3343 | 0.55716 | 0.37525 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.82639 | 0.043502 | 0.86989 | Cap-Tons/1000 sf | 746.4 | 1244 | 983.4 | 0.3519 | 0.5865 | 0.4086 | 0 | 0 | 0 | 746.4 | 1244 | 983.4 | 0.3519 | 0.5865 | 0.4086 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.64424 | 0.035798 | 0.71584 | Cap-Tons/1000 sf | 721.5 | 1192.5 | 859.2 | 0.41056 | 0.67769 | 0.45246 | 0 | 0 | 0 | 721.5 | 1192.5 | 859.2 | 0.41056 | 0.67769 | 0.45246 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EUN | EDUCATION - UNIVERSITY | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.58045 | 0.030556 | 0.61101 | Cap-Tons/1000 sf | 829.65 | 1382.75 | 1051.65 | 0.24414 | 0.4069 | 0.28719 | 0 | 0 | 0 | 829.65 | 1382.75 | 1051.65 | 0.24414 | 0.4069 | 0.28719 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | GRO | GROCERY | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 1.0681 | 0.056226 | 1.1243 | Cap-Tons/1000 sf | 959.55 | 1599.25 | 1297.05 | 0.26991 | 0.44985 | 0.31856 | 0 | 0 | 0 | 959.55 | 1599.25 | 1297.05 | 0.26991 | 0.44985 | 0.31856 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.78906 | 0.043846 | 0.87675 | Cap-Tons/1000 sf | 1440.45 | 2400.75 | 1834.45 | 0.22898 | 0.38163 | 0.27213 | 0 | 0 | 0 | 1440.45 | 2400.75 | 1834.45 | 0.22898 | 0.38163 | 0.27213 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HTL | LODGING - HOTEL | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.46601 | 0.024532 | 0.49055 | Cap-Tons/1000 sf | 1365.15 | 2275.25 | 1748.65 | 0.23852 | 0.39754 | 0.28302 | 0 | 0 | 0 | 1365.15 | 2275.25 | 1748.65 | 0.23852 | 0.39754 | 0.28302 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | MTL | LODGING - MOTEL | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.46601 | 0.024532 | 0.49055 | Cap-Tons/1000 sf | 1365.15 | 2275.25 | 1748.65 | 0.23852 | 0.39754 | 0.28302 | 0 | 0 | 0 | 1365.15 | 2275.25 | 1748.65 | 0.23852 | 0.39754 | 0.28302 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.83291 | 0.043846 | 0.87675 | Cap-Tons/1000 sf | 1120.2 | 1867 | 1501.2 | 0.23786 | 0.39643 | 0.28351 | 0 | 0 | 0 | 1120.2 | 1867 | 1501.2 | 0.23786 | 0.39643 | 0.28351 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFL | OFFICE - LARGE | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.60844 | 0.032029 | 0.64047 | Cap-Tons/1000 sf | 861.336 | 1435.5599 | 1024.186 | 0.28584 | 0.4764 | 0.33144 | 0 | 0 | 0 | 861.336 | 1435.5599 | 1024.186 | 0.28584 | 0.4764 | 0.33144 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFS | OFFICE - SMALL | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.69988 | 0.03889 | 0.77766 | Cap-Tons/1000 sf | 701.1 | 1168.5 | 858.35 | 0.26469 | 0.44115 | 0.31234 | 0 | 0 | 0 | 701.1 | 1168.5 | 858.35 | 0.26469 | 0.44115 | 0.31234 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 1.2308 | 0.068392 | 1.3676 | Cap-Tons/1000 sf | 1102.95 | 1838.25 | 1433.45 | 0.27538 | 0.45896 | 0.31658 | 0 | 0 | 0 | 1102.95 | 1838.25 | 1433.45 | 0.27538 | 0.45896 | 0.31658 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.81237 | 0.04514 | 0.90265 | Cap-Tons/1000 sf | 927.1865 | 1545.3109 | 1162.1865 | 0.31962 | 0.53269 | 0.36137 | 0 | 0 | 0 | 927.1865 | 1545.3109 | 1162.1865 | 0.31962 | 0.53269 | 0.36137 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | SCN | STORAGE - CONDITIONED | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.25401 | 0.014114 | 0.28224 | Cap-Tons/1000 sf | 617.1 | 1028.5 | 816.1 | 0.27174 | 0.45289 | 0.31714 | 0 | 0 | 0 | 617.1 | 1028.5 | 816.1 | 0.27174 | 0.45289 | 0.31714 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ASM | ASSEMBLY | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.94349 | 0.052426 | 1.0483 | Cap-Tons/1000 sf | 1120 | 1348.5 | 1348.5 | 0.35657 | 0.41327 | 0.41327 | 0 | 0 | 0 | 1120 | 1348.5 | 1348.5 | 0.35657 | 0.41327 | 0.41327 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.54668 | 0.030377 | 0.60743 | Cap-Tons/1000 sf | 991.5 | 1177 | 1177 | 0.22236 | 0.25991 | 0.25991 | 0 | 0 | 0 | 991.5 | 1177 | 1177 | 0.22236 | 0.25991 | 0.25991 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.66214 | 0.036793 | 0.73573 | Cap-Tons/1000 sf | 866.45 | 996.25 | 996.25 | 0.30338 | 0.34653 | 0.34653 | 0 | 0 | 0 | 866.45 | 996.25 | 996.25 | 0.30338 | 0.34653 | 0.34653 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.82639 | 0.043502 | 0.86989 | Cap-Tons/1000 sf | 1071 | 1244 | 1244 | 0.32072 | 0.37222 | 0.37222 | 0 | 0 | 0 | 1071 | 1244 | 1244 | 0.32072 | 0.37222 | 0.37222 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.64424 | 0.035798 | 0.71584 | Cap-Tons/1000 sf | 1056.05 | 1192.5 | 1192.5 | 0.34256 | 0.38491 | 0.38491 | 0 | 0 | 0 | 1056.05 | 1192.5 | 1192.5 | 0.34256 | 0.38491 | 0.38491 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EUN | EDUCATION - UNIVERSITY | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.58045 | 0.030556 | 0.61101 | Cap-Tons/1000 sf | 1165.25 | 1382.75 | 1382.75 | 0.2705 | 0.3112 | 0.3112 | 0 | 0 | 0 | 1165.25 | 1382.75 | 1382.75 | 0.2705 | 0.3112 | 0.3112 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | GRO | GROCERY | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 1.0681 | 0.056226 | 1.1243 | Cap-Tons/1000 sf | 1263.25 | 1599.25 | 1599.25 | 0.18531 | 0.23851 | 0.23851 | 0 | 0 | 0 | 1263.25 | 1599.25 | 1599.25 | 0.18531 | 0.23851 | 0.23851 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.78906 | 0.043846 | 0.87675 | Cap-Tons/1000 sf | 2000.25 | 2400.75 | 2400.75 | 0.232 | 0.2733 | 0.2733 | 0 | 0 | 0 | 2000.25 | 2400.75 | 2400.75 | 0.232 | 0.2733 | 0.2733 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HTL | LODGING - HOTEL | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.46601 | 0.024532 | 0.49055 | Cap-Tons/1000 sf | 1889.75 | 2275.25 | 2275.25 | 0.24957 | 0.29402 | 0.29402 | 0 | 0 | 0 | 1889.75 | 2275.25 | 2275.25 | 0.24957 | 0.29402 | 0.29402 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | MTL | LODGING - MOTEL | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.46601 | 0.024532 | 0.49055 | Cap-Tons/1000 sf | 1889.75 | 2275.25 | 2275.25 | 0.24957 | 0.29402 | 0.29402 | 0 | 0 | 0 | 1889.75 | 2275.25 | 2275.25 | 0.24957 | 0.29402 | 0.29402 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.83291 | 0.043846 | 0.87675 | Cap-Tons/1000 sf | 1482 | 1867 | 1867 | 0.18025 | 0.22325 | 0.22325 | 0 | 0 | 0 | 1482 | 1867 | 1867 | 0.18025 | 0.22325 | 0.22325 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFL | OFFICE - LARGE | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.60844 | 0.032029 | 0.64047 | Cap-Tons/1000 sf | 1282.8099 | 1435.5599 | 1435.5599 | 0.43919 | 0.48019 | 0.48019 | 0 | 0 | 0 | 1282.8099 | 1435.5599 | 1435.5599 | 0.43919 | 0.48019 | 0.48019 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFS | OFFICE - SMALL | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.69988 | 0.03889 | 0.77766 | Cap-Tons/1000 sf | 1011.6 | 1168.5 | 1168.5 | 0.36615 | 0.41215 | 0.41215 | 0 | 0 | 0 | 1011.6 | 1168.5 | 1168.5 | 0.36615 | 0.41215 | 0.41215 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 1.2308 | 0.068392 | 1.3676 | Cap-Tons/1000 sf | 1491.75 | 1838.25 | 1838.25 | 0.20178 | 0.24748 | 0.24748 | 0 | 0 | 0 | 1491.75 | 1838.25 | 1838.25 | 0.20178 | 0.24748 | 0.24748 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.81237 | 0.04514 | 0.90265 | Cap-Tons/1000 sf | 1307.8109 | 1545.3109 | 1545.3109 | 0.36871 | 0.42476 | 0.42476 | 0 | 0 | 0 | 1307.8109 | 1545.3109 | 1545.3109 | 0.36871 | 0.42476 | 0.42476 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.37152 | 0.019557 | 0.39108 | Cap-Tons/1000 sf | 1208.75 | 1434.25 | 1434.25 | 0.24524 | 0.28594 | 0.28594 | 0 | 0 | 0 | 1208.75 | 1434.25 | 1434.25 | 0.24524 | 0.28594 | 0.28594 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.42671 | 0.023711 | 0.47413 | Cap-Tons/1000 sf | 1252 | 1520 | 1520 | 0.21329 | 0.25574 | 0.25574 | 0 | 0 | 0 | 1252 | 1520 | 1520 | 0.21329 | 0.25574 | 0.25574 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTS | RETAIL - SMALL | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.46376 | 0.02577 | 0.5153 | Cap-Tons/1000 sf | 1147.75 | 1369.25 | 1369.25 | 0.20833 | 0.24473 | 0.24473 | 0 | 0 | 0 | 1147.75 | 1369.25 | 1369.25 | 0.20833 | 0.24473 | 0.24473 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | SCN | STORAGE - CONDITIONED | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.25401 | 0.014114 | 0.28224 | Cap-Tons/1000 sf | 826 | 1028.5 | 1028.5 | 0.17122 | 0.21172 | 0.21172 | 0 | 0 | 0 | 826 | 1028.5 | 1028.5 | 0.17122 | 0.21172 | 0.21172 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ASM | ASSEMBLY | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.94349 | 0.052426 | 1.0483 | Cap-Tons/1000 sf | 809.1 | 1348.5 | 1027.6 | 0.24283 | 0.40472 | 0.26738 | 0 | 0 | 0 | 809.1 | 1348.5 | 1027.6 | 0.24283 | 0.40472 | 0.26738 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.54668 | 0.030377 | 0.60743 | Cap-Tons/1000 sf | 706.2 | 1177 | 896.7 | 0.22329 | 0.37215 | 0.25319 | 0 | 0 | 0 | 706.2 | 1177 | 896.7 | 0.22329 | 0.37215 | 0.25319 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.66214 | 0.036793 | 0.73573 | Cap-Tons/1000 sf | 597.75 | 996.25 | 733 | 0.14953 | 0.24921 | 0.18613 | 0 | 0 | 0 | 597.75 | 996.25 | 733 | 0.14953 | 0.24921 | 0.18613 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.82639 | 0.043502 | 0.86989 | Cap-Tons/1000 sf | 746.4 | 1244 | 1008.4 | 0.23902 | 0.39837 | 0.29852 | 0 | 0 | 0 | 746.4 | 1244 | 1008.4 | 0.23902 | 0.39837 | 0.29852 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.64424 | 0.035798 | 0.71584 | Cap-Tons/1000 sf | 715.5 | 1192.5 | 860.45 | 0.16049 | 0.26749 | 0.19404 | 0 | 0 | 0 | 715.5 | 1192.5 | 860.45 | 0.16049 | 0.26749 | 0.19404 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EUN | EDUCATION - UNIVERSITY | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.58045 | 0.030556 | 0.61101 | Cap-Tons/1000 sf | 829.65 | 1382.75 | 1048.65 | 0.22904 | 0.38173 | 0.26384 | 0 | 0 | 0 | 829.65 | 1382.75 | 1048.65 | 0.22904 | 0.38173 | 0.26384 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | GRO | GROCERY | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 1.0681 | 0.056226 | 1.1243 | Cap-Tons/1000 sf | 959.55 | 1599.25 | 1296.55 | 0.28168 | 0.46947 | 0.33088 | 0 | 0 | 0 | 959.55 | 1599.25 | 1296.55 | 0.28168 | 0.46947 | 0.33088 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.78906 | 0.043846 | 0.87675 | Cap-Tons/1000 sf | 1440.45 | 2400.75 | 1831.45 | 0.23836 | 0.39726 | 0.27726 | 0 | 0 | 0 | 1440.45 | 2400.75 | 1831.45 | 0.23836 | 0.39726 | 0.27726 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HTL | LODGING - HOTEL | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.46601 | 0.024532 | 0.49055 | Cap-Tons/1000 sf | 1365.15 | 2275.25 | 1741.15 | 0.24183 | 0.40305 | 0.27963 | 0 | 0 | 0 | 1365.15 | 2275.25 | 1741.15 | 0.24183 | 0.40305 | 0.27963 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | MTL | LODGING - MOTEL | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.46601 | 0.024532 | 0.49055 | Cap-Tons/1000 sf | 1365.15 | 2275.25 | 1741.15 | 0.24183 | 0.40305 | 0.27963 | 0 | 0 | 0 | 1365.15 | 2275.25 | 1741.15 | 0.24183 | 0.40305 | 0.27963 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.83291 | 0.043846 | 0.87675 | Cap-Tons/1000 sf | 1120.2 | 1867 | 1501.7 | 0.23871 | 0.39786 | 0.27981 | 0 | 0 | 0 | 1120.2 | 1867 | 1501.7 | 0.23871 | 0.39786 | 0.27981 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFL | OFFICE - LARGE | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.60844 | 0.032029 | 0.64047 | Cap-Tons/1000 sf | 861.336 | 1435.5599 | 1022.036 | 0.28019 | 0.46698 | 0.31839 | 0 | 0 | 0 | 861.336 | 1435.5599 | 1022.036 | 0.28019 | 0.46698 | 0.31839 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFS | OFFICE - SMALL | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.69988 | 0.03889 | 0.77766 | Cap-Tons/1000 sf | 701.1 | 1168.5 | 855.4 | 0.26937 | 0.44894 | 0.30957 | 0 | 0 | 0 | 701.1 | 1168.5 | 855.4 | 0.26937 | 0.44894 | 0.30957 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.42671 | 0.023711 | 0.47413 | Cap-Tons/1000 sf | 912 | 1520 | 1168 | 0.24344 | 0.40573 | 0.27519 | 0 | 0 | 0 | 912 | 1520 | 1168 | 0.24344 | 0.40573 | 0.27519 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTS | RETAIL - SMALL | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.46376 | 0.02577 | 0.5153 | Cap-Tons/1000 sf | 821.55 | 1369.25 | 1030.05 | 0.24194 | 0.40323 | 0.27494 | 0 | 0 | 0 | 821.55 | 1369.25 | 1030.05 | 0.24194 | 0.40323 | 0.27494 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | SCN | STORAGE - CONDITIONED | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.25401 | 0.014114 | 0.28224 | Cap-Tons/1000 sf | 617.1 | 1028.5 | 813.6 | 0.26228 | 0.43714 | 0.30038 | 0 | 0 | 0 | 617.1 | 1028.5 | 813.6 | 0.26228 | 0.43714 | 0.30038 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ASM | ASSEMBLY | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.94349 | 0.052426 | 1.0483 | Cap-Tons/1000 sf | 1116 | 1348.5 | 1348.5 | 0.32417 | 0.38292 | 0.38292 | 0 | 0 | 0 | 1116 | 1348.5 | 1348.5 | 0.32417 | 0.38292 | 0.38292 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.54668 | 0.030377 | 0.60743 | Cap-Tons/1000 sf | 989 | 1177 | 1177 | 0.13542 | 0.16367 | 0.16367 | 0 | 0 | 0 | 989 | 1177 | 1177 | 0.13542 | 0.16367 | 0.16367 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.66214 | 0.036793 | 0.73573 | Cap-Tons/1000 sf | 865.95 | 996.25 | 996.25 | 0.27078 | 0.31058 | 0.31058 | 0 | 0 | 0 | 865.95 | 996.25 | 996.25 | 0.27078 | 0.31058 | 0.31058 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.82639 | 0.043502 | 0.86989 | Cap-Tons/1000 sf | 1049.5 | 1244 | 1244 | 0.26252 | 0.31102 | 0.31102 | 0 | 0 | 0 | 1049.5 | 1244 | 1244 | 0.26252 | 0.31102 | 0.31102 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.64424 | 0.035798 | 0.71584 | Cap-Tons/1000 sf | 1052.95 | 1192.5 | 1192.5 | 0.30295 | 0.34225 | 0.34225 | 0 | 0 | 0 | 1052.95 | 1192.5 | 1192.5 | 0.30295 | 0.34225 | 0.34225 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EUN | EDUCATION - UNIVERSITY | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.58045 | 0.030556 | 0.61101 | Cap-Tons/1000 sf | 1164.25 | 1382.75 | 1382.75 | 0.18568 | 0.21783 | 0.21783 | 0 | 0 | 0 | 1164.25 | 1382.75 | 1382.75 | 0.18568 | 0.21783 | 0.21783 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | GRO | GROCERY | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 1.0681 | 0.056226 | 1.1243 | Cap-Tons/1000 sf | 1261.25 | 1599.25 | 1599.25 | 0.20361 | 0.26096 | 0.26096 | 0 | 0 | 0 | 1261.25 | 1599.25 | 1599.25 | 0.20361 | 0.26096 | 0.26096 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.78906 | 0.043846 | 0.87675 | Cap-Tons/1000 sf | 1997.25 | 2400.75 | 2400.75 | 0.21733 | 0.25688 | 0.25688 | 0 | 0 | 0 | 1997.25 | 2400.75 | 2400.75 | 0.21733 | 0.25688 | 0.25688 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HTL | LODGING - HOTEL | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.46601 | 0.024532 | 0.49055 | Cap-Tons/1000 sf | 1893.75 | 2275.25 | 2275.25 | 0.23134 | 0.27339 | 0.27339 | 0 | 0 | 0 | 1893.75 | 2275.25 | 2275.25 | 0.23134 | 0.27339 | 0.27339 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | MTL | LODGING - MOTEL | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.46601 | 0.024532 | 0.49055 | Cap-Tons/1000 sf | 1893.75 | 2275.25 | 2275.25 | 0.23134 | 0.27339 | 0.27339 | 0 | 0 | 0 | 1893.75 | 2275.25 | 2275.25 | 0.23134 | 0.27339 | 0.27339 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.83291 | 0.043846 | 0.87675 | Cap-Tons/1000 sf | 1481 | 1867 | 1867 | 0.15399 | 0.19244 | 0.19244 | 0 | 0 | 0 | 1481 | 1867 | 1867 | 0.15399 | 0.19244 | 0.19244 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFL | OFFICE - LARGE | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.60844 | 0.032029 | 0.64047 | Cap-Tons/1000 sf | 1281.3599 | 1435.5599 | 1435.5599 | 0.3441 | 0.3797 | 0.3797 | 0 | 0 | 0 | 1281.3599 | 1435.5599 | 1435.5599 | 0.3441 | 0.3797 | 0.3797 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFS | OFFICE - SMALL | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.69988 | 0.03889 | 0.77766 | Cap-Tons/1000 sf | 1014.7 | 1168.5 | 1168.5 | 0.3258 | 0.3659 | 0.3659 | 0 | 0 | 0 | 1014.7 | 1168.5 | 1168.5 | 0.3258 | 0.3659 | 0.3659 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 1.2308 | 0.068392 | 1.3676 | Cap-Tons/1000 sf | 1492.25 | 1838.25 | 1838.25 | 0.18454 | 0.22734 | 0.22734 | 0 | 0 | 0 | 1492.25 | 1838.25 | 1838.25 | 0.18454 | 0.22734 | 0.22734 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.81237 | 0.04514 | 0.90265 | Cap-Tons/1000 sf | 1294.8109 | 1545.3109 | 1545.3109 | 0.30961 | 0.36546 | 0.36546 | 0 | 0 | 0 | 1294.8109 | 1545.3109 | 1545.3109 | 0.30961 | 0.36546 | 0.36546 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.37152 | 0.019557 | 0.39108 | Cap-Tons/1000 sf | 1215.25 | 1434.25 | 1434.25 | 0.1369 | 0.16285 | 0.16285 | 0 | 0 | 0 | 1215.25 | 1434.25 | 1434.25 | 0.1369 | 0.16285 | 0.16285 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.42671 | 0.023711 | 0.47413 | Cap-Tons/1000 sf | 1256.5 | 1520 | 1520 | 0.16235 | 0.1959 | 0.1959 | 0 | 0 | 0 | 1256.5 | 1520 | 1520 | 0.16235 | 0.1959 | 0.1959 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTS | RETAIL - SMALL | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.46376 | 0.02577 | 0.5153 | Cap-Tons/1000 sf | 1153.75 | 1369.25 | 1369.25 | 0.16278 | 0.19258 | 0.19258 | 0 | 0 | 0 | 1153.75 | 1369.25 | 1369.25 | 0.16278 | 0.19258 | 0.19258 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | SCN | STORAGE - CONDITIONED | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.25401 | 0.014114 | 0.28224 | Cap-Tons/1000 sf | 826.5 | 1028.5 | 1028.5 | 0.090048 | 0.11688 | 0.11688 | 0 | 0 | 0 | 826.5 | 1028.5 | 1028.5 | 0.090048 | 0.11688 | 0.11688 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ASM | ASSEMBLY | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.94349 | 0.052426 | 1.0483 | Cap-Tons/1000 sf | 809.1 | 1348.5 | 1038.1 | 0.27114 | 0.4519 | 0.32289 | 0 | 0 | 0 | 809.1 | 1348.5 | 1038.1 | 0.27114 | 0.4519 | 0.32289 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.54668 | 0.030377 | 0.60743 | Cap-Tons/1000 sf | 706.2 | 1177 | 916.2 | 0.18155 | 0.30258 | 0.2073 | 0 | 0 | 0 | 706.2 | 1177 | 916.2 | 0.18155 | 0.30258 | 0.2073 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.66214 | 0.036793 | 0.73573 | Cap-Tons/1000 sf | 597.75 | 996.25 | 753.75 | 0.18699 | 0.31165 | 0.23474 | 0 | 0 | 0 | 597.75 | 996.25 | 753.75 | 0.18699 | 0.31165 | 0.23474 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.82639 | 0.043502 | 0.86989 | Cap-Tons/1000 sf | 746.4 | 1244 | 1051.4 | 0.25028 | 0.41713 | 0.31698 | 0 | 0 | 0 | 746.4 | 1244 | 1051.4 | 0.25028 | 0.41713 | 0.31698 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.64424 | 0.035798 | 0.71584 | Cap-Tons/1000 sf | 715.5 | 1192.5 | 888.5 | 0.20003 | 0.33339 | 0.24538 | 0 | 0 | 0 | 715.5 | 1192.5 | 888.5 | 0.20003 | 0.33339 | 0.24538 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HTL | LODGING - HOTEL | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.46601 | 0.024532 | 0.49055 | Cap-Tons/1000 sf | 1365.15 | 2275.25 | 1746.15 | 0.26689 | 0.44481 | 0.30884 | 0 | 0 | 0 | 1365.15 | 2275.25 | 1746.15 | 0.26689 | 0.44481 | 0.30884 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | MTL | LODGING - MOTEL | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.46601 | 0.024532 | 0.49055 | Cap-Tons/1000 sf | 1365.15 | 2275.25 | 1746.15 | 0.26689 | 0.44481 | 0.30884 | 0 | 0 | 0 | 1365.15 | 2275.25 | 1746.15 | 0.26689 | 0.44481 | 0.30884 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.83291 | 0.043846 | 0.87675 | Cap-Tons/1000 sf | 1120.2 | 1867 | 1503.7 | 0.25286 | 0.42143 | 0.29221 | 0 | 0 | 0 | 1120.2 | 1867 | 1503.7 | 0.25286 | 0.42143 | 0.29221 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFL | OFFICE - LARGE | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.60844 | 0.032029 | 0.64047 | Cap-Tons/1000 sf | 861.336 | 1435.5599 | 1031.436 | 0.27196 | 0.45327 | 0.31831 | 0 | 0 | 0 | 861.336 | 1435.5599 | 1031.436 | 0.27196 | 0.45327 | 0.31831 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFS | OFFICE - SMALL | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.69988 | 0.03889 | 0.77766 | Cap-Tons/1000 sf | 701.1 | 1168.5 | 862.3 | 0.27115 | 0.45191 | 0.3195 | 0 | 0 | 0 | 701.1 | 1168.5 | 862.3 | 0.27115 | 0.45191 | 0.3195 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 1.2308 | 0.068392 | 1.3676 | Cap-Tons/1000 sf | 1102.95 | 1838.25 | 1431.95 | 0.29936 | 0.49893 | 0.34136 | 0 | 0 | 0 | 1102.95 | 1838.25 | 1431.95 | 0.29936 | 0.49893 | 0.34136 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.81237 | 0.04514 | 0.90265 | Cap-Tons/1000 sf | 927.1865 | 1545.3109 | 1165.1865 | 0.34015 | 0.56691 | 0.3905 | 0 | 0 | 0 | 927.1865 | 1545.3109 | 1165.1865 | 0.34015 | 0.56691 | 0.3905 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.37152 | 0.019557 | 0.39108 | Cap-Tons/1000 sf | 860.55 | 1434.25 | 1071.05 | 0.28033 | 0.46721 | 0.31483 | 0 | 0 | 0 | 860.55 | 1434.25 | 1071.05 | 0.28033 | 0.46721 | 0.31483 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.42671 | 0.023711 | 0.47413 | Cap-Tons/1000 sf | 912 | 1520 | 1168 | 0.2818 | 0.46967 | 0.32415 | 0 | 0 | 0 | 912 | 1520 | 1168 | 0.2818 | 0.46967 | 0.32415 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTS | RETAIL - SMALL | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.46376 | 0.02577 | 0.5153 | Cap-Tons/1000 sf | 821.55 | 1369.25 | 1027.55 | 0.27179 | 0.45298 | 0.30674 | 0 | 0 | 0 | 821.55 | 1369.25 | 1027.55 | 0.27179 | 0.45298 | 0.30674 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | SCN | STORAGE - CONDITIONED | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.25401 | 0.014114 | 0.28224 | Cap-Tons/1000 sf | 617.1 | 1028.5 | 820.6 | 0.26207 | 0.43679 | 0.30147 | 0 | 0 | 0 | 617.1 | 1028.5 | 820.6 | 0.26207 | 0.43679 | 0.30147 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ASM | ASSEMBLY | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.94349 | 0.052426 | 1.0483 | Cap-Tons/1000 sf | 1095.5 | 1348.5 | 1348.5 | 0.36121 | 0.43741 | 0.43741 | 0 | 0 | 0 | 1095.5 | 1348.5 | 1348.5 | 0.36121 | 0.43741 | 0.43741 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.54668 | 0.030377 | 0.60743 | Cap-Tons/1000 sf | 974.5 | 1177 | 1177 | 0.38359 | 0.44914 | 0.44914 | 0 | 0 | 0 | 974.5 | 1177 | 1177 | 0.38359 | 0.44914 | 0.44914 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.66214 | 0.036793 | 0.73573 | Cap-Tons/1000 sf | 851.25 | 996.25 | 996.25 | 0.42953 | 0.49608 | 0.49608 | 0 | 0 | 0 | 851.25 | 996.25 | 996.25 | 0.42953 | 0.49608 | 0.49608 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.82639 | 0.043502 | 0.86989 | Cap-Tons/1000 sf | 993 | 1244 | 1244 | 0.29073 | 0.36413 | 0.36413 | 0 | 0 | 0 | 993 | 1244 | 1244 | 0.29073 | 0.36413 | 0.36413 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.64424 | 0.035798 | 0.71584 | Cap-Tons/1000 sf | 1035.5 | 1192.5 | 1192.5 | 0.48358 | 0.54958 | 0.54958 | 0 | 0 | 0 | 1035.5 | 1192.5 | 1192.5 | 0.48358 | 0.54958 | 0.54958 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EUN | EDUCATION - UNIVERSITY | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.58045 | 0.030556 | 0.61101 | Cap-Tons/1000 sf | 1157.25 | 1382.75 | 1382.75 | 0.34398 | 0.40153 | 0.40153 | 0 | 0 | 0 | 1157.25 | 1382.75 | 1382.75 | 0.34398 | 0.40153 | 0.40153 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | GRO | GROCERY | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 1.0681 | 0.056226 | 1.1243 | Cap-Tons/1000 sf | 1256.25 | 1599.25 | 1599.25 | 0.19212 | 0.24782 | 0.24782 | 0 | 0 | 0 | 1256.25 | 1599.25 | 1599.25 | 0.19212 | 0.24782 | 0.24782 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.78906 | 0.043846 | 0.87675 | Cap-Tons/1000 sf | 1998.75 | 2400.75 | 2400.75 | 0.18904 | 0.22699 | 0.22699 | 0 | 0 | 0 | 1998.75 | 2400.75 | 2400.75 | 0.18904 | 0.22699 | 0.22699 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HTL | LODGING - HOTEL | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.46601 | 0.024532 | 0.49055 | Cap-Tons/1000 sf | 1896.25 | 2275.25 | 2275.25 | 0.21456 | 0.25581 | 0.25581 | 0 | 0 | 0 | 1896.25 | 2275.25 | 2275.25 | 0.21456 | 0.25581 | 0.25581 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | MTL | LODGING - MOTEL | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.46601 | 0.024532 | 0.49055 | Cap-Tons/1000 sf | 1896.25 | 2275.25 | 2275.25 | 0.21456 | 0.25581 | 0.25581 | 0 | 0 | 0 | 1896.25 | 2275.25 | 2275.25 | 0.21456 | 0.25581 | 0.25581 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.83291 | 0.043846 | 0.87675 | Cap-Tons/1000 sf | 1485 | 1867 | 1867 | 0.13865 | 0.18025 | 0.18025 | 0 | 0 | 0 | 1485 | 1867 | 1867 | 0.13865 | 0.18025 | 0.18025 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFL | OFFICE - LARGE | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.60844 | 0.032029 | 0.64047 | Cap-Tons/1000 sf | 1275.1099 | 1435.5599 | 1435.5599 | 0.48515 | 0.5356 | 0.5356 | 0 | 0 | 0 | 1275.1099 | 1435.5599 | 1435.5599 | 0.48515 | 0.5356 | 0.5356 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFS | OFFICE - SMALL | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.69988 | 0.03889 | 0.77766 | Cap-Tons/1000 sf | 1010.05 | 1168.5 | 1168.5 | 0.36752 | 0.41557 | 0.41557 | 0 | 0 | 0 | 1010.05 | 1168.5 | 1168.5 | 0.36752 | 0.41557 | 0.41557 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 1.2308 | 0.068392 | 1.3676 | Cap-Tons/1000 sf | 1489.75 | 1838.25 | 1838.25 | 0.32066 | 0.39231 | 0.39231 | 0 | 0 | 0 | 1489.75 | 1838.25 | 1838.25 | 0.32066 | 0.39231 | 0.39231 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.81237 | 0.04514 | 0.90265 | Cap-Tons/1000 sf | 1289.8109 | 1545.3109 | 1545.3109 | 0.37865 | 0.44985 | 0.44985 | 0 | 0 | 0 | 1289.8109 | 1545.3109 | 1545.3109 | 0.37865 | 0.44985 | 0.44985 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.37152 | 0.019557 | 0.39108 | Cap-Tons/1000 sf | 1214.25 | 1434.25 | 1434.25 | 0.37527 | 0.43682 | 0.43682 | 0 | 0 | 0 | 1214.25 | 1434.25 | 1434.25 | 0.37527 | 0.43682 | 0.43682 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.42671 | 0.023711 | 0.47413 | Cap-Tons/1000 sf | 1257.5 | 1520 | 1520 | 0.20587 | 0.25207 | 0.25207 | 0 | 0 | 0 | 1257.5 | 1520 | 1520 | 0.20587 | 0.25207 | 0.25207 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTS | RETAIL - SMALL | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.46376 | 0.02577 | 0.5153 | Cap-Tons/1000 sf | 1157.75 | 1369.25 | 1369.25 | 0.35417 | 0.41392 | 0.41392 | 0 | 0 | 0 | 1157.75 | 1369.25 | 1369.25 | 0.35417 | 0.41392 | 0.41392 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | SCN | STORAGE - CONDITIONED | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.25401 | 0.014114 | 0.28224 | Cap-Tons/1000 sf | 825 | 1028.5 | 1028.5 | 0.14598 | 0.18888 | 0.18888 | 0 | 0 | 0 | 825 | 1028.5 | 1028.5 | 0.14598 | 0.18888 | 0.18888 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ASM | ASSEMBLY | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.94349 | 0.052426 | 1.0483 | Cap-Tons/1000 sf | 809.1 | 1348.5 | 1028.6 | 0.20449 | 0.34082 | 0.23379 | 0 | 0 | 0 | 809.1 | 1348.5 | 1028.6 | 0.20449 | 0.34082 | 0.23379 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.54668 | 0.030377 | 0.60743 | Cap-Tons/1000 sf | 706.2 | 1177 | 928.7 | 0.15004 | 0.25007 | 0.17884 | 0 | 0 | 0 | 706.2 | 1177 | 928.7 | 0.15004 | 0.25007 | 0.17884 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.66214 | 0.036793 | 0.73573 | Cap-Tons/1000 sf | 597.75 | 996.25 | 773.75 | 0.14139 | 0.23566 | 0.18899 | 0 | 0 | 0 | 597.75 | 996.25 | 773.75 | 0.14139 | 0.23566 | 0.18899 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.82639 | 0.043502 | 0.86989 | Cap-Tons/1000 sf | 746.4 | 1244 | 1052.9 | 0.19054 | 0.31757 | 0.25424 | 0 | 0 | 0 | 746.4 | 1244 | 1052.9 | 0.19054 | 0.31757 | 0.25424 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.64424 | 0.035798 | 0.71584 | Cap-Tons/1000 sf | 715.5 | 1192.5 | 931.5 | 0.13888 | 0.23146 | 0.18498 | 0 | 0 | 0 | 715.5 | 1192.5 | 931.5 | 0.13888 | 0.23146 | 0.18498 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EUN | EDUCATION - UNIVERSITY | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.58045 | 0.030556 | 0.61101 | Cap-Tons/1000 sf | 829.65 | 1382.75 | 1066.65 | 0.17198 | 0.28664 | 0.20528 | 0 | 0 | 0 | 829.65 | 1382.75 | 1066.65 | 0.17198 | 0.28664 | 0.20528 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | GRO | GROCERY | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 1.0681 | 0.056226 | 1.1243 | Cap-Tons/1000 sf | 959.55 | 1599.25 | 1291.05 | 0.21216 | 0.3536 | 0.26296 | 0 | 0 | 0 | 959.55 | 1599.25 | 1291.05 | 0.21216 | 0.3536 | 0.26296 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.78906 | 0.043846 | 0.87675 | Cap-Tons/1000 sf | 1440.45 | 2400.75 | 1845.45 | 0.21745 | 0.36242 | 0.2576 | 0 | 0 | 0 | 1440.45 | 2400.75 | 1845.45 | 0.21745 | 0.36242 | 0.2576 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HTL | LODGING - HOTEL | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.46601 | 0.024532 | 0.49055 | Cap-Tons/1000 sf | 1365.15 | 2275.25 | 1755.65 | 0.21985 | 0.36641 | 0.25895 | 0 | 0 | 0 | 1365.15 | 2275.25 | 1755.65 | 0.21985 | 0.36641 | 0.25895 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | MTL | LODGING - MOTEL | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.46601 | 0.024532 | 0.49055 | Cap-Tons/1000 sf | 1365.15 | 2275.25 | 1755.65 | 0.21985 | 0.36641 | 0.25895 | 0 | 0 | 0 | 1365.15 | 2275.25 | 1755.65 | 0.21985 | 0.36641 | 0.25895 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.83291 | 0.043846 | 0.87675 | Cap-Tons/1000 sf | 1120.2 | 1867 | 1509.2 | 0.19161 | 0.31934 | 0.23191 | 0 | 0 | 0 | 1120.2 | 1867 | 1509.2 | 0.19161 | 0.31934 | 0.23191 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFL | OFFICE - LARGE | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.60844 | 0.032029 | 0.64047 | Cap-Tons/1000 sf | 861.336 | 1435.5599 | 1046.336 | 0.23821 | 0.39702 | 0.27871 | 0 | 0 | 0 | 861.336 | 1435.5599 | 1046.336 | 0.23821 | 0.39702 | 0.27871 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFS | OFFICE - SMALL | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.69988 | 0.03889 | 0.77766 | Cap-Tons/1000 sf | 701.1 | 1168.5 | 878.1 | 0.22319 | 0.37199 | 0.26899 | 0 | 0 | 0 | 701.1 | 1168.5 | 878.1 | 0.22319 | 0.37199 | 0.26899 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 1.2308 | 0.068392 | 1.3676 | Cap-Tons/1000 sf | 1102.95 | 1838.25 | 1431.45 | 0.22841 | 0.38068 | 0.26361 | 0 | 0 | 0 | 1102.95 | 1838.25 | 1431.45 | 0.22841 | 0.38068 | 0.26361 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.81237 | 0.04514 | 0.90265 | Cap-Tons/1000 sf | 927.1865 | 1545.3109 | 1157.6865 | 0.25121 | 0.41869 | 0.28176 | 0 | 0 | 0 | 927.1865 | 1545.3109 | 1157.6865 | 0.25121 | 0.41869 | 0.28176 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.37152 | 0.019557 | 0.39108 | Cap-Tons/1000 sf | 860.55 | 1434.25 | 1073.55 | 0.2199 | 0.3665 | 0.25125 | 0 | 0 | 0 | 860.55 | 1434.25 | 1073.55 | 0.2199 | 0.3665 | 0.25125 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.42671 | 0.023711 | 0.47413 | Cap-Tons/1000 sf | 912 | 1520 | 1166.5 | 0.21994 | 0.36656 | 0.25819 | 0 | 0 | 0 | 912 | 1520 | 1166.5 | 0.21994 | 0.36656 | 0.25819 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTS | RETAIL - SMALL | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.46376 | 0.02577 | 0.5153 | Cap-Tons/1000 sf | 821.55 | 1369.25 | 1032.05 | 0.21769 | 0.36281 | 0.24979 | 0 | 0 | 0 | 821.55 | 1369.25 | 1032.05 | 0.21769 | 0.36281 | 0.24979 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | SCN | STORAGE - CONDITIONED | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.25401 | 0.014114 | 0.28224 | Cap-Tons/1000 sf | 617.1 | 1028.5 | 811.1 | 0.20615 | 0.34358 | 0.2426 | 0 | 0 | 0 | 617.1 | 1028.5 | 811.1 | 0.20615 | 0.34358 | 0.2426 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ASM | ASSEMBLY | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.94349 | 0.052426 | 1.0483 | Cap-Tons/1000 sf | 1111.5 | 1348.5 | 1348.5 | 0.37598 | 0.44563 | 0.44563 | 0 | 0 | 0 | 1111.5 | 1348.5 | 1348.5 | 0.37598 | 0.44563 | 0.44563 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.54668 | 0.030377 | 0.60743 | Cap-Tons/1000 sf | 978.5 | 1177 | 1177 | 0.3813 | 0.44605 | 0.44605 | 0 | 0 | 0 | 978.5 | 1177 | 1177 | 0.3813 | 0.44605 | 0.44605 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.66214 | 0.036793 | 0.73573 | Cap-Tons/1000 sf | 828.75 | 996.25 | 996.25 | 0.33589 | 0.39854 | 0.39854 | 0 | 0 | 0 | 828.75 | 996.25 | 996.25 | 0.33589 | 0.39854 | 0.39854 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.82639 | 0.043502 | 0.86989 | Cap-Tons/1000 sf | 965 | 1244 | 1244 | 0.24202 | 0.31192 | 0.31192 | 0 | 0 | 0 | 965 | 1244 | 1244 | 0.24202 | 0.31192 | 0.31192 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.64424 | 0.035798 | 0.71584 | Cap-Tons/1000 sf | 993.5 | 1192.5 | 1192.5 | 0.34908 | 0.41198 | 0.41198 | 0 | 0 | 0 | 993.5 | 1192.5 | 1192.5 | 0.34908 | 0.41198 | 0.41198 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EUN | EDUCATION - UNIVERSITY | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.58045 | 0.030556 | 0.61101 | Cap-Tons/1000 sf | 1155.25 | 1382.75 | 1382.75 | 0.27632 | 0.32622 | 0.32622 | 0 | 0 | 0 | 1155.25 | 1382.75 | 1382.75 | 0.27632 | 0.32622 | 0.32622 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | GRO | GROCERY | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 1.0681 | 0.056226 | 1.1243 | Cap-Tons/1000 sf | 1263.25 | 1599.25 | 1599.25 | 0.2148 | 0.2734 | 0.2734 | 0 | 0 | 0 | 1263.25 | 1599.25 | 1599.25 | 0.2148 | 0.2734 | 0.2734 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.78906 | 0.043846 | 0.87675 | Cap-Tons/1000 sf | 1984.75 | 2400.75 | 2400.75 | 0.22829 | 0.27344 | 0.27344 | 0 | 0 | 0 | 1984.75 | 2400.75 | 2400.75 | 0.22829 | 0.27344 | 0.27344 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HTL | LODGING - HOTEL | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.46601 | 0.024532 | 0.49055 | Cap-Tons/1000 sf | 1872.25 | 2275.25 | 2275.25 | 0.25472 | 0.30502 | 0.30502 | 0 | 0 | 0 | 1872.25 | 2275.25 | 2275.25 | 0.25472 | 0.30502 | 0.30502 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | MTL | LODGING - MOTEL | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.46601 | 0.024532 | 0.49055 | Cap-Tons/1000 sf | 1872.25 | 2275.25 | 2275.25 | 0.25472 | 0.30502 | 0.30502 | 0 | 0 | 0 | 1872.25 | 2275.25 | 2275.25 | 0.25472 | 0.30502 | 0.30502 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.83291 | 0.043846 | 0.87675 | Cap-Tons/1000 sf | 1459.5 | 1867 | 1867 | 0.18505 | 0.23515 | 0.23515 | 0 | 0 | 0 | 1459.5 | 1867 | 1867 | 0.18505 | 0.23515 | 0.23515 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFL | OFFICE - LARGE | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.60844 | 0.032029 | 0.64047 | Cap-Tons/1000 sf | 1269.5599 | 1435.5599 | 1435.5599 | 0.45158 | 0.50313 | 0.50313 | 0 | 0 | 0 | 1269.5599 | 1435.5599 | 1435.5599 | 0.45158 | 0.50313 | 0.50313 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFS | OFFICE - SMALL | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.69988 | 0.03889 | 0.77766 | Cap-Tons/1000 sf | 1004 | 1168.5 | 1168.5 | 0.35982 | 0.41062 | 0.41062 | 0 | 0 | 0 | 1004 | 1168.5 | 1168.5 | 0.35982 | 0.41062 | 0.41062 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 1.2308 | 0.068392 | 1.3676 | Cap-Tons/1000 sf | 1497.75 | 1838.25 | 1838.25 | 0.2833 | 0.34555 | 0.34555 | 0 | 0 | 0 | 1497.75 | 1838.25 | 1838.25 | 0.2833 | 0.34555 | 0.34555 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.81237 | 0.04514 | 0.90265 | Cap-Tons/1000 sf | 1304.3109 | 1545.3109 | 1545.3109 | 0.404 | 0.47255 | 0.47255 | 0 | 0 | 0 | 1304.3109 | 1545.3109 | 1545.3109 | 0.404 | 0.47255 | 0.47255 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.37152 | 0.019557 | 0.39108 | Cap-Tons/1000 sf | 1204.75 | 1434.25 | 1434.25 | 0.20968 | 0.25178 | 0.25178 | 0 | 0 | 0 | 1204.75 | 1434.25 | 1434.25 | 0.20968 | 0.25178 | 0.25178 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.42671 | 0.023711 | 0.47413 | Cap-Tons/1000 sf | 1256 | 1520 | 1520 | 0.30443 | 0.36483 | 0.36483 | 0 | 0 | 0 | 1256 | 1520 | 1520 | 0.30443 | 0.36483 | 0.36483 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTS | RETAIL - SMALL | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.46376 | 0.02577 | 0.5153 | Cap-Tons/1000 sf | 1153.75 | 1369.25 | 1369.25 | 0.26834 | 0.31669 | 0.31669 | 0 | 0 | 0 | 1153.75 | 1369.25 | 1369.25 | 0.26834 | 0.31669 | 0.31669 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
| HVAC - SEER Rated Split System AC (SEER 14) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 14) | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan; Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER14 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | SCN | STORAGE - CONDITIONED | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.25401 | 0.014114 | 0.28224 | Cap-Tons/1000 sf | 829 | 1028.5 | 1028.5 | 0.1749 | 0.2202 | 0.2202 | 0 | 0 | 0 | 829 | 1028.5 | 1028.5 | 0.1749 | 0.2202 | 0.2202 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 870.3932 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ASM | ASSEMBLY | Existing | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.83582 | 0 | 0.96724 | Cap-Tons/1000 sf | 1098.3333 | 1394.6667 | 1175.9 | 0.48622 | 0.59312 | 0.51255 | 0 | 0 | 0 | 1098.3333 | 1394.6667 | 1175.9 | 0.48622 | 0.59312 | 0.51255 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | Existing | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.4818 | 0 | 0.55756 | Cap-Tons/1000 sf | 709.0545 | 1007.3131 | 780.8545 | 0.37915 | 0.52608 | 0.40811 | 0 | 0 | 0 | 709.0545 | 1007.3131 | 780.8545 | 0.37915 | 0.52608 | 0.40811 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | Existing | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.51248 | 0 | 0.59306 | Cap-Tons/1000 sf | 602.8733 | 799.2333 | 650.4733 | 0.48787 | 0.62753 | 0.51513 | 0 | 0 | 0 | 602.8733 | 799.2333 | 650.4733 | 0.48787 | 0.62753 | 0.51513 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | Existing | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.6128 | 0 | 0.70915 | Cap-Tons/1000 sf | 834.8333 | 1180.1667 | 915.6667 | 0.3976 | 0.54194 | 0.4233 | 0 | 0 | 0 | 834.8333 | 1180.1667 | 915.6667 | 0.3976 | 0.54194 | 0.4233 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | Existing | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.49429 | 0 | 0.57201 | Cap-Tons/1000 sf | 734.3167 | 941.3167 | 783.75 | 0.57893 | 0.71626 | 0.60596 | 0 | 0 | 0 | 734.3167 | 941.3167 | 783.75 | 0.57893 | 0.71626 | 0.60596 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EUN | EDUCATION - UNIVERSITY | Existing | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.51877 | 0 | 0.55658 | Cap-Tons/1000 sf | 676.0998 | 1032.3885 | 757.9998 | 0.35089 | 0.52863 | 0.38469 | 0 | 0 | 0 | 676.0998 | 1032.3885 | 757.9998 | 0.35089 | 0.52863 | 0.38469 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | GRO | GROCERY | Existing | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.86635 | 0 | 0.92949 | Cap-Tons/1000 sf | 783.7833 | 1089.7833 | 897.1167 | 0.18866 | 0.263 | 0.20786 | 0 | 0 | 0 | 783.7833 | 1089.7833 | 897.1167 | 0.18866 | 0.263 | 0.20786 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | Existing | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.71085 | 0 | 0.82262 | Cap-Tons/1000 sf | 950.1833 | 1563.9167 | 1094.6167 | 0.19829 | 0.32585 | 0.22329 | 0 | 0 | 0 | 950.1833 | 1563.9167 | 1094.6167 | 0.19829 | 0.32585 | 0.22329 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HTL | LODGING - HOTEL | Existing | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.4087 | 0 | 0.43849 | Cap-Tons/1000 sf | 1224.8733 | 1807.9 | 1357.0733 | 0.35486 | 0.51633 | 0.38532 | 0 | 0 | 0 | 1224.8733 | 1807.9 | 1357.0733 | 0.35486 | 0.51633 | 0.38532 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | MTL | LODGING - MOTEL | Existing | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.4087 | 0 | 0.43849 | Cap-Tons/1000 sf | 1224.8733 | 1807.9 | 1357.0733 | 0.35486 | 0.51633 | 0.38532 | 0 | 0 | 0 | 1224.8733 | 1807.9 | 1357.0733 | 0.35486 | 0.51633 | 0.38532 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | Existing | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.76674 | 0 | 0.82262 | Cap-Tons/1000 sf | 991.3667 | 1436.1667 | 1119.8 | 0.22825 | 0.32515 | 0.24979 | 0 | 0 | 0 | 991.3667 | 1436.1667 | 1119.8 | 0.22825 | 0.32515 | 0.24979 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFL | OFFICE - LARGE | Existing | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.54446 | 0 | 0.58414 | Cap-Tons/1000 sf | 1083.5599 | 1435.5599 | 1146.9599 | 0.5212 | 0.6932 | 0.54974 | 0 | 0 | 0 | 1083.5599 | 1435.5599 | 1146.9599 | 0.5212 | 0.6932 | 0.54974 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFS | OFFICE - SMALL | Existing | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.59035 | 0 | 0.68317 | Cap-Tons/1000 sf | 780.7846 | 1086.1179 | 838.1513 | 0.43759 | 0.60259 | 0.46396 | 0 | 0 | 0 | 780.7846 | 1086.1179 | 838.1513 | 0.43759 | 0.60259 | 0.46396 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | Existing | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 1.0264 | 0 | 1.1878 | Cap-Tons/1000 sf | 1179.6667 | 1593.6667 | 1292 | 0.38589 | 0.51006 | 0.41072 | 0 | 0 | 0 | 1179.6667 | 1593.6667 | 1292 | 0.38589 | 0.51006 | 0.41072 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | Existing | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.67965 | 0 | 0.78651 | Cap-Tons/1000 sf | 1237.9776 | 1545.3109 | 1319.8442 | 0.499 | 0.61436 | 0.5249 | 0 | 0 | 0 | 1237.9776 | 1545.3109 | 1319.8442 | 0.499 | 0.61436 | 0.5249 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | Existing | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.34638 | 0 | 0.37163 | Cap-Tons/1000 sf | 1043.2148 | 1382.2148 | 1119.4148 | 0.49845 | 0.63811 | 0.52671 | 0 | 0 | 0 | 1043.2148 | 1382.2148 | 1119.4148 | 0.49845 | 0.63811 | 0.52671 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | Existing | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.34652 | 0 | 0.40101 | Cap-Tons/1000 sf | 1092.8978 | 1433.8978 | 1183.5311 | 0.59047 | 0.7494 | 0.62367 | 0 | 0 | 0 | 1092.8978 | 1433.8978 | 1183.5311 | 0.59047 | 0.7494 | 0.62367 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTS | RETAIL - SMALL | Existing | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.39888 | 0 | 0.46159 | Cap-Tons/1000 sf | 1017.2737 | 1353.6783 | 1092.2403 | 0.54092 | 0.696 | 0.57002 | 0 | 0 | 0 | 1017.2737 | 1353.6783 | 1092.2403 | 0.54092 | 0.696 | 0.57002 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | SCN | STORAGE - CONDITIONED | Existing | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.22128 | 0 | 0.25607 | Cap-Tons/1000 sf | 691.91 | 912.5167 | 759.7433 | 0.14919 | 0.19769 | 0.16306 | 0 | 0 | 0 | 691.91 | 912.5167 | 759.7433 | 0.14919 | 0.19769 | 0.16306 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ASM | ASSEMBLY | New | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.83582 | 0 | 0.96724 | Cap-Tons/1000 sf | 1238 | 1394.6667 | 1310.0333 | 0.26513 | 0.30599 | 0.28176 | 0 | 0 | 0 | 1238 | 1394.6667 | 1310.0333 | 0.26513 | 0.30599 | 0.28176 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | New | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.4818 | 0 | 0.55756 | Cap-Tons/1000 sf | 846.9131 | 1007.3131 | 913.0798 | 0.25775 | 0.30895 | 0.28319 | 0 | 0 | 0 | 846.9131 | 1007.3131 | 913.0798 | 0.25775 | 0.30895 | 0.28319 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | New | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.51248 | 0 | 0.59306 | Cap-Tons/1000 sf | 696.8 | 799.2333 | 742.3333 | 0.295 | 0.34154 | 0.32007 | 0 | 0 | 0 | 696.8 | 799.2333 | 742.3333 | 0.295 | 0.34154 | 0.32007 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | New | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.6128 | 0 | 0.70915 | Cap-Tons/1000 sf | 1035.5333 | 1180.1667 | 1094.3 | 0.21446 | 0.25386 | 0.22843 | 0 | 0 | 0 | 1035.5333 | 1180.1667 | 1094.3 | 0.21446 | 0.25386 | 0.22843 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | New | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.49429 | 0 | 0.57201 | Cap-Tons/1000 sf | 829.15 | 941.3167 | 878.0833 | 0.29453 | 0.3371 | 0.31903 | 0 | 0 | 0 | 829.15 | 941.3167 | 878.0833 | 0.29453 | 0.3371 | 0.31903 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EUN | EDUCATION - UNIVERSITY | New | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.51877 | 0 | 0.55658 | Cap-Tons/1000 sf | 852.5552 | 1032.3885 | 926.3885 | 0.26141 | 0.32288 | 0.29518 | 0 | 0 | 0 | 852.5552 | 1032.3885 | 926.3885 | 0.26141 | 0.32288 | 0.29518 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | GRO | GROCERY | New | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.86635 | 0 | 0.92949 | Cap-Tons/1000 sf | 834.1167 | 1089.7833 | 939.7833 | 0.14263 | 0.1843 | 0.1615 | 0 | 0 | 0 | 834.1167 | 1089.7833 | 939.7833 | 0.14263 | 0.1843 | 0.1615 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | New | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.71085 | 0 | 0.82262 | Cap-Tons/1000 sf | 1230.9167 | 1563.9167 | 1363.3167 | 0.17191 | 0.22171 | 0.19397 | 0 | 0 | 0 | 1230.9167 | 1563.9167 | 1363.3167 | 0.17191 | 0.22171 | 0.19397 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HTL | LODGING - HOTEL | New | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.4087 | 0 | 0.43849 | Cap-Tons/1000 sf | 1543.5667 | 1807.9 | 1652.6 | 0.29469 | 0.34876 | 0.32186 | 0 | 0 | 0 | 1543.5667 | 1807.9 | 1652.6 | 0.29469 | 0.34876 | 0.32186 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | MTL | LODGING - MOTEL | New | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.4087 | 0 | 0.43849 | Cap-Tons/1000 sf | 1543.5667 | 1807.9 | 1652.6 | 0.29469 | 0.34876 | 0.32186 | 0 | 0 | 0 | 1543.5667 | 1807.9 | 1652.6 | 0.29469 | 0.34876 | 0.32186 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | New | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.76674 | 0 | 0.82262 | Cap-Tons/1000 sf | 1155.5 | 1436.1667 | 1273.0333 | 0.15125 | 0.19029 | 0.16909 | 0 | 0 | 0 | 1155.5 | 1436.1667 | 1273.0333 | 0.15125 | 0.19029 | 0.16909 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFL | OFFICE - LARGE | New | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.54446 | 0 | 0.58414 | Cap-Tons/1000 sf | 1291.7266 | 1435.5599 | 1348.8266 | 0.47604 | 0.538 | 0.50644 | 0 | 0 | 0 | 1291.7266 | 1435.5599 | 1348.8266 | 0.47604 | 0.538 | 0.50644 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFS | OFFICE - SMALL | New | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.59035 | 0 | 0.68317 | Cap-Tons/1000 sf | 960.2846 | 1086.1179 | 1011.7513 | 0.41574 | 0.47427 | 0.44237 | 0 | 0 | 0 | 960.2846 | 1086.1179 | 1011.7513 | 0.41574 | 0.47427 | 0.44237 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | New | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 1.0264 | 0 | 1.1878 | Cap-Tons/1000 sf | 1336.3333 | 1593.6667 | 1442.9 | 0.24118 | 0.28708 | 0.26285 | 0 | 0 | 0 | 1336.3333 | 1593.6667 | 1442.9 | 0.24118 | 0.28708 | 0.26285 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | New | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.67965 | 0 | 0.78651 | Cap-Tons/1000 sf | 1361.6442 | 1545.3109 | 1444.0776 | 0.30392 | 0.35359 | 0.33399 | 0 | 0 | 0 | 1361.6442 | 1545.3109 | 1444.0776 | 0.30392 | 0.35359 | 0.33399 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | New | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.34638 | 0 | 0.37163 | Cap-Tons/1000 sf | 1221.1481 | 1382.2148 | 1289.2148 | 0.28456 | 0.32778 | 0.3067 | 0 | 0 | 0 | 1221.1481 | 1382.2148 | 1289.2148 | 0.28456 | 0.32778 | 0.3067 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | New | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.34652 | 0 | 0.40101 | Cap-Tons/1000 sf | 1257.6311 | 1433.8978 | 1339.0978 | 0.32328 | 0.37377 | 0.35348 | 0 | 0 | 0 | 1257.6311 | 1433.8978 | 1339.0978 | 0.32328 | 0.37377 | 0.35348 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTS | RETAIL - SMALL | New | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.39888 | 0 | 0.46159 | Cap-Tons/1000 sf | 1197.7117 | 1353.6783 | 1263.445 | 0.29719 | 0.33944 | 0.31949 | 0 | 0 | 0 | 1197.7117 | 1353.6783 | 1263.445 | 0.29719 | 0.33944 | 0.31949 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | SCN | STORAGE - CONDITIONED | New | CZ01 | Arcata Area (CZ01) |  |  |  | 1000 sf | 0.22128 | 0 | 0.25607 | Cap-Tons/1000 sf | 760.5833 | 912.5167 | 824.1833 | 0.15649 | 0.18789 | 0.16962 | 0 | 0 | 0 | 760.5833 | 912.5167 | 824.1833 | 0.15649 | 0.18789 | 0.16962 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ASM | ASSEMBLY | Existing | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.83582 | 0 | 0.96724 | Cap-Tons/1000 sf | 916.1333 | 1394.6667 | 1019.4 | 0.65935 | 0.99934 | 0.70695 | 0 | 0 | 0 | 916.1333 | 1394.6667 | 1019.4 | 0.65935 | 0.99934 | 0.70695 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | Existing | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.4818 | 0 | 0.55756 | Cap-Tons/1000 sf | 607.0545 | 1007.3131 | 698.1879 | 0.41438 | 0.68738 | 0.46281 | 0 | 0 | 0 | 607.0545 | 1007.3131 | 698.1879 | 0.41438 | 0.68738 | 0.46281 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | Existing | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.51248 | 0 | 0.59306 | Cap-Tons/1000 sf | 536.8733 | 799.2333 | 594.9733 | 0.17323 | 0.25764 | 0.19049 | 0 | 0 | 0 | 536.8733 | 799.2333 | 594.9733 | 0.17323 | 0.25764 | 0.19049 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | Existing | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.6128 | 0 | 0.70915 | Cap-Tons/1000 sf | 741.1667 | 1180.1667 | 833.2333 | 0.33853 | 0.53517 | 0.37177 | 0 | 0 | 0 | 741.1667 | 1180.1667 | 833.2333 | 0.33853 | 0.53517 | 0.37177 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | Existing | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.49429 | 0 | 0.57201 | Cap-Tons/1000 sf | 662.2567 | 941.3167 | 722.6233 | 0.15221 | 0.21566 | 0.16446 | 0 | 0 | 0 | 662.2567 | 941.3167 | 722.6233 | 0.15221 | 0.21566 | 0.16446 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EUN | EDUCATION - UNIVERSITY | Existing | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.51877 | 0 | 0.55658 | Cap-Tons/1000 sf | 619.4331 | 1032.3885 | 721.8331 | 0.36349 | 0.60581 | 0.41459 | 0 | 0 | 0 | 619.4331 | 1032.3885 | 721.8331 | 0.36349 | 0.60581 | 0.41459 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | GRO | GROCERY | Existing | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.86635 | 0 | 0.92949 | Cap-Tons/1000 sf | 716.67 | 1089.7833 | 834.87 | 0.43277 | 0.6552 | 0.47001 | 0 | 0 | 0 | 716.67 | 1089.7833 | 834.87 | 0.43277 | 0.6552 | 0.47001 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | Existing | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.71085 | 0 | 0.82262 | Cap-Tons/1000 sf | 938.35 | 1563.9167 | 1099.2167 | 0.29334 | 0.48889 | 0.3371 | 0 | 0 | 0 | 938.35 | 1563.9167 | 1099.2167 | 0.29334 | 0.48889 | 0.3371 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HTL | LODGING - HOTEL | Existing | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.4087 | 0 | 0.43849 | Cap-Tons/1000 sf | 1103.54 | 1807.9 | 1264.54 | 0.4598 | 0.75238 | 0.51533 | 0 | 0 | 0 | 1103.54 | 1807.9 | 1264.54 | 0.4598 | 0.75238 | 0.51533 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | MTL | LODGING - MOTEL | Existing | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.4087 | 0 | 0.43849 | Cap-Tons/1000 sf | 1103.54 | 1807.9 | 1264.54 | 0.4598 | 0.75238 | 0.51533 | 0 | 0 | 0 | 1103.54 | 1807.9 | 1264.54 | 0.4598 | 0.75238 | 0.51533 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | Existing | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.76674 | 0 | 0.82262 | Cap-Tons/1000 sf | 890.7 | 1436.1667 | 1038.0333 | 0.33734 | 0.54091 | 0.38 | 0 | 0 | 0 | 890.7 | 1436.1667 | 1038.0333 | 0.33734 | 0.54091 | 0.38 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFL | OFFICE - LARGE | Existing | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.54446 | 0 | 0.58414 | Cap-Tons/1000 sf | 987.2266 | 1435.5599 | 1065.1599 | 0.69546 | 1.0118 | 0.74366 | 0 | 0 | 0 | 987.2266 | 1435.5599 | 1065.1599 | 0.69546 | 1.0118 | 0.74366 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFS | OFFICE - SMALL | Existing | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.59035 | 0 | 0.68317 | Cap-Tons/1000 sf | 687.1374 | 1086.1179 | 758.2041 | 0.55505 | 0.87621 | 0.60188 | 0 | 0 | 0 | 687.1374 | 1086.1179 | 758.2041 | 0.55505 | 0.87621 | 0.60188 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | Existing | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 1.0264 | 0 | 1.1878 | Cap-Tons/1000 sf | 1045.6667 | 1593.6667 | 1180.6667 | 0.55478 | 0.83972 | 0.60411 | 0 | 0 | 0 | 1045.6667 | 1593.6667 | 1180.6667 | 0.55478 | 0.83972 | 0.60411 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | Existing | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.67965 | 0 | 0.78651 | Cap-Tons/1000 sf | 1034.3109 | 1545.3109 | 1140.0109 | 0.75849 | 1.1308 | 0.80806 | 0 | 0 | 0 | 1034.3109 | 1545.3109 | 1140.0109 | 0.75849 | 1.1308 | 0.80806 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | Existing | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.34638 | 0 | 0.37163 | Cap-Tons/1000 sf | 867.3289 | 1382.2148 | 972.8622 | 0.5572 | 0.88535 | 0.61064 | 0 | 0 | 0 | 867.3289 | 1382.2148 | 972.8622 | 0.5572 | 0.88535 | 0.61064 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | Existing | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.34652 | 0 | 0.40101 | Cap-Tons/1000 sf | 927.272 | 1433.8978 | 1042.772 | 0.59337 | 0.91316 | 0.6484 | 0 | 0 | 0 | 927.272 | 1433.8978 | 1042.772 | 0.59337 | 0.91316 | 0.6484 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTS | RETAIL - SMALL | Existing | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.39888 | 0 | 0.46159 | Cap-Tons/1000 sf | 859.2737 | 1353.6783 | 962.6403 | 0.59157 | 0.92797 | 0.65231 | 0 | 0 | 0 | 859.2737 | 1353.6783 | 962.6403 | 0.59157 | 0.92797 | 0.65231 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | SCN | STORAGE - CONDITIONED | Existing | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.22128 | 0 | 0.25607 | Cap-Tons/1000 sf | 641.2433 | 912.5167 | 717.71 | 0.58436 | 0.81325 | 0.62663 | 0 | 0 | 0 | 641.2433 | 912.5167 | 717.71 | 0.58436 | 0.81325 | 0.62663 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ASM | ASSEMBLY | New | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.83582 | 0 | 0.96724 | Cap-Tons/1000 sf | 1191.2333 | 1394.6667 | 1287.7 | 0.5164 | 0.60753 | 0.56163 | 0 | 0 | 0 | 1191.2333 | 1394.6667 | 1287.7 | 0.5164 | 0.60753 | 0.56163 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | New | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.4818 | 0 | 0.55756 | Cap-Tons/1000 sf | 828.9798 | 1007.3131 | 913.3465 | 0.32161 | 0.40159 | 0.36575 | 0 | 0 | 0 | 828.9798 | 1007.3131 | 913.3465 | 0.32161 | 0.40159 | 0.36575 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | New | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.51248 | 0 | 0.59306 | Cap-Tons/1000 sf | 689.2667 | 799.2333 | 741.8 | 0 | 0 | 0 | 0 | 0 | 0 | 689.2667 | 799.2333 | 741.8 | 0 | 0 | 0 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | New | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.6128 | 0 | 0.70915 | Cap-Tons/1000 sf | 1052.8667 | 1180.1667 | 1112.8 | 0.20176 | 0.23636 | 0.216 | 0 | 0 | 0 | 1052.8667 | 1180.1667 | 1112.8 | 0.20176 | 0.23636 | 0.216 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | New | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.49429 | 0 | 0.57201 | Cap-Tons/1000 sf | 824.55 | 941.3167 | 880.55 | 0 | 0 | 0 | 0 | 0 | 0 | 824.55 | 941.3167 | 880.55 | 0 | 0 | 0 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EUN | EDUCATION - UNIVERSITY | New | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.51877 | 0 | 0.55658 | Cap-Tons/1000 sf | 836.7552 | 1032.3885 | 929.8219 | 0.26013 | 0.33413 | 0.29173 | 0 | 0 | 0 | 836.7552 | 1032.3885 | 929.8219 | 0.26013 | 0.33413 | 0.29173 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | GRO | GROCERY | New | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.86635 | 0 | 0.92949 | Cap-Tons/1000 sf | 838.7833 | 1089.7833 | 954.45 | 0.20804 | 0.27424 | 0.23221 | 0 | 0 | 0 | 838.7833 | 1089.7833 | 954.45 | 0.20804 | 0.27424 | 0.23221 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | New | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.71085 | 0 | 0.82262 | Cap-Tons/1000 sf | 1224.9167 | 1563.9167 | 1373.75 | 0.18141 | 0.24388 | 0.20888 | 0 | 0 | 0 | 1224.9167 | 1563.9167 | 1373.75 | 0.18141 | 0.24388 | 0.20888 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HTL | LODGING - HOTEL | New | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.4087 | 0 | 0.43849 | Cap-Tons/1000 sf | 1491.9 | 1807.9 | 1635.5667 | 0.3201 | 0.4001 | 0.3539 | 0 | 0 | 0 | 1491.9 | 1807.9 | 1635.5667 | 0.3201 | 0.4001 | 0.3539 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | MTL | LODGING - MOTEL | New | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.4087 | 0 | 0.43849 | Cap-Tons/1000 sf | 1491.9 | 1807.9 | 1635.5667 | 0.3201 | 0.4001 | 0.3539 | 0 | 0 | 0 | 1491.9 | 1807.9 | 1635.5667 | 0.3201 | 0.4001 | 0.3539 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | New | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.76674 | 0 | 0.82262 | Cap-Tons/1000 sf | 1140.5 | 1436.1667 | 1274.5667 | 0.18403 | 0.24396 | 0.2096 | 0 | 0 | 0 | 1140.5 | 1436.1667 | 1274.5667 | 0.18403 | 0.24396 | 0.2096 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFL | OFFICE - LARGE | New | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.54446 | 0 | 0.58414 | Cap-Tons/1000 sf | 1273.9266 | 1435.5599 | 1345.7266 | 0.45798 | 0.54131 | 0.49231 | 0 | 0 | 0 | 1273.9266 | 1435.5599 | 1345.7266 | 0.45798 | 0.54131 | 0.49231 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFS | OFFICE - SMALL | New | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.59035 | 0 | 0.68317 | Cap-Tons/1000 sf | 934.9846 | 1086.1179 | 1001.8179 | 0.40518 | 0.4893 | 0.45795 | 0 | 0 | 0 | 934.9846 | 1086.1179 | 1001.8179 | 0.40518 | 0.4893 | 0.45795 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | New | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 1.0264 | 0 | 1.1878 | Cap-Tons/1000 sf | 1316 | 1593.6667 | 1445 | 0.37421 | 0.45781 | 0.41997 | 0 | 0 | 0 | 1316 | 1593.6667 | 1445 | 0.37421 | 0.45781 | 0.41997 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | New | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.67965 | 0 | 0.78651 | Cap-Tons/1000 sf | 1332.9776 | 1545.3109 | 1436.6776 | 0.62486 | 0.72589 | 0.67509 | 0 | 0 | 0 | 1332.9776 | 1545.3109 | 1436.6776 | 0.62486 | 0.72589 | 0.67509 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | New | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.34638 | 0 | 0.37163 | Cap-Tons/1000 sf | 1179.2148 | 1382.2148 | 1279.8815 | 0.40551 | 0.48931 | 0.45584 | 0 | 0 | 0 | 1179.2148 | 1382.2148 | 1279.8815 | 0.40551 | 0.48931 | 0.45584 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | New | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.34652 | 0 | 0.40101 | Cap-Tons/1000 sf | 1210.5978 | 1433.8978 | 1319.1311 | 0.38547 | 0.4677 | 0.43407 | 0 | 0 | 0 | 1210.5978 | 1433.8978 | 1319.1311 | 0.38547 | 0.4677 | 0.43407 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTS | RETAIL - SMALL | New | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.39888 | 0 | 0.46159 | Cap-Tons/1000 sf | 1160.4783 | 1353.6783 | 1254.545 | 0.417 | 0.503 | 0.45047 | 0 | 0 | 0 | 1160.4783 | 1353.6783 | 1254.545 | 0.417 | 0.503 | 0.45047 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | SCN | STORAGE - CONDITIONED | New | CZ02 | Santa Rosa Area (CZ02) |  |  |  | 1000 sf | 0.22128 | 0 | 0.25607 | Cap-Tons/1000 sf | 758.2833 | 912.5167 | 828.55 | 0.26218 | 0.32338 | 0.28731 | 0 | 0 | 0 | 758.2833 | 912.5167 | 828.55 | 0.26218 | 0.32338 | 0.28731 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ASM | ASSEMBLY | Existing | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.83582 | 0 | 0.96724 | Cap-Tons/1000 sf | 994.6667 | 1394.6667 | 1086.1667 | 0.72099 | 1.0067 | 0.76096 | 0 | 0 | 0 | 994.6667 | 1394.6667 | 1086.1667 | 0.72099 | 1.0067 | 0.76096 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | Existing | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.4818 | 0 | 0.55756 | Cap-Tons/1000 sf | 647.7212 | 1007.3131 | 728.3545 | 0.36186 | 0.56055 | 0.3982 | 0 | 0 | 0 | 647.7212 | 1007.3131 | 728.3545 | 0.36186 | 0.56055 | 0.3982 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | Existing | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.51248 | 0 | 0.59306 | Cap-Tons/1000 sf | 562.2067 | 799.2333 | 613.94 | 0.041398 | 0.059072 | 0.044795 | 0 | 0 | 0 | 562.2067 | 799.2333 | 613.94 | 0.041398 | 0.059072 | 0.044795 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | Existing | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.6128 | 0 | 0.70915 | Cap-Tons/1000 sf | 831.1667 | 1180.1667 | 904.1 | 0.28851 | 0.40718 | 0.30974 | 0 | 0 | 0 | 831.1667 | 1180.1667 | 904.1 | 0.28851 | 0.40718 | 0.30974 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | Existing | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.49429 | 0 | 0.57201 | Cap-Tons/1000 sf | 690.2567 | 941.3167 | 744.29 | 0.032028 | 0.043818 | 0.034131 | 0 | 0 | 0 | 690.2567 | 941.3167 | 744.29 | 0.032028 | 0.043818 | 0.034131 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EUN | EDUCATION - UNIVERSITY | Existing | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.51877 | 0 | 0.55658 | Cap-Tons/1000 sf | 619.4331 | 1032.3885 | 713.3331 | 0.30499 | 0.50831 | 0.34316 | 0 | 0 | 0 | 619.4331 | 1032.3885 | 713.3331 | 0.30499 | 0.50831 | 0.34316 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | GRO | GROCERY | Existing | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.86635 | 0 | 0.92949 | Cap-Tons/1000 sf | 758.67 | 1089.7833 | 871.7033 | 0.3851 | 0.55208 | 0.41323 | 0 | 0 | 0 | 758.67 | 1089.7833 | 871.7033 | 0.3851 | 0.55208 | 0.41323 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | Existing | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.71085 | 0 | 0.82262 | Cap-Tons/1000 sf | 938.35 | 1563.9167 | 1094.25 | 0.2493 | 0.4155 | 0.28327 | 0 | 0 | 0 | 938.35 | 1563.9167 | 1094.25 | 0.2493 | 0.4155 | 0.28327 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HTL | LODGING - HOTEL | Existing | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.4087 | 0 | 0.43849 | Cap-Tons/1000 sf | 1117.54 | 1807.9 | 1269.3067 | 0.39462 | 0.63794 | 0.43549 | 0 | 0 | 0 | 1117.54 | 1807.9 | 1269.3067 | 0.39462 | 0.63794 | 0.43549 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | MTL | LODGING - MOTEL | Existing | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.4087 | 0 | 0.43849 | Cap-Tons/1000 sf | 1117.54 | 1807.9 | 1269.3067 | 0.39462 | 0.63794 | 0.43549 | 0 | 0 | 0 | 1117.54 | 1807.9 | 1269.3067 | 0.39462 | 0.63794 | 0.43549 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | Existing | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.76674 | 0 | 0.82262 | Cap-Tons/1000 sf | 928.7 | 1436.1667 | 1066.5 | 0.30104 | 0.46112 | 0.33354 | 0 | 0 | 0 | 928.7 | 1436.1667 | 1066.5 | 0.30104 | 0.46112 | 0.33354 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFL | OFFICE - LARGE | Existing | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.54446 | 0 | 0.58414 | Cap-Tons/1000 sf | 1026.5599 | 1435.5599 | 1099.3933 | 0.65976 | 0.91809 | 0.69686 | 0 | 0 | 0 | 1026.5599 | 1435.5599 | 1099.3933 | 0.65976 | 0.91809 | 0.69686 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFS | OFFICE - SMALL | Existing | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.59035 | 0 | 0.68317 | Cap-Tons/1000 sf | 719.1179 | 1086.1179 | 785.3513 | 0.50655 | 0.76589 | 0.54199 | 0 | 0 | 0 | 719.1179 | 1086.1179 | 785.3513 | 0.50655 | 0.76589 | 0.54199 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | Existing | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 1.0264 | 0 | 1.1878 | Cap-Tons/1000 sf | 1101 | 1593.6667 | 1224 | 0.50212 | 0.7193 | 0.54099 | 0 | 0 | 0 | 1101 | 1593.6667 | 1224 | 0.50212 | 0.7193 | 0.54099 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | Existing | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.67965 | 0 | 0.78651 | Cap-Tons/1000 sf | 1143.6442 | 1545.3109 | 1236.5776 | 0.78813 | 1.0621 | 0.8296 | 0 | 0 | 0 | 1143.6442 | 1545.3109 | 1236.5776 | 0.78813 | 1.0621 | 0.8296 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | Existing | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.34638 | 0 | 0.37163 | Cap-Tons/1000 sf | 926.6622 | 1382.2148 | 1020.3955 | 0.5462 | 0.81026 | 0.58777 | 0 | 0 | 0 | 926.6622 | 1382.2148 | 1020.3955 | 0.5462 | 0.81026 | 0.58777 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | Existing | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.34652 | 0 | 0.40101 | Cap-Tons/1000 sf | 984.6053 | 1433.8978 | 1089.4053 | 0.59459 | 0.86125 | 0.63785 | 0 | 0 | 0 | 984.6053 | 1433.8978 | 1089.4053 | 0.59459 | 0.86125 | 0.63785 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTS | RETAIL - SMALL | Existing | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.39888 | 0 | 0.46159 | Cap-Tons/1000 sf | 924.607 | 1353.6783 | 1014.1737 | 0.57427 | 0.83524 | 0.61634 | 0 | 0 | 0 | 924.607 | 1353.6783 | 1014.1737 | 0.57427 | 0.83524 | 0.61634 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | SCN | STORAGE - CONDITIONED | Existing | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.22128 | 0 | 0.25607 | Cap-Tons/1000 sf | 685.2433 | 912.5167 | 752.9433 | 0.42799 | 0.55671 | 0.45579 | 0 | 0 | 0 | 685.2433 | 912.5167 | 752.9433 | 0.42799 | 0.55671 | 0.45579 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ASM | ASSEMBLY | New | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.83582 | 0 | 0.96724 | Cap-Tons/1000 sf | 1218.9 | 1394.6667 | 1308.0333 | 0.50449 | 0.57983 | 0.54526 | 0 | 0 | 0 | 1218.9 | 1394.6667 | 1308.0333 | 0.50449 | 0.57983 | 0.54526 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | New | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.4818 | 0 | 0.55756 | Cap-Tons/1000 sf | 838.3131 | 1007.3131 | 914.2131 | 0.27539 | 0.33733 | 0.31055 | 0 | 0 | 0 | 838.3131 | 1007.3131 | 914.2131 | 0.27539 | 0.33733 | 0.31055 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | New | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.51248 | 0 | 0.59306 | Cap-Tons/1000 sf | 693.8667 | 799.2333 | 741.7333 | 0 | 0 | 0 | 0 | 0 | 0 | 693.8667 | 799.2333 | 741.7333 | 0 | 0 | 0 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | New | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.6128 | 0 | 0.70915 | Cap-Tons/1000 sf | 1069.3 | 1180.1667 | 1118.1333 | 0 | 0 | 0 | 0 | 0 | 0 | 1069.3 | 1180.1667 | 1118.1333 | 0 | 0 | 0 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | New | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.49429 | 0 | 0.57201 | Cap-Tons/1000 sf | 830.5167 | 941.3167 | 881.1833 | 0 | 0 | 0 | 0 | 0 | 0 | 830.5167 | 941.3167 | 881.1833 | 0 | 0 | 0 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EUN | EDUCATION - UNIVERSITY | New | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.51877 | 0 | 0.55658 | Cap-Tons/1000 sf | 832.5885 | 1032.3885 | 921.1219 | 0.24099 | 0.30614 | 0.27885 | 0 | 0 | 0 | 832.5885 | 1032.3885 | 921.1219 | 0.24099 | 0.30614 | 0.27885 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | GRO | GROCERY | New | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.86635 | 0 | 0.92949 | Cap-Tons/1000 sf | 840.45 | 1089.7833 | 950.55 | 0.19004 | 0.24475 | 0.22117 | 0 | 0 | 0 | 840.45 | 1089.7833 | 950.55 | 0.19004 | 0.24475 | 0.22117 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | New | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.71085 | 0 | 0.82262 | Cap-Tons/1000 sf | 1213.25 | 1563.9167 | 1356.9833 | 0.15516 | 0.20923 | 0.17646 | 0 | 0 | 0 | 1213.25 | 1563.9167 | 1356.9833 | 0.15516 | 0.20923 | 0.17646 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HTL | LODGING - HOTEL | New | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.4087 | 0 | 0.43849 | Cap-Tons/1000 sf | 1495.9 | 1807.9 | 1629.8333 | 0.30119 | 0.37092 | 0.34116 | 0 | 0 | 0 | 1495.9 | 1807.9 | 1629.8333 | 0.30119 | 0.37092 | 0.34116 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | MTL | LODGING - MOTEL | New | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.4087 | 0 | 0.43849 | Cap-Tons/1000 sf | 1495.9 | 1807.9 | 1629.8333 | 0.30119 | 0.37092 | 0.34116 | 0 | 0 | 0 | 1495.9 | 1807.9 | 1629.8333 | 0.30119 | 0.37092 | 0.34116 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | New | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.76674 | 0 | 0.82262 | Cap-Tons/1000 sf | 1144.5 | 1436.1667 | 1271.5333 | 0.15943 | 0.20836 | 0.1796 | 0 | 0 | 0 | 1144.5 | 1436.1667 | 1271.5333 | 0.15943 | 0.20836 | 0.1796 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFL | OFFICE - LARGE | New | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.54446 | 0 | 0.58414 | Cap-Tons/1000 sf | 1273.9933 | 1435.5599 | 1342.2933 | 0.47446 | 0.54638 | 0.51469 | 0 | 0 | 0 | 1273.9933 | 1435.5599 | 1342.2933 | 0.47446 | 0.54638 | 0.51469 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFS | OFFICE - SMALL | New | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.59035 | 0 | 0.68317 | Cap-Tons/1000 sf | 938.7846 | 1086.1179 | 1000.9846 | 0.43899 | 0.51349 | 0.47789 | 0 | 0 | 0 | 938.7846 | 1086.1179 | 1000.9846 | 0.43899 | 0.51349 | 0.47789 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | New | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 1.0264 | 0 | 1.1878 | Cap-Tons/1000 sf | 1324.3333 | 1593.6667 | 1443.9333 | 0.3412 | 0.4121 | 0.38004 | 0 | 0 | 0 | 1324.3333 | 1593.6667 | 1443.9333 | 0.3412 | 0.4121 | 0.38004 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | New | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.67965 | 0 | 0.78651 | Cap-Tons/1000 sf | 1357.4109 | 1545.3109 | 1446.4776 | 0.51623 | 0.59299 | 0.55703 | 0 | 0 | 0 | 1357.4109 | 1545.3109 | 1446.4776 | 0.51623 | 0.59299 | 0.55703 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | New | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.34638 | 0 | 0.37163 | Cap-Tons/1000 sf | 1189.9148 | 1382.2148 | 1278.3148 | 0.43813 | 0.51267 | 0.47867 | 0 | 0 | 0 | 1189.9148 | 1382.2148 | 1278.3148 | 0.43813 | 0.51267 | 0.47867 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | New | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.34652 | 0 | 0.40101 | Cap-Tons/1000 sf | 1218.5644 | 1433.8978 | 1318.8978 | 0.40801 | 0.48351 | 0.44954 | 0 | 0 | 0 | 1218.5644 | 1433.8978 | 1318.8978 | 0.40801 | 0.48351 | 0.44954 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTS | RETAIL - SMALL | New | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.39888 | 0 | 0.46159 | Cap-Tons/1000 sf | 1174.145 | 1353.6783 | 1256.5117 | 0.4473 | 0.52056 | 0.4882 | 0 | 0 | 0 | 1174.145 | 1353.6783 | 1256.5117 | 0.4473 | 0.52056 | 0.4882 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | SCN | STORAGE - CONDITIONED | New | CZ03 | Oakland Area (CZ03) |  |  |  | 1000 sf | 0.22128 | 0 | 0.25607 | Cap-Tons/1000 sf | 764.7167 | 912.5167 | 829.5167 | 0.22159 | 0.26606 | 0.24366 | 0 | 0 | 0 | 764.7167 | 912.5167 | 829.5167 | 0.22159 | 0.26606 | 0.24366 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ASM | ASSEMBLY | Existing | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.83582 | 0 | 0.96724 | Cap-Tons/1000 sf | 886.8 | 1394.6667 | 995.2667 | 0.57118 | 0.89694 | 0.61738 | 0 | 0 | 0 | 886.8 | 1394.6667 | 995.2667 | 0.57118 | 0.89694 | 0.61738 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | Existing | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.4818 | 0 | 0.55756 | Cap-Tons/1000 sf | 604.3879 | 1007.3131 | 695.4545 | 0.40437 | 0.67395 | 0.45227 | 0 | 0 | 0 | 604.3879 | 1007.3131 | 695.4545 | 0.40437 | 0.67395 | 0.45227 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | Existing | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.51248 | 0 | 0.59306 | Cap-Tons/1000 sf | 522.8733 | 799.2333 | 582.7733 | 0.56698 | 0.86344 | 0.61301 | 0 | 0 | 0 | 522.8733 | 799.2333 | 582.7733 | 0.56698 | 0.86344 | 0.61301 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | Existing | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.6128 | 0 | 0.70915 | Cap-Tons/1000 sf | 755.8333 | 1180.1667 | 840.1 | 0.56584 | 0.87517 | 0.61401 | 0 | 0 | 0 | 755.8333 | 1180.1667 | 840.1 | 0.56584 | 0.87517 | 0.61401 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | Existing | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.49429 | 0 | 0.57201 | Cap-Tons/1000 sf | 647.59 | 941.3167 | 709.7567 | 0.71539 | 1.0321 | 0.76326 | 0 | 0 | 0 | 647.59 | 941.3167 | 709.7567 | 0.71539 | 1.0321 | 0.76326 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EUN | EDUCATION - UNIVERSITY | Existing | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.51877 | 0 | 0.55658 | Cap-Tons/1000 sf | 619.4331 | 1032.3885 | 724.4998 | 0.36877 | 0.61461 | 0.41897 | 0 | 0 | 0 | 619.4331 | 1032.3885 | 724.4998 | 0.36877 | 0.61461 | 0.41897 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | GRO | GROCERY | Existing | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.86635 | 0 | 0.92949 | Cap-Tons/1000 sf | 711.3367 | 1089.7833 | 830.3033 | 0.38246 | 0.5835 | 0.41659 | 0 | 0 | 0 | 711.3367 | 1089.7833 | 830.3033 | 0.38246 | 0.5835 | 0.41659 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | Existing | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.71085 | 0 | 0.82262 | Cap-Tons/1000 sf | 938.35 | 1563.9167 | 1104.75 | 0.26239 | 0.43731 | 0.30292 | 0 | 0 | 0 | 938.35 | 1563.9167 | 1104.75 | 0.26239 | 0.43731 | 0.30292 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HTL | LODGING - HOTEL | Existing | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.4087 | 0 | 0.43849 | Cap-Tons/1000 sf | 1084.74 | 1807.9 | 1252.74 | 0.39489 | 0.65815 | 0.44529 | 0 | 0 | 0 | 1084.74 | 1807.9 | 1252.74 | 0.39489 | 0.65815 | 0.44529 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | MTL | LODGING - MOTEL | Existing | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.4087 | 0 | 0.43849 | Cap-Tons/1000 sf | 1084.74 | 1807.9 | 1252.74 | 0.39489 | 0.65815 | 0.44529 | 0 | 0 | 0 | 1084.74 | 1807.9 | 1252.74 | 0.39489 | 0.65815 | 0.44529 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | Existing | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.76674 | 0 | 0.82262 | Cap-Tons/1000 sf | 864.0333 | 1436.1667 | 1015.1667 | 0.29365 | 0.4879 | 0.33268 | 0 | 0 | 0 | 864.0333 | 1436.1667 | 1015.1667 | 0.29365 | 0.4879 | 0.33268 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFL | OFFICE - LARGE | Existing | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.54446 | 0 | 0.58414 | Cap-Tons/1000 sf | 965.8933 | 1435.5599 | 1047.0933 | 0.635 | 0.94366 | 0.67963 | 0 | 0 | 0 | 965.8933 | 1435.5599 | 1047.0933 | 0.635 | 0.94366 | 0.67963 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFS | OFFICE - SMALL | Existing | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.59035 | 0 | 0.68317 | Cap-Tons/1000 sf | 672.4708 | 1086.1179 | 745.7374 | 0.49443 | 0.79845 | 0.53709 | 0 | 0 | 0 | 672.4708 | 1086.1179 | 745.7374 | 0.49443 | 0.79845 | 0.53709 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | Existing | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 1.0264 | 0 | 1.1878 | Cap-Tons/1000 sf | 1015.6667 | 1593.6667 | 1155 | 0.48191 | 0.75339 | 0.52798 | 0 | 0 | 0 | 1015.6667 | 1593.6667 | 1155 | 0.48191 | 0.75339 | 0.52798 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | Existing | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.67965 | 0 | 0.78651 | Cap-Tons/1000 sf | 998.6442 | 1545.3109 | 1107.9109 | 0.63929 | 0.98763 | 0.68546 | 0 | 0 | 0 | 998.6442 | 1545.3109 | 1107.9109 | 0.63929 | 0.98763 | 0.68546 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | Existing | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.34638 | 0 | 0.37163 | Cap-Tons/1000 sf | 841.9955 | 1382.2148 | 951.8622 | 0.46675 | 0.76571 | 0.51408 | 0 | 0 | 0 | 841.9955 | 1382.2148 | 951.8622 | 0.46675 | 0.76571 | 0.51408 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | Existing | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.34652 | 0 | 0.40101 | Cap-Tons/1000 sf | 893.9387 | 1433.8978 | 1015.0387 | 0.49104 | 0.78653 | 0.53954 | 0 | 0 | 0 | 893.9387 | 1433.8978 | 1015.0387 | 0.49104 | 0.78653 | 0.53954 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTS | RETAIL - SMALL | Existing | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.39888 | 0 | 0.46159 | Cap-Tons/1000 sf | 846.607 | 1353.6783 | 951.8737 | 0.49975 | 0.79687 | 0.55108 | 0 | 0 | 0 | 846.607 | 1353.6783 | 951.8737 | 0.49975 | 0.79687 | 0.55108 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | SCN | STORAGE - CONDITIONED | Existing | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.22128 | 0 | 0.25607 | Cap-Tons/1000 sf | 635.2433 | 912.5167 | 712.7767 | 0.47387 | 0.66734 | 0.51187 | 0 | 0 | 0 | 635.2433 | 912.5167 | 712.7767 | 0.47387 | 0.66734 | 0.51187 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ASM | ASSEMBLY | New | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.83582 | 0 | 0.96724 | Cap-Tons/1000 sf | 1185.2 | 1394.6667 | 1289.5 | 0.66951 | 0.76951 | 0.71364 | 0 | 0 | 0 | 1185.2 | 1394.6667 | 1289.5 | 0.66951 | 0.76951 | 0.71364 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | New | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.4818 | 0 | 0.55756 | Cap-Tons/1000 sf | 831.5465 | 1007.3131 | 915.7798 | 0.37574 | 0.45924 | 0.42131 | 0 | 0 | 0 | 831.5465 | 1007.3131 | 915.7798 | 0.37574 | 0.45924 | 0.42131 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | New | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.51248 | 0 | 0.59306 | Cap-Tons/1000 sf | 687.0667 | 799.2333 | 741.6667 | 0.5345 | 0.62153 | 0.57786 | 0 | 0 | 0 | 687.0667 | 799.2333 | 741.6667 | 0.5345 | 0.62153 | 0.57786 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | New | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.6128 | 0 | 0.70915 | Cap-Tons/1000 sf | 972 | 1134 | 1039.9 | 0.63 | 0.735 | 0.6719 | 0 | 0 | 0 | 972 | 1134 | 1039.9 | 0.63 | 0.735 | 0.6719 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | New | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.49429 | 0 | 0.57201 | Cap-Tons/1000 sf | 822.2833 | 941.3167 | 880.2833 | 0.62432 | 0.71482 | 0.66998 | 0 | 0 | 0 | 822.2833 | 941.3167 | 880.2833 | 0.62432 | 0.71482 | 0.66998 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EUN | EDUCATION - UNIVERSITY | New | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.51877 | 0 | 0.55658 | Cap-Tons/1000 sf | 825.4885 | 1032.3885 | 923.9552 | 0.30089 | 0.38519 | 0.34985 | 0 | 0 | 0 | 825.4885 | 1032.3885 | 923.9552 | 0.30089 | 0.38519 | 0.34985 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | GRO | GROCERY | New | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.86635 | 0 | 0.92949 | Cap-Tons/1000 sf | 835.45 | 1089.7833 | 954.1167 | 0.19378 | 0.25685 | 0.21841 | 0 | 0 | 0 | 835.45 | 1089.7833 | 954.1167 | 0.19378 | 0.25685 | 0.21841 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | New | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.71085 | 0 | 0.82262 | Cap-Tons/1000 sf | 1212.25 | 1563.9167 | 1365.6833 | 0.16554 | 0.22547 | 0.19057 | 0 | 0 | 0 | 1212.25 | 1563.9167 | 1365.6833 | 0.16554 | 0.22547 | 0.19057 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HTL | LODGING - HOTEL | New | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.4087 | 0 | 0.43849 | Cap-Tons/1000 sf | 1475.2333 | 1807.9 | 1628.2333 | 0.28087 | 0.35621 | 0.31131 | 0 | 0 | 0 | 1475.2333 | 1807.9 | 1628.2333 | 0.28087 | 0.35621 | 0.31131 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | MTL | LODGING - MOTEL | New | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.4087 | 0 | 0.43849 | Cap-Tons/1000 sf | 1475.2333 | 1807.9 | 1628.2333 | 0.28087 | 0.35621 | 0.31131 | 0 | 0 | 0 | 1475.2333 | 1807.9 | 1628.2333 | 0.28087 | 0.35621 | 0.31131 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | New | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.76674 | 0 | 0.82262 | Cap-Tons/1000 sf | 1131.1667 | 1436.1667 | 1269.5333 | 0.16919 | 0.22639 | 0.19262 | 0 | 0 | 0 | 1131.1667 | 1436.1667 | 1269.5333 | 0.16919 | 0.22639 | 0.19262 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFL | OFFICE - LARGE | New | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.54446 | 0 | 0.58414 | Cap-Tons/1000 sf | 1269.5599 | 1435.5599 | 1345.8933 | 0.42105 | 0.49929 | 0.46932 | 0 | 0 | 0 | 1269.5599 | 1435.5599 | 1345.8933 | 0.42105 | 0.49929 | 0.46932 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFS | OFFICE - SMALL | New | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.59035 | 0 | 0.68317 | Cap-Tons/1000 sf | 928.9179 | 1086.1179 | 999.6846 | 0.44665 | 0.53015 | 0.49488 | 0 | 0 | 0 | 928.9179 | 1086.1179 | 999.6846 | 0.44665 | 0.53015 | 0.49488 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | New | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 1.0264 | 0 | 1.1878 | Cap-Tons/1000 sf | 1307 | 1593.6667 | 1442 | 0.41177 | 0.5022 | 0.45617 | 0 | 0 | 0 | 1307 | 1593.6667 | 1442 | 0.41177 | 0.5022 | 0.45617 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | New | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.67965 | 0 | 0.78651 | Cap-Tons/1000 sf | 1328.3109 | 1545.3109 | 1435.5109 | 0.68762 | 0.78749 | 0.73215 | 0 | 0 | 0 | 1328.3109 | 1545.3109 | 1435.5109 | 0.68762 | 0.78749 | 0.73215 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | New | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.34638 | 0 | 0.37163 | Cap-Tons/1000 sf | 1173.0148 | 1382.2148 | 1277.1815 | 0.45502 | 0.53832 | 0.50035 | 0 | 0 | 0 | 1173.0148 | 1382.2148 | 1277.1815 | 0.45502 | 0.53832 | 0.50035 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | New | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.34652 | 0 | 0.40101 | Cap-Tons/1000 sf | 1199.4978 | 1433.8978 | 1315.3644 | 0.45013 | 0.53826 | 0.49573 | 0 | 0 | 0 | 1199.4978 | 1433.8978 | 1315.3644 | 0.45013 | 0.53826 | 0.49573 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTS | RETAIL - SMALL | New | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.39888 | 0 | 0.46159 | Cap-Tons/1000 sf | 1157.745 | 1353.6783 | 1255.245 | 0.42827 | 0.50947 | 0.47477 | 0 | 0 | 0 | 1157.745 | 1353.6783 | 1255.245 | 0.42827 | 0.50947 | 0.47477 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | SCN | STORAGE - CONDITIONED | New | CZ04 | Sunnyvale Area (CZ04) |  |  |  | 1000 sf | 0.22128 | 0 | 0.25607 | Cap-Tons/1000 sf | 756.0833 | 912.5167 | 828.95 | 0.23971 | 0.29671 | 0.26314 | 0 | 0 | 0 | 756.0833 | 912.5167 | 828.95 | 0.23971 | 0.29671 | 0.26314 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ASM | ASSEMBLY | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.83582 | 0 | 0.96724 | Cap-Tons/1000 sf | 996.3333 | 1394.6667 | 1091.2 | 0.59861 | 0.83694 | 0.63551 | 0 | 0 | 0 | 996.3333 | 1394.6667 | 1091.2 | 0.59861 | 0.83694 | 0.63551 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.4818 | 0 | 0.55756 | Cap-Tons/1000 sf | 648.3879 | 1007.3131 | 728.8545 | 0.37914 | 0.58669 | 0.41654 | 0 | 0 | 0 | 648.3879 | 1007.3131 | 728.8545 | 0.37914 | 0.58669 | 0.41654 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.51248 | 0 | 0.59306 | Cap-Tons/1000 sf | 552.8733 | 799.2333 | 605.94 | 0.46826 | 0.67239 | 0.50336 | 0 | 0 | 0 | 552.8733 | 799.2333 | 605.94 | 0.46826 | 0.67239 | 0.50336 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.6128 | 0 | 0.70915 | Cap-Tons/1000 sf | 798.1667 | 1180.1667 | 877.8 | 0.45173 | 0.66206 | 0.48533 | 0 | 0 | 0 | 798.1667 | 1180.1667 | 877.8 | 0.45173 | 0.66206 | 0.48533 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.49429 | 0 | 0.57201 | Cap-Tons/1000 sf | 684.9833 | 941.3167 | 739.5167 | 0.60425 | 0.82025 | 0.64021 | 0 | 0 | 0 | 684.9833 | 941.3167 | 739.5167 | 0.60425 | 0.82025 | 0.64021 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EUN | EDUCATION - UNIVERSITY | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.51877 | 0 | 0.55658 | Cap-Tons/1000 sf | 619.4331 | 1032.3885 | 714.9998 | 0.31815 | 0.53026 | 0.35862 | 0 | 0 | 0 | 619.4331 | 1032.3885 | 714.9998 | 0.31815 | 0.53026 | 0.35862 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | GRO | GROCERY | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.86635 | 0 | 0.92949 | Cap-Tons/1000 sf | 760.0033 | 1089.7833 | 872.9367 | 0.28239 | 0.40657 | 0.30469 | 0 | 0 | 0 | 760.0033 | 1089.7833 | 872.9367 | 0.28239 | 0.40657 | 0.30469 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.71085 | 0 | 0.82262 | Cap-Tons/1000 sf | 938.35 | 1563.9167 | 1093.9833 | 0.21953 | 0.36588 | 0.25013 | 0 | 0 | 0 | 938.35 | 1563.9167 | 1093.9833 | 0.21953 | 0.36588 | 0.25013 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HTL | LODGING - HOTEL | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.4087 | 0 | 0.43849 | Cap-Tons/1000 sf | 1130.2067 | 1807.9 | 1283.04 | 0.34897 | 0.55762 | 0.3851 | 0 | 0 | 0 | 1130.2067 | 1807.9 | 1283.04 | 0.34897 | 0.55762 | 0.3851 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | MTL | LODGING - MOTEL | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.4087 | 0 | 0.43849 | Cap-Tons/1000 sf | 1130.2067 | 1807.9 | 1283.04 | 0.34897 | 0.55762 | 0.3851 | 0 | 0 | 0 | 1130.2067 | 1807.9 | 1283.04 | 0.34897 | 0.55762 | 0.3851 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.76674 | 0 | 0.82262 | Cap-Tons/1000 sf | 928.7 | 1436.1667 | 1066.2 | 0.25331 | 0.38813 | 0.28251 | 0 | 0 | 0 | 928.7 | 1436.1667 | 1066.2 | 0.25331 | 0.38813 | 0.28251 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFL | OFFICE - LARGE | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.54446 | 0 | 0.58414 | Cap-Tons/1000 sf | 1020.5599 | 1435.5599 | 1095.0933 | 0.58288 | 0.81621 | 0.61791 | 0 | 0 | 0 | 1020.5599 | 1435.5599 | 1095.0933 | 0.58288 | 0.81621 | 0.61791 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFS | OFFICE - SMALL | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.59035 | 0 | 0.68317 | Cap-Tons/1000 sf | 713.1179 | 1086.1179 | 780.3179 | 0.44519 | 0.67853 | 0.47799 | 0 | 0 | 0 | 713.1179 | 1086.1179 | 780.3179 | 0.44519 | 0.67853 | 0.47799 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 1.0264 | 0 | 1.1878 | Cap-Tons/1000 sf | 1088.3333 | 1593.6667 | 1213.2667 | 0.4253 | 0.61672 | 0.46127 | 0 | 0 | 0 | 1088.3333 | 1593.6667 | 1213.2667 | 0.4253 | 0.61672 | 0.46127 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.67965 | 0 | 0.78651 | Cap-Tons/1000 sf | 1146.9776 | 1545.3109 | 1239.4109 | 0.60543 | 0.81276 | 0.6404 | 0 | 0 | 0 | 1146.9776 | 1545.3109 | 1239.4109 | 0.60543 | 0.81276 | 0.6404 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.34638 | 0 | 0.37163 | Cap-Tons/1000 sf | 920.6622 | 1382.2148 | 1016.5289 | 0.44267 | 0.66068 | 0.47951 | 0 | 0 | 0 | 920.6622 | 1382.2148 | 1016.5289 | 0.44267 | 0.66068 | 0.47951 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.34652 | 0 | 0.40101 | Cap-Tons/1000 sf | 973.9387 | 1433.8978 | 1081.8053 | 0.47655 | 0.6982 | 0.51602 | 0 | 0 | 0 | 973.9387 | 1433.8978 | 1081.8053 | 0.47655 | 0.6982 | 0.51602 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTS | RETAIL - SMALL | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.39888 | 0 | 0.46159 | Cap-Tons/1000 sf | 912.607 | 1353.6783 | 1004.5737 | 0.47413 | 0.69934 | 0.51226 | 0 | 0 | 0 | 912.607 | 1353.6783 | 1004.5737 | 0.47413 | 0.69934 | 0.51226 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | SCN | STORAGE - CONDITIONED | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.22128 | 0 | 0.25607 | Cap-Tons/1000 sf | 689.2433 | 912.5167 | 755.9767 | 0.27282 | 0.356 | 0.29345 | 0 | 0 | 0 | 689.2433 | 912.5167 | 755.9767 | 0.27282 | 0.356 | 0.29345 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ASM | ASSEMBLY | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.83582 | 0 | 0.96724 | Cap-Tons/1000 sf | 1220.6333 | 1394.6667 | 1308.2 | 0.31585 | 0.37572 | 0.33952 | 0 | 0 | 0 | 1220.6333 | 1394.6667 | 1308.2 | 0.31585 | 0.37572 | 0.33952 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.4818 | 0 | 0.55756 | Cap-Tons/1000 sf | 841.3465 | 1007.3131 | 914.0798 | 0.25572 | 0.31432 | 0.27889 | 0 | 0 | 0 | 841.3465 | 1007.3131 | 914.0798 | 0.25572 | 0.31432 | 0.27889 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.51248 | 0 | 0.59306 | Cap-Tons/1000 sf | 691.9 | 799.2333 | 740.9 | 0.30373 | 0.35733 | 0.32557 | 0 | 0 | 0 | 691.9 | 799.2333 | 740.9 | 0.30373 | 0.35733 | 0.32557 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.6128 | 0 | 0.70915 | Cap-Tons/1000 sf | 1062.0333 | 1180.1667 | 1112 | 0.35511 | 0.40925 | 0.37931 | 0 | 0 | 0 | 1062.0333 | 1180.1667 | 1112 | 0.35511 | 0.40925 | 0.37931 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.49429 | 0 | 0.57201 | Cap-Tons/1000 sf | 832.3833 | 941.3167 | 880.85 | 0.371 | 0.42726 | 0.39246 | 0 | 0 | 0 | 832.3833 | 941.3167 | 880.85 | 0.371 | 0.42726 | 0.39246 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EUN | EDUCATION - UNIVERSITY | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.51877 | 0 | 0.55658 | Cap-Tons/1000 sf | 832.6552 | 1032.3885 | 920.6219 | 0.2344 | 0.30173 | 0.26086 | 0 | 0 | 0 | 832.6552 | 1032.3885 | 920.6219 | 0.2344 | 0.30173 | 0.26086 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | GRO | GROCERY | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.86635 | 0 | 0.92949 | Cap-Tons/1000 sf | 839.1167 | 1089.7833 | 949.5167 | 0.16531 | 0.21286 | 0.18851 | 0 | 0 | 0 | 839.1167 | 1089.7833 | 949.5167 | 0.16531 | 0.21286 | 0.18851 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.71085 | 0 | 0.82262 | Cap-Tons/1000 sf | 1215.25 | 1563.9167 | 1358.1833 | 0.1456 | 0.19573 | 0.1649 | 0 | 0 | 0 | 1215.25 | 1563.9167 | 1358.1833 | 0.1456 | 0.19573 | 0.1649 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HTL | LODGING - HOTEL | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.4087 | 0 | 0.43849 | Cap-Tons/1000 sf | 1494.2333 | 1807.9 | 1624.6333 | 0.25169 | 0.31216 | 0.27483 | 0 | 0 | 0 | 1494.2333 | 1807.9 | 1624.6333 | 0.25169 | 0.31216 | 0.27483 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | MTL | LODGING - MOTEL | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.4087 | 0 | 0.43849 | Cap-Tons/1000 sf | 1494.2333 | 1807.9 | 1624.6333 | 0.25169 | 0.31216 | 0.27483 | 0 | 0 | 0 | 1494.2333 | 1807.9 | 1624.6333 | 0.25169 | 0.31216 | 0.27483 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.76674 | 0 | 0.82262 | Cap-Tons/1000 sf | 1140.5 | 1436.1667 | 1261.2333 | 0.1435 | 0.1877 | 0.16123 | 0 | 0 | 0 | 1140.5 | 1436.1667 | 1261.2333 | 0.1435 | 0.1877 | 0.16123 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFL | OFFICE - LARGE | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.54446 | 0 | 0.58414 | Cap-Tons/1000 sf | 1272.9599 | 1435.5599 | 1342.2933 | 0.37115 | 0.43812 | 0.40805 | 0 | 0 | 0 | 1272.9599 | 1435.5599 | 1342.2933 | 0.37115 | 0.43812 | 0.40805 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFS | OFFICE - SMALL | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.59035 | 0 | 0.68317 | Cap-Tons/1000 sf | 939.4513 | 1086.1179 | 1000.6179 | 0.3641 | 0.43053 | 0.39706 | 0 | 0 | 0 | 939.4513 | 1086.1179 | 1000.6179 | 0.3641 | 0.43053 | 0.39706 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 1.0264 | 0 | 1.1878 | Cap-Tons/1000 sf | 1325 | 1593.6667 | 1439.5 | 0.26622 | 0.3224 | 0.29892 | 0 | 0 | 0 | 1325 | 1593.6667 | 1439.5 | 0.26622 | 0.3224 | 0.29892 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.67965 | 0 | 0.78651 | Cap-Tons/1000 sf | 1351.6442 | 1545.3109 | 1445.0442 | 0.37075 | 0.4355 | 0.40799 | 0 | 0 | 0 | 1351.6442 | 1545.3109 | 1445.0442 | 0.37075 | 0.4355 | 0.40799 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.34638 | 0 | 0.37163 | Cap-Tons/1000 sf | 1191.0481 | 1382.2148 | 1276.9481 | 0.29103 | 0.3487 | 0.31403 | 0 | 0 | 0 | 1191.0481 | 1382.2148 | 1276.9481 | 0.29103 | 0.3487 | 0.31403 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.34652 | 0 | 0.40101 | Cap-Tons/1000 sf | 1229.0644 | 1433.8978 | 1326.1644 | 0.30897 | 0.37171 | 0.33357 | 0 | 0 | 0 | 1229.0644 | 1433.8978 | 1326.1644 | 0.30897 | 0.37171 | 0.33357 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTS | RETAIL - SMALL | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.39888 | 0 | 0.46159 | Cap-Tons/1000 sf | 1174.6117 | 1353.6783 | 1251.1783 | 0.33057 | 0.3891 | 0.3527 | 0 | 0 | 0 | 1174.6117 | 1353.6783 | 1251.1783 | 0.33057 | 0.3891 | 0.3527 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | SCN | STORAGE - CONDITIONED | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.22128 | 0 | 0.25607 | Cap-Tons/1000 sf | 764.9167 | 912.5167 | 829.7833 | 0.21137 | 0.25277 | 0.22996 | 0 | 0 | 0 | 764.9167 | 912.5167 | 829.7833 | 0.21137 | 0.25277 | 0.22996 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ASM | ASSEMBLY | Existing | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.83582 | 0 | 0.96724 | Cap-Tons/1000 sf | 836.8 | 1394.6667 | 955.5333 | 0.50236 | 0.83726 | 0.55466 | 0 | 0 | 0 | 836.8 | 1394.6667 | 955.5333 | 0.50236 | 0.83726 | 0.55466 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | Existing | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.4818 | 0 | 0.55756 | Cap-Tons/1000 sf | 604.3879 | 1007.3131 | 716.1879 | 0.36486 | 0.60811 | 0.41336 | 0 | 0 | 0 | 604.3879 | 1007.3131 | 716.1879 | 0.36486 | 0.60811 | 0.41336 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | Existing | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.51248 | 0 | 0.59306 | Cap-Tons/1000 sf | 479.54 | 799.2333 | 553.84 | 0.18239 | 0.30398 | 0.20696 | 0 | 0 | 0 | 479.54 | 799.2333 | 553.84 | 0.18239 | 0.30398 | 0.20696 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | Existing | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.6128 | 0 | 0.70915 | Cap-Tons/1000 sf | 708.1 | 1180.1667 | 812.1333 | 0.303 | 0.50499 | 0.33636 | 0 | 0 | 0 | 708.1 | 1180.1667 | 812.1333 | 0.303 | 0.50499 | 0.33636 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | Existing | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.49429 | 0 | 0.57201 | Cap-Tons/1000 sf | 578.2567 | 941.3167 | 660.69 | 0.19501 | 0.31737 | 0.21914 | 0 | 0 | 0 | 578.2567 | 941.3167 | 660.69 | 0.19501 | 0.31737 | 0.21914 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EUN | EDUCATION - UNIVERSITY | Existing | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.51877 | 0 | 0.55658 | Cap-Tons/1000 sf | 619.4331 | 1032.3885 | 738.1331 | 0.33415 | 0.55692 | 0.38105 | 0 | 0 | 0 | 619.4331 | 1032.3885 | 738.1331 | 0.33415 | 0.55692 | 0.38105 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | GRO | GROCERY | Existing | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.86635 | 0 | 0.92949 | Cap-Tons/1000 sf | 653.87 | 1089.7833 | 781.5367 | 0.33974 | 0.56623 | 0.37637 | 0 | 0 | 0 | 653.87 | 1089.7833 | 781.5367 | 0.33974 | 0.56623 | 0.37637 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | Existing | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.71085 | 0 | 0.82262 | Cap-Tons/1000 sf | 938.35 | 1563.9167 | 1118.35 | 0.28095 | 0.46826 | 0.32289 | 0 | 0 | 0 | 938.35 | 1563.9167 | 1118.35 | 0.28095 | 0.46826 | 0.32289 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HTL | LODGING - HOTEL | Existing | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.4087 | 0 | 0.43849 | Cap-Tons/1000 sf | 1084.74 | 1807.9 | 1264.74 | 0.39413 | 0.65688 | 0.44686 | 0 | 0 | 0 | 1084.74 | 1807.9 | 1264.74 | 0.39413 | 0.65688 | 0.44686 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | MTL | LODGING - MOTEL | Existing | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.4087 | 0 | 0.43849 | Cap-Tons/1000 sf | 1084.74 | 1807.9 | 1264.74 | 0.39413 | 0.65688 | 0.44686 | 0 | 0 | 0 | 1084.74 | 1807.9 | 1264.74 | 0.39413 | 0.65688 | 0.44686 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | Existing | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.76674 | 0 | 0.82262 | Cap-Tons/1000 sf | 861.7 | 1436.1667 | 1027.3667 | 0.29169 | 0.48615 | 0.32999 | 0 | 0 | 0 | 861.7 | 1436.1667 | 1027.3667 | 0.29169 | 0.48615 | 0.32999 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFL | OFFICE - LARGE | Existing | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.54446 | 0 | 0.58414 | Cap-Tons/1000 sf | 913.8933 | 1435.5599 | 1004.2599 | 0.56994 | 0.89561 | 0.62034 | 0 | 0 | 0 | 913.8933 | 1435.5599 | 1004.2599 | 0.56994 | 0.89561 | 0.62034 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFS | OFFICE - SMALL | Existing | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.59035 | 0 | 0.68317 | Cap-Tons/1000 sf | 651.6708 | 1086.1179 | 735.3374 | 0.45559 | 0.75932 | 0.50673 | 0 | 0 | 0 | 651.6708 | 1086.1179 | 735.3374 | 0.45559 | 0.75932 | 0.50673 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | Existing | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 1.0264 | 0 | 1.1878 | Cap-Tons/1000 sf | 956.2 | 1593.6667 | 1111.2 | 0.43484 | 0.72474 | 0.48081 | 0 | 0 | 0 | 956.2 | 1593.6667 | 1111.2 | 0.43484 | 0.72474 | 0.48081 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | Existing | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.67965 | 0 | 0.78651 | Cap-Tons/1000 sf | 927.1865 | 1545.3109 | 1050.1865 | 0.55264 | 0.92107 | 0.60484 | 0 | 0 | 0 | 927.1865 | 1545.3109 | 1050.1865 | 0.55264 | 0.92107 | 0.60484 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | Existing | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.34638 | 0 | 0.37163 | Cap-Tons/1000 sf | 829.3289 | 1382.2148 | 950.1622 | 0.44438 | 0.74063 | 0.49371 | 0 | 0 | 0 | 829.3289 | 1382.2148 | 950.1622 | 0.44438 | 0.74063 | 0.49371 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | Existing | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.34652 | 0 | 0.40101 | Cap-Tons/1000 sf | 860.3387 | 1433.8978 | 992.672 | 0.44999 | 0.74999 | 0.49969 | 0 | 0 | 0 | 860.3387 | 1433.8978 | 992.672 | 0.44999 | 0.74999 | 0.49969 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTS | RETAIL - SMALL | Existing | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.39888 | 0 | 0.46159 | Cap-Tons/1000 sf | 812.207 | 1353.6783 | 931.2737 | 0.46749 | 0.77914 | 0.52119 | 0 | 0 | 0 | 812.207 | 1353.6783 | 931.2737 | 0.46749 | 0.77914 | 0.52119 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | SCN | STORAGE - CONDITIONED | Existing | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.22128 | 0 | 0.25607 | Cap-Tons/1000 sf | 567.91 | 912.5167 | 658.4433 | 0.40486 | 0.64818 | 0.44726 | 0 | 0 | 0 | 567.91 | 912.5167 | 658.4433 | 0.40486 | 0.64818 | 0.44726 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ASM | ASSEMBLY | New | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.83582 | 0 | 0.96724 | Cap-Tons/1000 sf | 1176.9333 | 1394.6667 | 1288.1 | 0.38204 | 0.4713 | 0.43087 | 0 | 0 | 0 | 1176.9333 | 1394.6667 | 1288.1 | 0.38204 | 0.4713 | 0.43087 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | New | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.4818 | 0 | 0.55756 | Cap-Tons/1000 sf | 800.1465 | 1007.3131 | 903.0131 | 0.29625 | 0.39013 | 0.35029 | 0 | 0 | 0 | 800.1465 | 1007.3131 | 903.0131 | 0.29625 | 0.39013 | 0.35029 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | New | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.51248 | 0 | 0.59306 | Cap-Tons/1000 sf | 671.8 | 799.2333 | 736.2667 | 0.15153 | 0.18733 | 0.16576 | 0 | 0 | 0 | 671.8 | 799.2333 | 736.2667 | 0.15153 | 0.18733 | 0.16576 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | New | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.6128 | 0 | 0.70915 | Cap-Tons/1000 sf | 1017.9667 | 1180.1667 | 1099.1 | 0.20919 | 0.26125 | 0.22812 | 0 | 0 | 0 | 1017.9667 | 1180.1667 | 1099.1 | 0.20919 | 0.26125 | 0.22812 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | New | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.49429 | 0 | 0.57201 | Cap-Tons/1000 sf | 804.85 | 941.3167 | 873.4167 | 0.14242 | 0.17268 | 0.15388 | 0 | 0 | 0 | 804.85 | 941.3167 | 873.4167 | 0.14242 | 0.17268 | 0.15388 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EUN | EDUCATION - UNIVERSITY | New | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.51877 | 0 | 0.55658 | Cap-Tons/1000 sf | 817.5885 | 1032.3885 | 926.6885 | 0.24691 | 0.33224 | 0.27631 | 0 | 0 | 0 | 817.5885 | 1032.3885 | 926.6885 | 0.24691 | 0.33224 | 0.27631 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | GRO | GROCERY | New | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.86635 | 0 | 0.92949 | Cap-Tons/1000 sf | 823.45 | 1089.7833 | 939.1167 | 0.19456 | 0.26789 | 0.21549 | 0 | 0 | 0 | 823.45 | 1089.7833 | 939.1167 | 0.19456 | 0.26789 | 0.21549 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | New | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.71085 | 0 | 0.82262 | Cap-Tons/1000 sf | 1212.25 | 1563.9167 | 1373.5833 | 0.17508 | 0.24241 | 0.19924 | 0 | 0 | 0 | 1212.25 | 1563.9167 | 1373.5833 | 0.17508 | 0.24241 | 0.19924 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HTL | LODGING - HOTEL | New | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.4087 | 0 | 0.43849 | Cap-Tons/1000 sf | 1469.8333 | 1807.9 | 1628.8333 | 0.28792 | 0.37125 | 0.31649 | 0 | 0 | 0 | 1469.8333 | 1807.9 | 1628.8333 | 0.28792 | 0.37125 | 0.31649 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | MTL | LODGING - MOTEL | New | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.4087 | 0 | 0.43849 | Cap-Tons/1000 sf | 1469.8333 | 1807.9 | 1628.8333 | 0.28792 | 0.37125 | 0.31649 | 0 | 0 | 0 | 1469.8333 | 1807.9 | 1628.8333 | 0.28792 | 0.37125 | 0.31649 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | New | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.76674 | 0 | 0.82262 | Cap-Tons/1000 sf | 1124.8667 | 1436.1667 | 1261.8667 | 0.17058 | 0.23465 | 0.19035 | 0 | 0 | 0 | 1124.8667 | 1436.1667 | 1261.8667 | 0.17058 | 0.23465 | 0.19035 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFL | OFFICE - LARGE | New | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.54446 | 0 | 0.58414 | Cap-Tons/1000 sf | 1264.1599 | 1435.5599 | 1347.6933 | 0.433 | 0.52167 | 0.46853 | 0 | 0 | 0 | 1264.1599 | 1435.5599 | 1347.6933 | 0.433 | 0.52167 | 0.46853 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFS | OFFICE - SMALL | New | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.59035 | 0 | 0.68317 | Cap-Tons/1000 sf | 921.7513 | 1086.1179 | 1000.5179 | 0.36044 | 0.44977 | 0.39747 | 0 | 0 | 0 | 921.7513 | 1086.1179 | 1000.5179 | 0.36044 | 0.44977 | 0.39747 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | New | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 1.0264 | 0 | 1.1878 | Cap-Tons/1000 sf | 1296 | 1593.6667 | 1441.6667 | 0.35619 | 0.44603 | 0.40186 | 0 | 0 | 0 | 1296 | 1593.6667 | 1441.6667 | 0.35619 | 0.44603 | 0.40186 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | New | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.67965 | 0 | 0.78651 | Cap-Tons/1000 sf | 1306.9109 | 1545.3109 | 1422.2442 | 0.45783 | 0.55373 | 0.50823 | 0 | 0 | 0 | 1306.9109 | 1545.3109 | 1422.2442 | 0.45783 | 0.55373 | 0.50823 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | New | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.34638 | 0 | 0.37163 | Cap-Tons/1000 sf | 1169.5481 | 1382.2148 | 1283.3481 | 0.32291 | 0.40758 | 0.35204 | 0 | 0 | 0 | 1169.5481 | 1382.2148 | 1283.3481 | 0.32291 | 0.40758 | 0.35204 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | New | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.34652 | 0 | 0.40101 | Cap-Tons/1000 sf | 1197.3311 | 1433.8978 | 1320.6644 | 0.33078 | 0.41678 | 0.35928 | 0 | 0 | 0 | 1197.3311 | 1433.8978 | 1320.6644 | 0.33078 | 0.41678 | 0.35928 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTS | RETAIL - SMALL | New | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.39888 | 0 | 0.46159 | Cap-Tons/1000 sf | 1149.0117 | 1353.6783 | 1258.9117 | 0.36574 | 0.45574 | 0.39684 | 0 | 0 | 0 | 1149.0117 | 1353.6783 | 1258.9117 | 0.36574 | 0.45574 | 0.39684 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | SCN | STORAGE - CONDITIONED | New | CZ11 | Red Bluff Area (CZ11) |  |  |  | 1000 sf | 0.22128 | 0 | 0.25607 | Cap-Tons/1000 sf | 748.7167 | 912.5167 | 824.25 | 0.2402 | 0.3082 | 0.2616 | 0 | 0 | 0 | 748.7167 | 912.5167 | 824.25 | 0.2402 | 0.3082 | 0.2616 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ASM | ASSEMBLY | Existing | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.83582 | 0 | 0.96724 | Cap-Tons/1000 sf | 876.1333 | 1394.6667 | 986.1333 | 0.51018 | 0.80972 | 0.55515 | 0 | 0 | 0 | 876.1333 | 1394.6667 | 986.1333 | 0.51018 | 0.80972 | 0.55515 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | Existing | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.4818 | 0 | 0.55756 | Cap-Tons/1000 sf | 604.3879 | 1007.3131 | 704.6212 | 0.3483 | 0.5805 | 0.39523 | 0 | 0 | 0 | 604.3879 | 1007.3131 | 704.6212 | 0.3483 | 0.5805 | 0.39523 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | Existing | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.51248 | 0 | 0.59306 | Cap-Tons/1000 sf | 498.8733 | 799.2333 | 566.0067 | 0.15656 | 0.25062 | 0.17666 | 0 | 0 | 0 | 498.8733 | 799.2333 | 566.0067 | 0.15656 | 0.25062 | 0.17666 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | Existing | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.6128 | 0 | 0.70915 | Cap-Tons/1000 sf | 717.8333 | 1180.1667 | 813.3333 | 0.29777 | 0.48852 | 0.3313 | 0 | 0 | 0 | 717.8333 | 1180.1667 | 813.3333 | 0.29777 | 0.48852 | 0.3313 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | Existing | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.49429 | 0 | 0.57201 | Cap-Tons/1000 sf | 618.2567 | 941.3167 | 689.0567 | 0.16554 | 0.25136 | 0.18324 | 0 | 0 | 0 | 618.2567 | 941.3167 | 689.0567 | 0.16554 | 0.25136 | 0.18324 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EUN | EDUCATION - UNIVERSITY | Existing | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.51877 | 0 | 0.55658 | Cap-Tons/1000 sf | 619.4331 | 1032.3885 | 729.3998 | 0.32341 | 0.53902 | 0.37104 | 0 | 0 | 0 | 619.4331 | 1032.3885 | 729.3998 | 0.32341 | 0.53902 | 0.37104 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | GRO | GROCERY | Existing | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.86635 | 0 | 0.92949 | Cap-Tons/1000 sf | 688.67 | 1089.7833 | 811.0033 | 0.35407 | 0.55855 | 0.3896 | 0 | 0 | 0 | 688.67 | 1089.7833 | 811.0033 | 0.35407 | 0.55855 | 0.3896 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | Existing | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.71085 | 0 | 0.82262 | Cap-Tons/1000 sf | 938.35 | 1563.9167 | 1106.6833 | 0.27116 | 0.45193 | 0.31293 | 0 | 0 | 0 | 938.35 | 1563.9167 | 1106.6833 | 0.27116 | 0.45193 | 0.31293 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HTL | LODGING - HOTEL | Existing | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.4087 | 0 | 0.43849 | Cap-Tons/1000 sf | 1088.8733 | 1807.9 | 1256.8733 | 0.39653 | 0.65818 | 0.44637 | 0 | 0 | 0 | 1088.8733 | 1807.9 | 1256.8733 | 0.39653 | 0.65818 | 0.44637 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | MTL | LODGING - MOTEL | Existing | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.4087 | 0 | 0.43849 | Cap-Tons/1000 sf | 1088.8733 | 1807.9 | 1256.8733 | 0.39653 | 0.65818 | 0.44637 | 0 | 0 | 0 | 1088.8733 | 1807.9 | 1256.8733 | 0.39653 | 0.65818 | 0.44637 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | Existing | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.76674 | 0 | 0.82262 | Cap-Tons/1000 sf | 861.7 | 1436.1667 | 1018.0333 | 0.28963 | 0.48272 | 0.33007 | 0 | 0 | 0 | 861.7 | 1436.1667 | 1018.0333 | 0.28963 | 0.48272 | 0.33007 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFL | OFFICE - LARGE | Existing | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.54446 | 0 | 0.58414 | Cap-Tons/1000 sf | 941.8933 | 1435.5599 | 1027.0266 | 0.61354 | 0.93554 | 0.66377 | 0 | 0 | 0 | 941.8933 | 1435.5599 | 1027.0266 | 0.61354 | 0.93554 | 0.66377 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFS | OFFICE - SMALL | Existing | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.59035 | 0 | 0.68317 | Cap-Tons/1000 sf | 660.4708 | 1086.1179 | 736.9041 | 0.48081 | 0.79031 | 0.52835 | 0 | 0 | 0 | 660.4708 | 1086.1179 | 736.9041 | 0.48081 | 0.79031 | 0.52835 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | Existing | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 1.0264 | 0 | 1.1878 | Cap-Tons/1000 sf | 1004.3333 | 1593.6667 | 1147.6667 | 0.44309 | 0.70022 | 0.48926 | 0 | 0 | 0 | 1004.3333 | 1593.6667 | 1147.6667 | 0.44309 | 0.70022 | 0.48926 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | Existing | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.67965 | 0 | 0.78651 | Cap-Tons/1000 sf | 927.1865 | 1545.3109 | 1047.4865 | 0.56127 | 0.93545 | 0.6137 | 0 | 0 | 0 | 927.1865 | 1545.3109 | 1047.4865 | 0.56127 | 0.93545 | 0.6137 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | Existing | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.34638 | 0 | 0.37163 | Cap-Tons/1000 sf | 842.6622 | 1382.2148 | 953.6622 | 0.45072 | 0.73845 | 0.49906 | 0 | 0 | 0 | 842.6622 | 1382.2148 | 953.6622 | 0.45072 | 0.73845 | 0.49906 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | Existing | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.34652 | 0 | 0.40101 | Cap-Tons/1000 sf | 898.6053 | 1433.8978 | 1021.1387 | 0.47043 | 0.74849 | 0.51883 | 0 | 0 | 0 | 898.6053 | 1433.8978 | 1021.1387 | 0.47043 | 0.74849 | 0.51883 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTS | RETAIL - SMALL | Existing | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.39888 | 0 | 0.46159 | Cap-Tons/1000 sf | 818.607 | 1353.6783 | 930.4403 | 0.48623 | 0.8036 | 0.5422 | 0 | 0 | 0 | 818.607 | 1353.6783 | 930.4403 | 0.48623 | 0.8036 | 0.5422 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | SCN | STORAGE - CONDITIONED | Existing | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.22128 | 0 | 0.25607 | Cap-Tons/1000 sf | 609.91 | 912.5167 | 693.4767 | 0.43141 | 0.63633 | 0.47228 | 0 | 0 | 0 | 609.91 | 912.5167 | 693.4767 | 0.43141 | 0.63633 | 0.47228 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ASM | ASSEMBLY | New | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.83582 | 0 | 0.96724 | Cap-Tons/1000 sf | 1180.3333 | 1394.6667 | 1278.1 | 0.51656 | 0.60622 | 0.55509 | 0 | 0 | 0 | 1180.3333 | 1394.6667 | 1278.1 | 0.51656 | 0.60622 | 0.55509 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | New | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.4818 | 0 | 0.55756 | Cap-Tons/1000 sf | 823.1798 | 1007.3131 | 914.2798 | 0.26613 | 0.34086 | 0.31009 | 0 | 0 | 0 | 823.1798 | 1007.3131 | 914.2798 | 0.26613 | 0.34086 | 0.31009 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | New | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.51248 | 0 | 0.59306 | Cap-Tons/1000 sf | 679.3 | 799.2333 | 737.8333 | 0.038806 | 0.047006 | 0.042196 | 0 | 0 | 0 | 679.3 | 799.2333 | 737.8333 | 0.038806 | 0.047006 | 0.042196 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | New | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.6128 | 0 | 0.70915 | Cap-Tons/1000 sf | 1035.0667 | 1180.1667 | 1105.2667 | 0.19801 | 0.23888 | 0.21431 | 0 | 0 | 0 | 1035.0667 | 1180.1667 | 1105.2667 | 0.19801 | 0.23888 | 0.21431 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | New | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.49429 | 0 | 0.57201 | Cap-Tons/1000 sf | 812.35 | 941.3167 | 875.35 | 0.038118 | 0.045384 | 0.041091 | 0 | 0 | 0 | 812.35 | 941.3167 | 875.35 | 0.038118 | 0.045384 | 0.041091 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EUN | EDUCATION - UNIVERSITY | New | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.51877 | 0 | 0.55658 | Cap-Tons/1000 sf | 825.1219 | 1032.3885 | 927.0219 | 0.23956 | 0.31556 | 0.26866 | 0 | 0 | 0 | 825.1219 | 1032.3885 | 927.0219 | 0.23956 | 0.31556 | 0.26866 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | GRO | GROCERY | New | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.86635 | 0 | 0.92949 | Cap-Tons/1000 sf | 834.7833 | 1089.7833 | 953.45 | 0.18588 | 0.24994 | 0.20908 | 0 | 0 | 0 | 834.7833 | 1089.7833 | 953.45 | 0.18588 | 0.24994 | 0.20908 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | New | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.71085 | 0 | 0.82262 | Cap-Tons/1000 sf | 1218.9833 | 1563.9167 | 1372.3833 | 0.17185 | 0.23425 | 0.19672 | 0 | 0 | 0 | 1218.9833 | 1563.9167 | 1372.3833 | 0.17185 | 0.23425 | 0.19672 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HTL | LODGING - HOTEL | New | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.4087 | 0 | 0.43849 | Cap-Tons/1000 sf | 1480.2333 | 1807.9 | 1633.2333 | 0.2875 | 0.36483 | 0.31697 | 0 | 0 | 0 | 1480.2333 | 1807.9 | 1633.2333 | 0.2875 | 0.36483 | 0.31697 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | MTL | LODGING - MOTEL | New | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.4087 | 0 | 0.43849 | Cap-Tons/1000 sf | 1480.2333 | 1807.9 | 1633.2333 | 0.2875 | 0.36483 | 0.31697 | 0 | 0 | 0 | 1480.2333 | 1807.9 | 1633.2333 | 0.2875 | 0.36483 | 0.31697 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | New | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.76674 | 0 | 0.82262 | Cap-Tons/1000 sf | 1131.4 | 1436.1667 | 1272.8 | 0.17107 | 0.23107 | 0.1948 | 0 | 0 | 0 | 1131.4 | 1436.1667 | 1272.8 | 0.17107 | 0.23107 | 0.1948 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFL | OFFICE - LARGE | New | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.54446 | 0 | 0.58414 | Cap-Tons/1000 sf | 1270.4599 | 1435.5599 | 1348.2933 | 0.4333 | 0.51597 | 0.46597 | 0 | 0 | 0 | 1270.4599 | 1435.5599 | 1348.2933 | 0.4333 | 0.51597 | 0.46597 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFS | OFFICE - SMALL | New | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.59035 | 0 | 0.68317 | Cap-Tons/1000 sf | 933.1846 | 1086.1179 | 1003.1846 | 0.35905 | 0.43905 | 0.38995 | 0 | 0 | 0 | 933.1846 | 1086.1179 | 1003.1846 | 0.35905 | 0.43905 | 0.38995 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | New | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 1.0264 | 0 | 1.1878 | Cap-Tons/1000 sf | 1308 | 1593.6667 | 1441.3333 | 0.33469 | 0.41332 | 0.37702 | 0 | 0 | 0 | 1308 | 1593.6667 | 1441.3333 | 0.33469 | 0.41332 | 0.37702 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | New | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.67965 | 0 | 0.78651 | Cap-Tons/1000 sf | 1310.3109 | 1545.3109 | 1428.6442 | 0.53004 | 0.62898 | 0.58051 | 0 | 0 | 0 | 1310.3109 | 1545.3109 | 1428.6442 | 0.53004 | 0.62898 | 0.58051 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | New | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.34638 | 0 | 0.37163 | Cap-Tons/1000 sf | 1177.8815 | 1382.2148 | 1282.4815 | 0.31928 | 0.39528 | 0.34875 | 0 | 0 | 0 | 1177.8815 | 1382.2148 | 1282.4815 | 0.31928 | 0.39528 | 0.34875 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | New | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.34652 | 0 | 0.40101 | Cap-Tons/1000 sf | 1205.1311 | 1433.8978 | 1319.6311 | 0.36278 | 0.44152 | 0.40722 | 0 | 0 | 0 | 1205.1311 | 1433.8978 | 1319.6311 | 0.36278 | 0.44152 | 0.40722 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTS | RETAIL - SMALL | New | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.39888 | 0 | 0.46159 | Cap-Tons/1000 sf | 1151.0783 | 1353.6783 | 1255.845 | 0.3679 | 0.45194 | 0.41897 | 0 | 0 | 0 | 1151.0783 | 1353.6783 | 1255.845 | 0.3679 | 0.45194 | 0.41897 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | SCN | STORAGE - CONDITIONED | New | CZ12 | Sacramento Area (CZ12) |  |  |  | 1000 sf | 0.22128 | 0 | 0.25607 | Cap-Tons/1000 sf | 752.5167 | 912.5167 | 829.05 | 0.23894 | 0.30107 | 0.26287 | 0 | 0 | 0 | 752.5167 | 912.5167 | 829.05 | 0.23894 | 0.30107 | 0.26287 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ASM | ASSEMBLY | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.83582 | 0 | 0.96724 | Cap-Tons/1000 sf | 836.8 | 1394.6667 | 959.5667 | 0.4386 | 0.731 | 0.4844 | 0 | 0 | 0 | 836.8 | 1394.6667 | 959.5667 | 0.4386 | 0.731 | 0.4844 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.4818 | 0 | 0.55756 | Cap-Tons/1000 sf | 604.3879 | 1007.3131 | 716.6879 | 0.31221 | 0.52035 | 0.35978 | 0 | 0 | 0 | 604.3879 | 1007.3131 | 716.6879 | 0.31221 | 0.52035 | 0.35978 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.51248 | 0 | 0.59306 | Cap-Tons/1000 sf | 479.54 | 799.2333 | 556.4733 | 0.15751 | 0.26252 | 0.18221 | 0 | 0 | 0 | 479.54 | 799.2333 | 556.4733 | 0.15751 | 0.26252 | 0.18221 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.6128 | 0 | 0.70915 | Cap-Tons/1000 sf | 708.1 | 1180.1667 | 816.2667 | 0.25008 | 0.4168 | 0.28368 | 0 | 0 | 0 | 708.1 | 1180.1667 | 816.2667 | 0.25008 | 0.4168 | 0.28368 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.49429 | 0 | 0.57201 | Cap-Tons/1000 sf | 565.59 | 941.3167 | 651.2233 | 0.15906 | 0.26472 | 0.18233 | 0 | 0 | 0 | 565.59 | 941.3167 | 651.2233 | 0.15906 | 0.26472 | 0.18233 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EUN | EDUCATION - UNIVERSITY | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.51877 | 0 | 0.55658 | Cap-Tons/1000 sf | 619.4331 | 1032.3885 | 738.8665 | 0.29542 | 0.49236 | 0.34262 | 0 | 0 | 0 | 619.4331 | 1032.3885 | 738.8665 | 0.29542 | 0.49236 | 0.34262 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | GRO | GROCERY | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.86635 | 0 | 0.92949 | Cap-Tons/1000 sf | 653.87 | 1089.7833 | 783.2033 | 0.29968 | 0.49947 | 0.33661 | 0 | 0 | 0 | 653.87 | 1089.7833 | 783.2033 | 0.29968 | 0.49947 | 0.33661 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.71085 | 0 | 0.82262 | Cap-Tons/1000 sf | 938.35 | 1563.9167 | 1121.6833 | 0.25548 | 0.42579 | 0.29801 | 0 | 0 | 0 | 938.35 | 1563.9167 | 1121.6833 | 0.25548 | 0.42579 | 0.29801 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HTL | LODGING - HOTEL | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.4087 | 0 | 0.43849 | Cap-Tons/1000 sf | 1084.74 | 1807.9 | 1270.4067 | 0.36435 | 0.60725 | 0.41535 | 0 | 0 | 0 | 1084.74 | 1807.9 | 1270.4067 | 0.36435 | 0.60725 | 0.41535 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | MTL | LODGING - MOTEL | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.4087 | 0 | 0.43849 | Cap-Tons/1000 sf | 1084.74 | 1807.9 | 1270.4067 | 0.36435 | 0.60725 | 0.41535 | 0 | 0 | 0 | 1084.74 | 1807.9 | 1270.4067 | 0.36435 | 0.60725 | 0.41535 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.76674 | 0 | 0.82262 | Cap-Tons/1000 sf | 861.7 | 1436.1667 | 1030.7 | 0.26059 | 0.43431 | 0.30085 | 0 | 0 | 0 | 861.7 | 1436.1667 | 1030.7 | 0.26059 | 0.43431 | 0.30085 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFL | OFFICE - LARGE | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.54446 | 0 | 0.58414 | Cap-Tons/1000 sf | 904.8933 | 1435.5599 | 996.5599 | 0.53521 | 0.84955 | 0.58341 | 0 | 0 | 0 | 904.8933 | 1435.5599 | 996.5599 | 0.53521 | 0.84955 | 0.58341 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFS | OFFICE - SMALL | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.59035 | 0 | 0.68317 | Cap-Tons/1000 sf | 651.6708 | 1086.1179 | 738.0041 | 0.42403 | 0.70672 | 0.4725 | 0 | 0 | 0 | 651.6708 | 1086.1179 | 738.0041 | 0.42403 | 0.70672 | 0.4725 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 1.0264 | 0 | 1.1878 | Cap-Tons/1000 sf | 956.2 | 1593.6667 | 1115.5333 | 0.38064 | 0.6344 | 0.42781 | 0 | 0 | 0 | 956.2 | 1593.6667 | 1115.5333 | 0.38064 | 0.6344 | 0.42781 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.67965 | 0 | 0.78651 | Cap-Tons/1000 sf | 927.1865 | 1545.3109 | 1052.1865 | 0.47797 | 0.79662 | 0.52421 | 0 | 0 | 0 | 927.1865 | 1545.3109 | 1052.1865 | 0.47797 | 0.79662 | 0.52421 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.34638 | 0 | 0.37163 | Cap-Tons/1000 sf | 829.3289 | 1382.2148 | 954.5289 | 0.41049 | 0.68414 | 0.46122 | 0 | 0 | 0 | 829.3289 | 1382.2148 | 954.5289 | 0.41049 | 0.68414 | 0.46122 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.34652 | 0 | 0.40101 | Cap-Tons/1000 sf | 860.3387 | 1433.8978 | 998.0053 | 0.41177 | 0.68629 | 0.46254 | 0 | 0 | 0 | 860.3387 | 1433.8978 | 998.0053 | 0.41177 | 0.68629 | 0.46254 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTS | RETAIL - SMALL | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.39888 | 0 | 0.46159 | Cap-Tons/1000 sf | 812.207 | 1353.6783 | 936.8737 | 0.43677 | 0.72795 | 0.494 | 0 | 0 | 0 | 812.207 | 1353.6783 | 936.8737 | 0.43677 | 0.72795 | 0.494 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | SCN | STORAGE - CONDITIONED | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.22128 | 0 | 0.25607 | Cap-Tons/1000 sf | 547.51 | 912.5167 | 643.11 | 0.34388 | 0.57313 | 0.38851 | 0 | 0 | 0 | 547.51 | 912.5167 | 643.11 | 0.34388 | 0.57313 | 0.38851 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ASM | ASSEMBLY | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.83582 | 0 | 0.96724 | Cap-Tons/1000 sf | 1155.7667 | 1394.6667 | 1271.1667 | 0.62603 | 0.73183 | 0.66873 | 0 | 0 | 0 | 1155.7667 | 1394.6667 | 1271.1667 | 0.62603 | 0.73183 | 0.66873 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.4818 | 0 | 0.55756 | Cap-Tons/1000 sf | 797.3798 | 1007.3131 | 906.6131 | 0.40494 | 0.5 | 0.45334 | 0 | 0 | 0 | 797.3798 | 1007.3131 | 906.6131 | 0.40494 | 0.5 | 0.45334 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.51248 | 0 | 0.59306 | Cap-Tons/1000 sf | 666.2 | 799.2333 | 732.8333 | 0.15127 | 0.18704 | 0.1706 | 0 | 0 | 0 | 666.2 | 799.2333 | 732.8333 | 0.15127 | 0.18704 | 0.1706 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.6128 | 0 | 0.70915 | Cap-Tons/1000 sf | 1010.2 | 1180.1667 | 1096.9 | 0.1847 | 0.2335 | 0.20407 | 0 | 0 | 0 | 1010.2 | 1180.1667 | 1096.9 | 0.1847 | 0.2335 | 0.20407 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.49429 | 0 | 0.57201 | Cap-Tons/1000 sf | 795.9167 | 941.3167 | 869.25 | 0.12286 | 0.15053 | 0.13456 | 0 | 0 | 0 | 795.9167 | 941.3167 | 869.25 | 0.12286 | 0.15053 | 0.13456 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EUN | EDUCATION - UNIVERSITY | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.51877 | 0 | 0.55658 | Cap-Tons/1000 sf | 817.8219 | 1032.3885 | 928.4885 | 0.22522 | 0.30085 | 0.27036 | 0 | 0 | 0 | 817.8219 | 1032.3885 | 928.4885 | 0.22522 | 0.30085 | 0.27036 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | GRO | GROCERY | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.86635 | 0 | 0.92949 | Cap-Tons/1000 sf | 822.7833 | 1089.7833 | 950.1167 | 0.17343 | 0.2399 | 0.19843 | 0 | 0 | 0 | 822.7833 | 1089.7833 | 950.1167 | 0.17343 | 0.2399 | 0.19843 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.71085 | 0 | 0.82262 | Cap-Tons/1000 sf | 1212.1167 | 1563.9167 | 1378.7833 | 0.16397 | 0.22757 | 0.1892 | 0 | 0 | 0 | 1212.1167 | 1563.9167 | 1378.7833 | 0.16397 | 0.22757 | 0.1892 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HTL | LODGING - HOTEL | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.4087 | 0 | 0.43849 | Cap-Tons/1000 sf | 1462.4667 | 1807.9 | 1633.8 | 0.26669 | 0.34602 | 0.29699 | 0 | 0 | 0 | 1462.4667 | 1807.9 | 1633.8 | 0.26669 | 0.34602 | 0.29699 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | MTL | LODGING - MOTEL | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.4087 | 0 | 0.43849 | Cap-Tons/1000 sf | 1462.4667 | 1807.9 | 1633.8 | 0.26669 | 0.34602 | 0.29699 | 0 | 0 | 0 | 1462.4667 | 1807.9 | 1633.8 | 0.26669 | 0.34602 | 0.29699 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.76674 | 0 | 0.82262 | Cap-Tons/1000 sf | 1124.1667 | 1436.1667 | 1277.8333 | 0.15805 | 0.21799 | 0.18182 | 0 | 0 | 0 | 1124.1667 | 1436.1667 | 1277.8333 | 0.15805 | 0.21799 | 0.18182 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFL | OFFICE - LARGE | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.54446 | 0 | 0.58414 | Cap-Tons/1000 sf | 1265.7266 | 1435.5599 | 1350.9933 | 0.4057 | 0.48837 | 0.43813 | 0 | 0 | 0 | 1265.7266 | 1435.5599 | 1350.9933 | 0.4057 | 0.48837 | 0.43813 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFS | OFFICE - SMALL | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.59035 | 0 | 0.68317 | Cap-Tons/1000 sf | 919.9179 | 1086.1179 | 1001.4513 | 0.36496 | 0.45066 | 0.41629 | 0 | 0 | 0 | 919.9179 | 1086.1179 | 1001.4513 | 0.36496 | 0.45066 | 0.41629 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 1.0264 | 0 | 1.1878 | Cap-Tons/1000 sf | 1288.3333 | 1593.6667 | 1438.3333 | 0.37099 | 0.45879 | 0.41436 | 0 | 0 | 0 | 1288.3333 | 1593.6667 | 1438.3333 | 0.37099 | 0.45879 | 0.41436 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.67965 | 0 | 0.78651 | Cap-Tons/1000 sf | 1308.7109 | 1545.3109 | 1422.0442 | 0.63766 | 0.73523 | 0.67716 | 0 | 0 | 0 | 1308.7109 | 1545.3109 | 1422.0442 | 0.63766 | 0.73523 | 0.67716 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.34638 | 0 | 0.37163 | Cap-Tons/1000 sf | 1162.3481 | 1382.2148 | 1280.4481 | 0.50631 | 0.59197 | 0.55404 | 0 | 0 | 0 | 1162.3481 | 1382.2148 | 1280.4481 | 0.50631 | 0.59197 | 0.55404 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.34652 | 0 | 0.40101 | Cap-Tons/1000 sf | 1185.6311 | 1433.8978 | 1316.9644 | 0.44 | 0.52863 | 0.48777 | 0 | 0 | 0 | 1185.6311 | 1433.8978 | 1316.9644 | 0.44 | 0.52863 | 0.48777 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTS | RETAIL - SMALL | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.39888 | 0 | 0.46159 | Cap-Tons/1000 sf | 1139.2783 | 1353.6783 | 1255.6117 | 0.33794 | 0.42461 | 0.37158 | 0 | 0 | 0 | 1139.2783 | 1353.6783 | 1255.6117 | 0.33794 | 0.42461 | 0.37158 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | SCN | STORAGE - CONDITIONED | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.22128 | 0 | 0.25607 | Cap-Tons/1000 sf | 746.65 | 912.5167 | 833.2833 | 0.22149 | 0.28629 | 0.24662 | 0 | 0 | 0 | 746.65 | 912.5167 | 833.2833 | 0.22149 | 0.28629 | 0.24662 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ASM | ASSEMBLY | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.83582 | 0 | 0.96724 | Cap-Tons/1000 sf | 954.8 | 1394.6667 | 1052.2667 | 0.59249 | 0.85607 | 0.63656 | 0 | 0 | 0 | 954.8 | 1394.6667 | 1052.2667 | 0.59249 | 0.85607 | 0.63656 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.4818 | 0 | 0.55756 | Cap-Tons/1000 sf | 617.7212 | 1007.3131 | 712.5212 | 0.33528 | 0.54558 | 0.38128 | 0 | 0 | 0 | 617.7212 | 1007.3131 | 712.5212 | 0.33528 | 0.54558 | 0.38128 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.51248 | 0 | 0.59306 | Cap-Tons/1000 sf | 554.8733 | 799.2333 | 615.1733 | 0.13722 | 0.19704 | 0.1484 | 0 | 0 | 0 | 554.8733 | 799.2333 | 615.1733 | 0.13722 | 0.19704 | 0.1484 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.6128 | 0 | 0.70915 | Cap-Tons/1000 sf | 761.8333 | 1180.1667 | 855.0667 | 0.32508 | 0.49978 | 0.35261 | 0 | 0 | 0 | 761.8333 | 1180.1667 | 855.0667 | 0.32508 | 0.49978 | 0.35261 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.49429 | 0 | 0.57201 | Cap-Tons/1000 sf | 674.2567 | 941.3167 | 737.5567 | 0.13534 | 0.18823 | 0.14485 | 0 | 0 | 0 | 674.2567 | 941.3167 | 737.5567 | 0.13534 | 0.18823 | 0.14485 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EUN | EDUCATION - UNIVERSITY | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.51877 | 0 | 0.55658 | Cap-Tons/1000 sf | 619.4331 | 1032.3885 | 721.7331 | 0.31111 | 0.51851 | 0.35797 | 0 | 0 | 0 | 619.4331 | 1032.3885 | 721.7331 | 0.31111 | 0.51851 | 0.35797 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | GRO | GROCERY | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.86635 | 0 | 0.92949 | Cap-Tons/1000 sf | 736.0033 | 1089.7833 | 852.0033 | 0.37058 | 0.54786 | 0.39908 | 0 | 0 | 0 | 736.0033 | 1089.7833 | 852.0033 | 0.37058 | 0.54786 | 0.39908 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.71085 | 0 | 0.82262 | Cap-Tons/1000 sf | 938.35 | 1563.9167 | 1094.9167 | 0.26329 | 0.43882 | 0.29903 | 0 | 0 | 0 | 938.35 | 1563.9167 | 1094.9167 | 0.26329 | 0.43882 | 0.29903 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HTL | LODGING - HOTEL | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.4087 | 0 | 0.43849 | Cap-Tons/1000 sf | 1157.54 | 1807.9 | 1310.8067 | 0.42987 | 0.66913 | 0.47337 | 0 | 0 | 0 | 1157.54 | 1807.9 | 1310.8067 | 0.42987 | 0.66913 | 0.47337 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | MTL | LODGING - MOTEL | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.4087 | 0 | 0.43849 | Cap-Tons/1000 sf | 1157.54 | 1807.9 | 1310.8067 | 0.42987 | 0.66913 | 0.47337 | 0 | 0 | 0 | 1157.54 | 1807.9 | 1310.8067 | 0.42987 | 0.66913 | 0.47337 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.76674 | 0 | 0.82262 | Cap-Tons/1000 sf | 909.3667 | 1436.1667 | 1053.9667 | 0.28425 | 0.44579 | 0.32235 | 0 | 0 | 0 | 909.3667 | 1436.1667 | 1053.9667 | 0.28425 | 0.44579 | 0.32235 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFL | OFFICE - LARGE | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.54446 | 0 | 0.58414 | Cap-Tons/1000 sf | 999.2266 | 1435.5599 | 1077.8599 | 0.59536 | 0.85536 | 0.63493 | 0 | 0 | 0 | 999.2266 | 1435.5599 | 1077.8599 | 0.59536 | 0.85536 | 0.63493 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFS | OFFICE - SMALL | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.59035 | 0 | 0.68317 | Cap-Tons/1000 sf | 693.8041 | 1086.1179 | 764.7041 | 0.48161 | 0.75388 | 0.52031 | 0 | 0 | 0 | 693.8041 | 1086.1179 | 764.7041 | 0.48161 | 0.75388 | 0.52031 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 1.0264 | 0 | 1.1878 | Cap-Tons/1000 sf | 1071.6667 | 1593.6667 | 1204.6667 | 0.46596 | 0.6865 | 0.5114 | 0 | 0 | 0 | 1071.6667 | 1593.6667 | 1204.6667 | 0.46596 | 0.6865 | 0.5114 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.67965 | 0 | 0.78651 | Cap-Tons/1000 sf | 1080.9776 | 1545.3109 | 1183.8442 | 0.69419 | 0.98953 | 0.74093 | 0 | 0 | 0 | 1080.9776 | 1545.3109 | 1183.8442 | 0.69419 | 0.98953 | 0.74093 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.34638 | 0 | 0.37163 | Cap-Tons/1000 sf | 917.9955 | 1382.2148 | 1016.2955 | 0.5152 | 0.76846 | 0.5672 | 0 | 0 | 0 | 917.9955 | 1382.2148 | 1016.2955 | 0.5152 | 0.76846 | 0.5672 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.34652 | 0 | 0.40101 | Cap-Tons/1000 sf | 973.272 | 1433.8978 | 1080.772 | 0.56904 | 0.83037 | 0.62037 | 0 | 0 | 0 | 973.272 | 1433.8978 | 1080.772 | 0.56904 | 0.83037 | 0.62037 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTS | RETAIL - SMALL | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.39888 | 0 | 0.46159 | Cap-Tons/1000 sf | 905.2737 | 1353.6783 | 1002.207 | 0.56784 | 0.84311 | 0.62178 | 0 | 0 | 0 | 905.2737 | 1353.6783 | 1002.207 | 0.56784 | 0.84311 | 0.62178 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | SCN | STORAGE - CONDITIONED | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.22128 | 0 | 0.25607 | Cap-Tons/1000 sf | 639.91 | 912.5167 | 720.9767 | 0.44053 | 0.61625 | 0.48106 | 0 | 0 | 0 | 639.91 | 912.5167 | 720.9767 | 0.44053 | 0.61625 | 0.48106 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ASM | ASSEMBLY | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.83582 | 0 | 0.96724 | Cap-Tons/1000 sf | 1208.2667 | 1394.6667 | 1298.8667 | 0.34511 | 0.41378 | 0.37301 | 0 | 0 | 0 | 1208.2667 | 1394.6667 | 1298.8667 | 0.34511 | 0.41378 | 0.37301 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.4818 | 0 | 0.55756 | Cap-Tons/1000 sf | 825.0798 | 1007.3131 | 905.6131 | 0.2505 | 0.31536 | 0.2779 | 0 | 0 | 0 | 825.0798 | 1007.3131 | 905.6131 | 0.2505 | 0.31536 | 0.2779 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.51248 | 0 | 0.59306 | Cap-Tons/1000 sf | 684 | 799.2333 | 733.9 | 0 | 0 | 0 | 0 | 0 | 0 | 684 | 799.2333 | 733.9 | 0 | 0 | 0 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.6128 | 0 | 0.70915 | Cap-Tons/1000 sf | 1021.9667 | 1180.1667 | 1089.0333 | 0.14446 | 0.17446 | 0.15539 | 0 | 0 | 0 | 1021.9667 | 1180.1667 | 1089.0333 | 0.14446 | 0.17446 | 0.15539 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.49429 | 0 | 0.57201 | Cap-Tons/1000 sf | 817.95 | 941.3167 | 870.95 | 0 | 0 | 0 | 0 | 0 | 0 | 817.95 | 941.3167 | 870.95 | 0 | 0 | 0 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EUN | EDUCATION - UNIVERSITY | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.51877 | 0 | 0.55658 | Cap-Tons/1000 sf | 832.3885 | 1032.3885 | 920.3219 | 0.23405 | 0.29998 | 0.26525 | 0 | 0 | 0 | 832.3885 | 1032.3885 | 920.3219 | 0.23405 | 0.29998 | 0.26525 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | GRO | GROCERY | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.86635 | 0 | 0.92949 | Cap-Tons/1000 sf | 831.7833 | 1089.7833 | 940.1167 | 0.20269 | 0.26529 | 0.23259 | 0 | 0 | 0 | 831.7833 | 1089.7833 | 940.1167 | 0.20269 | 0.26529 | 0.23259 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.71085 | 0 | 0.82262 | Cap-Tons/1000 sf | 1225.5833 | 1563.9167 | 1366.7833 | 0.16358 | 0.21725 | 0.18595 | 0 | 0 | 0 | 1225.5833 | 1563.9167 | 1366.7833 | 0.16358 | 0.21725 | 0.18595 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HTL | LODGING - HOTEL | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.4087 | 0 | 0.43849 | Cap-Tons/1000 sf | 1497.5667 | 1807.9 | 1634.7333 | 0.28938 | 0.35805 | 0.31828 | 0 | 0 | 0 | 1497.5667 | 1807.9 | 1634.7333 | 0.28938 | 0.35805 | 0.31828 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | MTL | LODGING - MOTEL | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.4087 | 0 | 0.43849 | Cap-Tons/1000 sf | 1497.5667 | 1807.9 | 1634.7333 | 0.28938 | 0.35805 | 0.31828 | 0 | 0 | 0 | 1497.5667 | 1807.9 | 1634.7333 | 0.28938 | 0.35805 | 0.31828 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.76674 | 0 | 0.82262 | Cap-Tons/1000 sf | 1133.5 | 1436.1667 | 1264 | 0.15561 | 0.20508 | 0.18014 | 0 | 0 | 0 | 1133.5 | 1436.1667 | 1264 | 0.15561 | 0.20508 | 0.18014 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFL | OFFICE - LARGE | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.54446 | 0 | 0.58414 | Cap-Tons/1000 sf | 1279.5599 | 1435.5599 | 1347.5933 | 0.6962 | 0.77944 | 0.73847 | 0 | 0 | 0 | 1279.5599 | 1435.5599 | 1347.5933 | 0.6962 | 0.77944 | 0.73847 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFS | OFFICE - SMALL | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.59035 | 0 | 0.68317 | Cap-Tons/1000 sf | 941.9179 | 1086.1179 | 1004.9846 | 0.41396 | 0.48829 | 0.45473 | 0 | 0 | 0 | 941.9179 | 1086.1179 | 1004.9846 | 0.41396 | 0.48829 | 0.45473 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 1.0264 | 0 | 1.1878 | Cap-Tons/1000 sf | 1319 | 1593.6667 | 1443.6667 | 0.28746 | 0.35106 | 0.31489 | 0 | 0 | 0 | 1319 | 1593.6667 | 1443.6667 | 0.28746 | 0.35106 | 0.31489 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.67965 | 0 | 0.78651 | Cap-Tons/1000 sf | 1346.1109 | 1545.3109 | 1437.5109 | 0.36269 | 0.43269 | 0.38705 | 0 | 0 | 0 | 1346.1109 | 1545.3109 | 1437.5109 | 0.36269 | 0.43269 | 0.38705 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.34638 | 0 | 0.37163 | Cap-Tons/1000 sf | 1191.7815 | 1382.2148 | 1286.4481 | 0.31835 | 0.38329 | 0.35602 | 0 | 0 | 0 | 1191.7815 | 1382.2148 | 1286.4481 | 0.31835 | 0.38329 | 0.35602 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.34652 | 0 | 0.40101 | Cap-Tons/1000 sf | 1219.6978 | 1433.8978 | 1320.5978 | 0.33163 | 0.39896 | 0.36456 | 0 | 0 | 0 | 1219.6978 | 1433.8978 | 1320.5978 | 0.33163 | 0.39896 | 0.36456 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTS | RETAIL - SMALL | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.39888 | 0 | 0.46159 | Cap-Tons/1000 sf | 1165.545 | 1353.6783 | 1251.9117 | 0.37511 | 0.44711 | 0.40734 | 0 | 0 | 0 | 1165.545 | 1353.6783 | 1251.9117 | 0.37511 | 0.44711 | 0.40734 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | PGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | SCN | STORAGE - CONDITIONED | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.22128 | 0 | 0.25607 | Cap-Tons/1000 sf | 750.0167 | 912.5167 | 820.8833 | 0.22309 | 0.27549 | 0.24839 | 0 | 0 | 0 | 750.0167 | 912.5167 | 820.8833 | 0.22309 | 0.27549 | 0.24839 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ASM | ASSEMBLY | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.93897 | 0 | 1.0666 | Cap-Tons/1000 sf | 1000.3333 | 1394.6667 | 1095.2 | 0.59696 | 0.83129 | 0.63386 | 0 | 0 | 0 | 1000.3333 | 1394.6667 | 1095.2 | 0.59696 | 0.83129 | 0.63386 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.54701 | 0 | 0.62134 | Cap-Tons/1000 sf | 647.7212 | 1007.3131 | 728.1879 | 0.37957 | 0.58803 | 0.417 | 0 | 0 | 0 | 647.7212 | 1007.3131 | 728.1879 | 0.37957 | 0.58803 | 0.417 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.621 | 0 | 0.70538 | Cap-Tons/1000 sf | 551.54 | 799.2333 | 604.7067 | 0.46773 | 0.67337 | 0.50287 | 0 | 0 | 0 | 551.54 | 799.2333 | 604.7067 | 0.46773 | 0.67337 | 0.50287 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.79463 | 0 | 0.84519 | Cap-Tons/1000 sf | 793.5 | 1180.1667 | 873.8667 | 0.44802 | 0.66036 | 0.48169 | 0 | 0 | 0 | 793.5 | 1180.1667 | 873.8667 | 0.44802 | 0.66036 | 0.48169 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.61214 | 0 | 0.69532 | Cap-Tons/1000 sf | 682.3167 | 941.3167 | 736.9167 | 0.60048 | 0.81848 | 0.63644 | 0 | 0 | 0 | 682.3167 | 941.3167 | 736.9167 | 0.60048 | 0.81848 | 0.63644 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EUN | EDUCATION - UNIVERSITY | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.58484 | 0 | 0.62204 | Cap-Tons/1000 sf | 619.4331 | 1032.3885 | 714.9998 | 0.31857 | 0.53095 | 0.35907 | 0 | 0 | 0 | 619.4331 | 1032.3885 | 714.9998 | 0.31857 | 0.53095 | 0.35907 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | GRO | GROCERY | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 1.0397 | 0 | 1.1059 | Cap-Tons/1000 sf | 761.3367 | 1089.7833 | 874.27 | 0.28184 | 0.40501 | 0.30421 | 0 | 0 | 0 | 761.3367 | 1089.7833 | 874.27 | 0.28184 | 0.40501 | 0.30421 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.77621 | 0 | 0.88169 | Cap-Tons/1000 sf | 938.35 | 1563.9167 | 1094.05 | 0.22051 | 0.36751 | 0.25117 | 0 | 0 | 0 | 938.35 | 1563.9167 | 1094.05 | 0.22051 | 0.36751 | 0.25117 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HTL | LODGING - HOTEL | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.46549 | 0 | 0.49511 | Cap-Tons/1000 sf | 1114.8733 | 1807.9 | 1268.1733 | 0.34767 | 0.56344 | 0.38374 | 0 | 0 | 0 | 1114.8733 | 1807.9 | 1268.1733 | 0.34767 | 0.56344 | 0.38374 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | MTL | LODGING - MOTEL | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.46549 | 0 | 0.49511 | Cap-Tons/1000 sf | 1114.8733 | 1807.9 | 1268.1733 | 0.34767 | 0.56344 | 0.38374 | 0 | 0 | 0 | 1114.8733 | 1807.9 | 1268.1733 | 0.34767 | 0.56344 | 0.38374 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.82895 | 0 | 0.88169 | Cap-Tons/1000 sf | 924.7 | 1436.1667 | 1062.5667 | 0.25412 | 0.39128 | 0.28345 | 0 | 0 | 0 | 924.7 | 1436.1667 | 1062.5667 | 0.25412 | 0.39128 | 0.28345 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFL | OFFICE - LARGE | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.61708 | 0 | 0.65634 | Cap-Tons/1000 sf | 1005.2266 | 1435.5599 | 1080.0266 | 0.57757 | 0.82057 | 0.61234 | 0 | 0 | 0 | 1005.2266 | 1435.5599 | 1080.0266 | 0.57757 | 0.82057 | 0.61234 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFS | OFFICE - SMALL | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.65556 | 0 | 0.74464 | Cap-Tons/1000 sf | 712.1179 | 1086.1179 | 779.2846 | 0.44338 | 0.67671 | 0.47608 | 0 | 0 | 0 | 712.1179 | 1086.1179 | 779.2846 | 0.44338 | 0.67671 | 0.47608 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 1.143 | 0 | 1.2984 | Cap-Tons/1000 sf | 1099.6667 | 1593.6667 | 1224.7667 | 0.42521 | 0.60956 | 0.46118 | 0 | 0 | 0 | 1099.6667 | 1593.6667 | 1224.7667 | 0.42521 | 0.60956 | 0.46118 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.77022 | 0 | 0.87488 | Cap-Tons/1000 sf | 1160.3109 | 1545.3109 | 1252.6442 | 0.6013 | 0.79797 | 0.6361 | 0 | 0 | 0 | 1160.3109 | 1545.3109 | 1252.6442 | 0.6013 | 0.79797 | 0.6361 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.37551 | 0 | 0.3994 | Cap-Tons/1000 sf | 923.9955 | 1382.2148 | 1019.5289 | 0.44297 | 0.65852 | 0.4798 | 0 | 0 | 0 | 923.9955 | 1382.2148 | 1019.5289 | 0.44297 | 0.65852 | 0.4798 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.40936 | 0 | 0.46499 | Cap-Tons/1000 sf | 974.6053 | 1433.8978 | 1082.772 | 0.4759 | 0.69675 | 0.5156 | 0 | 0 | 0 | 974.6053 | 1433.8978 | 1082.772 | 0.4759 | 0.69675 | 0.5156 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTS | RETAIL - SMALL | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.45321 | 0 | 0.51479 | Cap-Tons/1000 sf | 916.607 | 1353.6783 | 1008.5737 | 0.47412 | 0.696 | 0.51228 | 0 | 0 | 0 | 916.607 | 1353.6783 | 1008.5737 | 0.47412 | 0.696 | 0.51228 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | SCN | STORAGE - CONDITIONED | Existing | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.24791 | 0 | 0.2816 | Cap-Tons/1000 sf | 689.2433 | 912.5167 | 756.1767 | 0.27703 | 0.36121 | 0.29783 | 0 | 0 | 0 | 689.2433 | 912.5167 | 756.1767 | 0.27703 | 0.36121 | 0.29783 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ASM | ASSEMBLY | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.93897 | 0 | 1.0666 | Cap-Tons/1000 sf | 1220.6333 | 1394.6667 | 1308.2 | 0.31585 | 0.37572 | 0.33952 | 0 | 0 | 0 | 1220.6333 | 1394.6667 | 1308.2 | 0.31585 | 0.37572 | 0.33952 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.54701 | 0 | 0.62134 | Cap-Tons/1000 sf | 841.3465 | 1007.3131 | 914.0798 | 0.25572 | 0.31432 | 0.27889 | 0 | 0 | 0 | 841.3465 | 1007.3131 | 914.0798 | 0.25572 | 0.31432 | 0.27889 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.621 | 0 | 0.70538 | Cap-Tons/1000 sf | 691.9 | 799.2333 | 740.9 | 0.30373 | 0.35733 | 0.32557 | 0 | 0 | 0 | 691.9 | 799.2333 | 740.9 | 0.30373 | 0.35733 | 0.32557 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.79463 | 0 | 0.84519 | Cap-Tons/1000 sf | 1062.0333 | 1180.1667 | 1112 | 0.35511 | 0.40925 | 0.37931 | 0 | 0 | 0 | 1062.0333 | 1180.1667 | 1112 | 0.35511 | 0.40925 | 0.37931 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.61214 | 0 | 0.69532 | Cap-Tons/1000 sf | 832.3833 | 941.3167 | 880.85 | 0.371 | 0.42726 | 0.39246 | 0 | 0 | 0 | 832.3833 | 941.3167 | 880.85 | 0.371 | 0.42726 | 0.39246 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EUN | EDUCATION - UNIVERSITY | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.58484 | 0 | 0.62204 | Cap-Tons/1000 sf | 832.6552 | 1032.3885 | 920.6219 | 0.2344 | 0.30173 | 0.26086 | 0 | 0 | 0 | 832.6552 | 1032.3885 | 920.6219 | 0.2344 | 0.30173 | 0.26086 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | GRO | GROCERY | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 1.0397 | 0 | 1.1059 | Cap-Tons/1000 sf | 839.1167 | 1089.7833 | 949.5167 | 0.16531 | 0.21286 | 0.18851 | 0 | 0 | 0 | 839.1167 | 1089.7833 | 949.5167 | 0.16531 | 0.21286 | 0.18851 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.77621 | 0 | 0.88169 | Cap-Tons/1000 sf | 1215.25 | 1563.9167 | 1358.1833 | 0.1456 | 0.19573 | 0.1649 | 0 | 0 | 0 | 1215.25 | 1563.9167 | 1358.1833 | 0.1456 | 0.19573 | 0.1649 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HTL | LODGING - HOTEL | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.46549 | 0 | 0.49511 | Cap-Tons/1000 sf | 1494.2333 | 1807.9 | 1624.6333 | 0.25169 | 0.31216 | 0.27483 | 0 | 0 | 0 | 1494.2333 | 1807.9 | 1624.6333 | 0.25169 | 0.31216 | 0.27483 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | MTL | LODGING - MOTEL | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.46549 | 0 | 0.49511 | Cap-Tons/1000 sf | 1494.2333 | 1807.9 | 1624.6333 | 0.25169 | 0.31216 | 0.27483 | 0 | 0 | 0 | 1494.2333 | 1807.9 | 1624.6333 | 0.25169 | 0.31216 | 0.27483 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.82895 | 0 | 0.88169 | Cap-Tons/1000 sf | 1140.5 | 1436.1667 | 1261.2333 | 0.1435 | 0.1877 | 0.16123 | 0 | 0 | 0 | 1140.5 | 1436.1667 | 1261.2333 | 0.1435 | 0.1877 | 0.16123 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFL | OFFICE - LARGE | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.61708 | 0 | 0.65634 | Cap-Tons/1000 sf | 1272.9599 | 1435.5599 | 1342.2933 | 0.37115 | 0.43812 | 0.40805 | 0 | 0 | 0 | 1272.9599 | 1435.5599 | 1342.2933 | 0.37115 | 0.43812 | 0.40805 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFS | OFFICE - SMALL | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.65556 | 0 | 0.74464 | Cap-Tons/1000 sf | 939.4513 | 1086.1179 | 1000.6179 | 0.3641 | 0.43053 | 0.39706 | 0 | 0 | 0 | 939.4513 | 1086.1179 | 1000.6179 | 0.3641 | 0.43053 | 0.39706 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 1.143 | 0 | 1.2984 | Cap-Tons/1000 sf | 1325 | 1593.6667 | 1439.5 | 0.26622 | 0.3224 | 0.29892 | 0 | 0 | 0 | 1325 | 1593.6667 | 1439.5 | 0.26622 | 0.3224 | 0.29892 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.77022 | 0 | 0.87488 | Cap-Tons/1000 sf | 1351.6442 | 1545.3109 | 1445.0442 | 0.37075 | 0.4355 | 0.40799 | 0 | 0 | 0 | 1351.6442 | 1545.3109 | 1445.0442 | 0.37075 | 0.4355 | 0.40799 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.37551 | 0 | 0.3994 | Cap-Tons/1000 sf | 1191.0481 | 1382.2148 | 1276.9481 | 0.29103 | 0.3487 | 0.31403 | 0 | 0 | 0 | 1191.0481 | 1382.2148 | 1276.9481 | 0.29103 | 0.3487 | 0.31403 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.40936 | 0 | 0.46499 | Cap-Tons/1000 sf | 1229.0644 | 1433.8978 | 1326.1644 | 0.30897 | 0.37171 | 0.33357 | 0 | 0 | 0 | 1229.0644 | 1433.8978 | 1326.1644 | 0.30897 | 0.37171 | 0.33357 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTS | RETAIL - SMALL | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.45321 | 0 | 0.51479 | Cap-Tons/1000 sf | 1174.6117 | 1353.6783 | 1251.1783 | 0.33057 | 0.3891 | 0.3527 | 0 | 0 | 0 | 1174.6117 | 1353.6783 | 1251.1783 | 0.33057 | 0.3891 | 0.3527 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | SCN | STORAGE - CONDITIONED | New | CZ05 | Santa Maria Area (CZ05) |  |  |  | 1000 sf | 0.24791 | 0 | 0.2816 | Cap-Tons/1000 sf | 764.9167 | 912.5167 | 829.7833 | 0.21137 | 0.25277 | 0.22996 | 0 | 0 | 0 | 764.9167 | 912.5167 | 829.7833 | 0.21137 | 0.25277 | 0.22996 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ASM | ASSEMBLY | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.93897 | 0 | 1.0666 | Cap-Tons/1000 sf | 900.8 | 1394.6667 | 1009.4333 | 0.46134 | 0.71337 | 0.49924 | 0 | 0 | 0 | 900.8 | 1394.6667 | 1009.4333 | 0.46134 | 0.71337 | 0.49924 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.54701 | 0 | 0.62134 | Cap-Tons/1000 sf | 604.3879 | 1007.3131 | 697.0545 | 0.34629 | 0.57715 | 0.38705 | 0 | 0 | 0 | 604.3879 | 1007.3131 | 697.0545 | 0.34629 | 0.57715 | 0.38705 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.621 | 0 | 0.70538 | Cap-Tons/1000 sf | 504.8733 | 799.2333 | 566.1067 | 0.46432 | 0.73557 | 0.50472 | 0 | 0 | 0 | 504.8733 | 799.2333 | 566.1067 | 0.46432 | 0.73557 | 0.50472 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.79463 | 0 | 0.84519 | Cap-Tons/1000 sf | 785.5 | 1180.1667 | 862.1333 | 0.54658 | 0.82058 | 0.58704 | 0 | 0 | 0 | 785.5 | 1180.1667 | 862.1333 | 0.54658 | 0.82058 | 0.58704 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.61214 | 0 | 0.69532 | Cap-Tons/1000 sf | 644.2567 | 941.3167 | 705.19 | 0.58655 | 0.8552 | 0.62559 | 0 | 0 | 0 | 644.2567 | 941.3167 | 705.19 | 0.58655 | 0.8552 | 0.62559 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EUN | EDUCATION - UNIVERSITY | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.58484 | 0 | 0.62204 | Cap-Tons/1000 sf | 619.4331 | 1032.3885 | 728.4665 | 0.30996 | 0.5166 | 0.35293 | 0 | 0 | 0 | 619.4331 | 1032.3885 | 728.4665 | 0.30996 | 0.5166 | 0.35293 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | GRO | GROCERY | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 1.0397 | 0 | 1.1059 | Cap-Tons/1000 sf | 725.3367 | 1089.7833 | 842.1033 | 0.33561 | 0.50218 | 0.36654 | 0 | 0 | 0 | 725.3367 | 1089.7833 | 842.1033 | 0.33561 | 0.50218 | 0.36654 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.77621 | 0 | 0.88169 | Cap-Tons/1000 sf | 938.35 | 1563.9167 | 1110.7833 | 0.21977 | 0.36628 | 0.25377 | 0 | 0 | 0 | 938.35 | 1563.9167 | 1110.7833 | 0.21977 | 0.36628 | 0.25377 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HTL | LODGING - HOTEL | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.46549 | 0 | 0.49511 | Cap-Tons/1000 sf | 1084.74 | 1807.9 | 1263.0733 | 0.32875 | 0.54791 | 0.37168 | 0 | 0 | 0 | 1084.74 | 1807.9 | 1263.0733 | 0.32875 | 0.54791 | 0.37168 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | MTL | LODGING - MOTEL | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.46549 | 0 | 0.49511 | Cap-Tons/1000 sf | 1084.74 | 1807.9 | 1263.0733 | 0.32875 | 0.54791 | 0.37168 | 0 | 0 | 0 | 1084.74 | 1807.9 | 1263.0733 | 0.32875 | 0.54791 | 0.37168 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.82895 | 0 | 0.88169 | Cap-Tons/1000 sf | 861.7 | 1436.1667 | 1013.6333 | 0.23948 | 0.39914 | 0.27135 | 0 | 0 | 0 | 861.7 | 1436.1667 | 1013.6333 | 0.23948 | 0.39914 | 0.27135 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFL | OFFICE - LARGE | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.61708 | 0 | 0.65634 | Cap-Tons/1000 sf | 932.5599 | 1435.5599 | 1017.3599 | 0.52155 | 0.79955 | 0.56005 | 0 | 0 | 0 | 932.5599 | 1435.5599 | 1017.3599 | 0.52155 | 0.79955 | 0.56005 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFS | OFFICE - SMALL | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.65556 | 0 | 0.74464 | Cap-Tons/1000 sf | 651.6708 | 1086.1179 | 728.8041 | 0.39818 | 0.66364 | 0.43588 | 0 | 0 | 0 | 651.6708 | 1086.1179 | 728.8041 | 0.39818 | 0.66364 | 0.43588 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 1.143 | 0 | 1.2984 | Cap-Tons/1000 sf | 1029.6667 | 1593.6667 | 1168.3667 | 0.38938 | 0.6009 | 0.42695 | 0 | 0 | 0 | 1029.6667 | 1593.6667 | 1168.3667 | 0.38938 | 0.6009 | 0.42695 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.77022 | 0 | 0.87488 | Cap-Tons/1000 sf | 1016.9776 | 1545.3109 | 1129.1776 | 0.56709 | 0.86176 | 0.60846 | 0 | 0 | 0 | 1016.9776 | 1545.3109 | 1129.1776 | 0.56709 | 0.86176 | 0.60846 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.37551 | 0 | 0.3994 | Cap-Tons/1000 sf | 829.3289 | 1382.2148 | 947.5955 | 0.39827 | 0.66378 | 0.44057 | 0 | 0 | 0 | 829.3289 | 1382.2148 | 947.5955 | 0.39827 | 0.66378 | 0.44057 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.40936 | 0 | 0.46499 | Cap-Tons/1000 sf | 879.272 | 1433.8978 | 1003.972 | 0.40687 | 0.66368 | 0.44827 | 0 | 0 | 0 | 879.272 | 1433.8978 | 1003.972 | 0.40687 | 0.66368 | 0.44827 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTS | RETAIL - SMALL | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.45321 | 0 | 0.51479 | Cap-Tons/1000 sf | 821.2737 | 1353.6783 | 932.107 | 0.41724 | 0.6877 | 0.46181 | 0 | 0 | 0 | 821.2737 | 1353.6783 | 932.107 | 0.41724 | 0.6877 | 0.46181 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | SCN | STORAGE - CONDITIONED | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.24791 | 0 | 0.2816 | Cap-Tons/1000 sf | 640.5767 | 912.5167 | 716.6433 | 0.44902 | 0.62804 | 0.48332 | 0 | 0 | 0 | 640.5767 | 912.5167 | 716.6433 | 0.44902 | 0.62804 | 0.48332 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ASM | ASSEMBLY | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.93897 | 0 | 1.0666 | Cap-Tons/1000 sf | 1182 | 1394.6667 | 1286.5667 | 0.43248 | 0.50888 | 0.46944 | 0 | 0 | 0 | 1182 | 1394.6667 | 1286.5667 | 0.43248 | 0.50888 | 0.46944 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.54701 | 0 | 0.62134 | Cap-Tons/1000 sf | 828.7465 | 1007.3131 | 916.0131 | 0.34989 | 0.42519 | 0.38902 | 0 | 0 | 0 | 828.7465 | 1007.3131 | 916.0131 | 0.34989 | 0.42519 | 0.38902 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.621 | 0 | 0.70538 | Cap-Tons/1000 sf | 684.8 | 799.2333 | 740.5333 | 0.45036 | 0.52499 | 0.48713 | 0 | 0 | 0 | 684.8 | 799.2333 | 740.5333 | 0.45036 | 0.52499 | 0.48713 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.79463 | 0 | 0.84519 | Cap-Tons/1000 sf | 1059.8333 | 1180.1667 | 1113.3667 | 0.61283 | 0.68536 | 0.64903 | 0 | 0 | 0 | 1059.8333 | 1180.1667 | 1113.3667 | 0.61283 | 0.68536 | 0.64903 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.61214 | 0 | 0.69532 | Cap-Tons/1000 sf | 822.7833 | 941.3167 | 881.25 | 0.58053 | 0.66193 | 0.61983 | 0 | 0 | 0 | 822.7833 | 941.3167 | 881.25 | 0.58053 | 0.66193 | 0.61983 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EUN | EDUCATION - UNIVERSITY | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.58484 | 0 | 0.62204 | Cap-Tons/1000 sf | 814.0552 | 1032.3885 | 914.7219 | 0.32139 | 0.40502 | 0.36372 | 0 | 0 | 0 | 814.0552 | 1032.3885 | 914.7219 | 0.32139 | 0.40502 | 0.36372 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | GRO | GROCERY | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 1.0397 | 0 | 1.1059 | Cap-Tons/1000 sf | 841.7833 | 1089.7833 | 950.75 | 0.1761 | 0.2329 | 0.1991 | 0 | 0 | 0 | 841.7833 | 1089.7833 | 950.75 | 0.1761 | 0.2329 | 0.1991 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.77621 | 0 | 0.88169 | Cap-Tons/1000 sf | 1193.5833 | 1563.9167 | 1358.1833 | 0.14487 | 0.20027 | 0.1673 | 0 | 0 | 0 | 1193.5833 | 1563.9167 | 1358.1833 | 0.14487 | 0.20027 | 0.1673 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HTL | LODGING - HOTEL | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.46549 | 0 | 0.49511 | Cap-Tons/1000 sf | 1453.5667 | 1807.9 | 1608.5667 | 0.26535 | 0.33592 | 0.30349 | 0 | 0 | 0 | 1453.5667 | 1807.9 | 1608.5667 | 0.26535 | 0.33592 | 0.30349 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | MTL | LODGING - MOTEL | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.46549 | 0 | 0.49511 | Cap-Tons/1000 sf | 1453.5667 | 1807.9 | 1608.5667 | 0.26535 | 0.33592 | 0.30349 | 0 | 0 | 0 | 1453.5667 | 1807.9 | 1608.5667 | 0.26535 | 0.33592 | 0.30349 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.82895 | 0 | 0.88169 | Cap-Tons/1000 sf | 1124.5 | 1436.1667 | 1254.7667 | 0.14417 | 0.19424 | 0.16274 | 0 | 0 | 0 | 1124.5 | 1436.1667 | 1254.7667 | 0.14417 | 0.19424 | 0.16274 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFL | OFFICE - LARGE | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.61708 | 0 | 0.65634 | Cap-Tons/1000 sf | 1259.1599 | 1435.5599 | 1339.9933 | 0.54996 | 0.62806 | 0.59166 | 0 | 0 | 0 | 1259.1599 | 1435.5599 | 1339.9933 | 0.54996 | 0.62806 | 0.59166 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFS | OFFICE - SMALL | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.65556 | 0 | 0.74464 | Cap-Tons/1000 sf | 920.1846 | 1086.1179 | 994.7513 | 0.46345 | 0.54448 | 0.50542 | 0 | 0 | 0 | 920.1846 | 1086.1179 | 994.7513 | 0.46345 | 0.54448 | 0.50542 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 1.143 | 0 | 1.2984 | Cap-Tons/1000 sf | 1306.3333 | 1593.6667 | 1438.6667 | 0.3382 | 0.41337 | 0.3749 | 0 | 0 | 0 | 1306.3333 | 1593.6667 | 1438.6667 | 0.3382 | 0.41337 | 0.3749 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.77022 | 0 | 0.87488 | Cap-Tons/1000 sf | 1330.5442 | 1545.3109 | 1442.2109 | 0.67633 | 0.76803 | 0.71783 | 0 | 0 | 0 | 1330.5442 | 1545.3109 | 1442.2109 | 0.67633 | 0.76803 | 0.71783 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.37551 | 0 | 0.3994 | Cap-Tons/1000 sf | 1158.6148 | 1382.2148 | 1273.4148 | 0.49057 | 0.57463 | 0.5325 | 0 | 0 | 0 | 1158.6148 | 1382.2148 | 1273.4148 | 0.49057 | 0.57463 | 0.5325 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.40936 | 0 | 0.46499 | Cap-Tons/1000 sf | 1191.8978 | 1433.8978 | 1313.1311 | 0.40913 | 0.49033 | 0.4499 | 0 | 0 | 0 | 1191.8978 | 1433.8978 | 1313.1311 | 0.40913 | 0.49033 | 0.4499 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTS | RETAIL - SMALL | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.45321 | 0 | 0.51479 | Cap-Tons/1000 sf | 1145.845 | 1353.6783 | 1245.4783 | 0.44632 | 0.52869 | 0.49012 | 0 | 0 | 0 | 1145.845 | 1353.6783 | 1245.4783 | 0.44632 | 0.52869 | 0.49012 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | SCN | STORAGE - CONDITIONED | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.24791 | 0 | 0.2816 | Cap-Tons/1000 sf | 753.7167 | 912.5167 | 827.8833 | 0.2335 | 0.28822 | 0.26533 | 0 | 0 | 0 | 753.7167 | 912.5167 | 827.8833 | 0.2335 | 0.28822 | 0.26533 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ASM | ASSEMBLY | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.93897 | 0 | 1.0666 | Cap-Tons/1000 sf | 836.8 | 1394.6667 | 954.8667 | 0.44674 | 0.74457 | 0.49264 | 0 | 0 | 0 | 836.8 | 1394.6667 | 954.8667 | 0.44674 | 0.74457 | 0.49264 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.54701 | 0 | 0.62134 | Cap-Tons/1000 sf | 604.3879 | 1007.3131 | 705.2212 | 0.35726 | 0.59543 | 0.40449 | 0 | 0 | 0 | 604.3879 | 1007.3131 | 705.2212 | 0.35726 | 0.59543 | 0.40449 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.621 | 0 | 0.70538 | Cap-Tons/1000 sf | 504.2067 | 799.2333 | 566.3733 | 0.44128 | 0.69856 | 0.48261 | 0 | 0 | 0 | 504.2067 | 799.2333 | 566.3733 | 0.44128 | 0.69856 | 0.48261 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.79463 | 0 | 0.84519 | Cap-Tons/1000 sf | 759.1667 | 1180.1667 | 839.6667 | 0.51638 | 0.80005 | 0.55988 | 0 | 0 | 0 | 759.1667 | 1180.1667 | 839.6667 | 0.51638 | 0.80005 | 0.55988 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.61214 | 0 | 0.69532 | Cap-Tons/1000 sf | 621.59 | 941.3167 | 686.7233 | 0.55768 | 0.84239 | 0.60068 | 0 | 0 | 0 | 621.59 | 941.3167 | 686.7233 | 0.55768 | 0.84239 | 0.60068 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EUN | EDUCATION - UNIVERSITY | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.58484 | 0 | 0.62204 | Cap-Tons/1000 sf | 619.4331 | 1032.3885 | 731.7665 | 0.3173 | 0.52883 | 0.36427 | 0 | 0 | 0 | 619.4331 | 1032.3885 | 731.7665 | 0.3173 | 0.52883 | 0.36427 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | GRO | GROCERY | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 1.0397 | 0 | 1.1059 | Cap-Tons/1000 sf | 695.3367 | 1089.7833 | 816.2367 | 0.33839 | 0.52894 | 0.37283 | 0 | 0 | 0 | 695.3367 | 1089.7833 | 816.2367 | 0.33839 | 0.52894 | 0.37283 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.77621 | 0 | 0.88169 | Cap-Tons/1000 sf | 938.35 | 1563.9167 | 1117.0167 | 0.23901 | 0.39834 | 0.27937 | 0 | 0 | 0 | 938.35 | 1563.9167 | 1117.0167 | 0.23901 | 0.39834 | 0.27937 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HTL | LODGING - HOTEL | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.46549 | 0 | 0.49511 | Cap-Tons/1000 sf | 1084.74 | 1807.9 | 1264.0733 | 0.33704 | 0.56173 | 0.38347 | 0 | 0 | 0 | 1084.74 | 1807.9 | 1264.0733 | 0.33704 | 0.56173 | 0.38347 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | MTL | LODGING - MOTEL | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.46549 | 0 | 0.49511 | Cap-Tons/1000 sf | 1084.74 | 1807.9 | 1264.0733 | 0.33704 | 0.56173 | 0.38347 | 0 | 0 | 0 | 1084.74 | 1807.9 | 1264.0733 | 0.33704 | 0.56173 | 0.38347 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.82895 | 0 | 0.88169 | Cap-Tons/1000 sf | 861.7 | 1436.1667 | 1020.3 | 0.26003 | 0.43338 | 0.29696 | 0 | 0 | 0 | 861.7 | 1436.1667 | 1020.3 | 0.26003 | 0.43338 | 0.29696 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFL | OFFICE - LARGE | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.61708 | 0 | 0.65634 | Cap-Tons/1000 sf | 909.8933 | 1435.5599 | 996.4599 | 0.52446 | 0.82613 | 0.56733 | 0 | 0 | 0 | 909.8933 | 1435.5599 | 996.4599 | 0.52446 | 0.82613 | 0.56733 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFS | OFFICE - SMALL | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.65556 | 0 | 0.74464 | Cap-Tons/1000 sf | 651.6708 | 1086.1179 | 731.4041 | 0.40926 | 0.68209 | 0.45202 | 0 | 0 | 0 | 651.6708 | 1086.1179 | 731.4041 | 0.40926 | 0.68209 | 0.45202 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 1.143 | 0 | 1.2984 | Cap-Tons/1000 sf | 967.6667 | 1593.6667 | 1116 | 0.39401 | 0.64868 | 0.43784 | 0 | 0 | 0 | 967.6667 | 1593.6667 | 1116 | 0.39401 | 0.64868 | 0.43784 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.77022 | 0 | 0.87488 | Cap-Tons/1000 sf | 941.2694 | 1545.3109 | 1060.1361 | 0.50822 | 0.83418 | 0.55492 | 0 | 0 | 0 | 941.2694 | 1545.3109 | 1060.1361 | 0.50822 | 0.83418 | 0.55492 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.37551 | 0 | 0.3994 | Cap-Tons/1000 sf | 829.3289 | 1382.2148 | 956.3289 | 0.3962 | 0.66033 | 0.4449 | 0 | 0 | 0 | 829.3289 | 1382.2148 | 956.3289 | 0.3962 | 0.66033 | 0.4449 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.40936 | 0 | 0.46499 | Cap-Tons/1000 sf | 860.3387 | 1433.8978 | 991.3387 | 0.39651 | 0.66084 | 0.44261 | 0 | 0 | 0 | 860.3387 | 1433.8978 | 991.3387 | 0.39651 | 0.66084 | 0.44261 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTS | RETAIL - SMALL | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.45321 | 0 | 0.51479 | Cap-Tons/1000 sf | 812.207 | 1353.6783 | 927.4403 | 0.40494 | 0.6749 | 0.45367 | 0 | 0 | 0 | 812.207 | 1353.6783 | 927.4403 | 0.40494 | 0.6749 | 0.45367 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | SCN | STORAGE - CONDITIONED | Existing | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.24791 | 0 | 0.2816 | Cap-Tons/1000 sf | 603.2433 | 912.5167 | 685.8433 | 0.41407 | 0.61927 | 0.45267 | 0 | 0 | 0 | 603.2433 | 912.5167 | 685.8433 | 0.41407 | 0.61927 | 0.45267 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ASM | ASSEMBLY | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.93897 | 0 | 1.0666 | Cap-Tons/1000 sf | 1164.8667 | 1394.6667 | 1277.8333 | 0.48217 | 0.57177 | 0.526 | 0 | 0 | 0 | 1164.8667 | 1394.6667 | 1277.8333 | 0.48217 | 0.57177 | 0.526 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.54701 | 0 | 0.62134 | Cap-Tons/1000 sf | 816.4798 | 1007.3131 | 910.8465 | 0.39054 | 0.47834 | 0.43614 | 0 | 0 | 0 | 816.4798 | 1007.3131 | 910.8465 | 0.39054 | 0.47834 | 0.43614 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.621 | 0 | 0.70538 | Cap-Tons/1000 sf | 682.4333 | 799.2333 | 737.2667 | 0.43851 | 0.51564 | 0.47761 | 0 | 0 | 0 | 682.4333 | 799.2333 | 737.2667 | 0.43851 | 0.51564 | 0.47761 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.79463 | 0 | 0.84519 | Cap-Tons/1000 sf | 1062.7667 | 1180.1667 | 1117.9667 | 0.41252 | 0.47832 | 0.43852 | 0 | 0 | 0 | 1062.7667 | 1180.1667 | 1117.9667 | 0.41252 | 0.47832 | 0.43852 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.61214 | 0 | 0.69532 | Cap-Tons/1000 sf | 817.5833 | 941.3167 | 877.55 | 0.55376 | 0.63743 | 0.59593 | 0 | 0 | 0 | 817.5833 | 941.3167 | 877.55 | 0.55376 | 0.63743 | 0.59593 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EUN | EDUCATION - UNIVERSITY | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.58484 | 0 | 0.62204 | Cap-Tons/1000 sf | 810.7219 | 1032.3885 | 916.6552 | 0.29988 | 0.38438 | 0.34595 | 0 | 0 | 0 | 810.7219 | 1032.3885 | 916.6552 | 0.29988 | 0.38438 | 0.34595 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | GRO | GROCERY | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 1.0397 | 0 | 1.1059 | Cap-Tons/1000 sf | 834.1167 | 1089.7833 | 954.05 | 0.18985 | 0.25507 | 0.22671 | 0 | 0 | 0 | 834.1167 | 1089.7833 | 954.05 | 0.18985 | 0.25507 | 0.22671 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.77621 | 0 | 0.88169 | Cap-Tons/1000 sf | 1190.5833 | 1563.9167 | 1358.9167 | 0.15277 | 0.21304 | 0.17804 | 0 | 0 | 0 | 1190.5833 | 1563.9167 | 1358.9167 | 0.15277 | 0.21304 | 0.17804 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HTL | LODGING - HOTEL | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.46549 | 0 | 0.49511 | Cap-Tons/1000 sf | 1446.5667 | 1807.9 | 1611.9 | 0.24008 | 0.31207 | 0.26864 | 0 | 0 | 0 | 1446.5667 | 1807.9 | 1611.9 | 0.24008 | 0.31207 | 0.26864 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | MTL | LODGING - MOTEL | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.46549 | 0 | 0.49511 | Cap-Tons/1000 sf | 1446.5667 | 1807.9 | 1611.9 | 0.24008 | 0.31207 | 0.26864 | 0 | 0 | 0 | 1446.5667 | 1807.9 | 1611.9 | 0.24008 | 0.31207 | 0.26864 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.82895 | 0 | 0.88169 | Cap-Tons/1000 sf | 1118.8333 | 1436.1667 | 1263.4333 | 0.154 | 0.21 | 0.17647 | 0 | 0 | 0 | 1118.8333 | 1436.1667 | 1263.4333 | 0.154 | 0.21 | 0.17647 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFL | OFFICE - LARGE | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.61708 | 0 | 0.65634 | Cap-Tons/1000 sf | 1255.4599 | 1435.5599 | 1338.0933 | 0.46259 | 0.5423 | 0.50879 | 0 | 0 | 0 | 1255.4599 | 1435.5599 | 1338.0933 | 0.46259 | 0.5423 | 0.50879 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFS | OFFICE - SMALL | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.65556 | 0 | 0.74464 | Cap-Tons/1000 sf | 920.1513 | 1086.1179 | 996.7513 | 0.38537 | 0.46444 | 0.43117 | 0 | 0 | 0 | 920.1513 | 1086.1179 | 996.7513 | 0.38537 | 0.46444 | 0.43117 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 1.143 | 0 | 1.2984 | Cap-Tons/1000 sf | 1288.3333 | 1593.6667 | 1433.3333 | 0.37309 | 0.46096 | 0.41559 | 0 | 0 | 0 | 1288.3333 | 1593.6667 | 1433.3333 | 0.37309 | 0.46096 | 0.41559 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.77022 | 0 | 0.87488 | Cap-Tons/1000 sf | 1307.3109 | 1545.3109 | 1425.7776 | 0.61198 | 0.71138 | 0.65902 | 0 | 0 | 0 | 1307.3109 | 1545.3109 | 1425.7776 | 0.61198 | 0.71138 | 0.65902 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.37551 | 0 | 0.3994 | Cap-Tons/1000 sf | 1139.2148 | 1382.2148 | 1261.6481 | 0.44958 | 0.53991 | 0.49678 | 0 | 0 | 0 | 1139.2148 | 1382.2148 | 1261.6481 | 0.44958 | 0.53991 | 0.49678 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.40936 | 0 | 0.46499 | Cap-Tons/1000 sf | 1179.5311 | 1433.8978 | 1304.1978 | 0.36484 | 0.44751 | 0.40957 | 0 | 0 | 0 | 1179.5311 | 1433.8978 | 1304.1978 | 0.36484 | 0.44751 | 0.40957 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTS | RETAIL - SMALL | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.45321 | 0 | 0.51479 | Cap-Tons/1000 sf | 1134.8117 | 1353.6783 | 1246.3117 | 0.42104 | 0.50564 | 0.46967 | 0 | 0 | 0 | 1134.8117 | 1353.6783 | 1246.3117 | 0.42104 | 0.50564 | 0.46967 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | SCN | STORAGE - CONDITIONED | New | CZ08 | El Toro Area (CZ08) |  |  |  | 1000 sf | 0.24791 | 0 | 0.2816 | Cap-Tons/1000 sf | 748.95 | 912.5167 | 825.8833 | 0.23526 | 0.29572 | 0.25912 | 0 | 0 | 0 | 748.95 | 912.5167 | 825.8833 | 0.23526 | 0.29572 | 0.25912 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ASM | ASSEMBLY | Existing | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 0.93897 | 0 | 1.0666 | Cap-Tons/1000 sf | 868.1333 | 1394.6667 | 978.5 | 0.55128 | 0.8852 | 0.59481 | 0 | 0 | 0 | 868.1333 | 1394.6667 | 978.5 | 0.55128 | 0.8852 | 0.59481 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | Existing | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 0.54701 | 0 | 0.62134 | Cap-Tons/1000 sf | 604.3879 | 1007.3131 | 699.3545 | 0.42018 | 0.70031 | 0.46785 | 0 | 0 | 0 | 604.3879 | 1007.3131 | 699.3545 | 0.42018 | 0.70031 | 0.46785 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | Existing | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 0.621 | 0 | 0.70538 | Cap-Tons/1000 sf | 498.8733 | 799.2333 | 562.7067 | 0.56613 | 0.90665 | 0.61339 | 0 | 0 | 0 | 498.8733 | 799.2333 | 562.7067 | 0.56613 | 0.90665 | 0.61339 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | Existing | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 0.79463 | 0 | 0.84519 | Cap-Tons/1000 sf | 738.5 | 1180.1667 | 822.9333 | 0.59058 | 0.93935 | 0.64102 | 0 | 0 | 0 | 738.5 | 1180.1667 | 822.9333 | 0.59058 | 0.93935 | 0.64102 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | Existing | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 0.61214 | 0 | 0.69532 | Cap-Tons/1000 sf | 623.59 | 941.3167 | 689.5233 | 0.69492 | 1.0467 | 0.74218 | 0 | 0 | 0 | 623.59 | 941.3167 | 689.5233 | 0.69492 | 1.0467 | 0.74218 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EUN | EDUCATION - UNIVERSITY | Existing | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 0.58484 | 0 | 0.62204 | Cap-Tons/1000 sf | 619.4331 | 1032.3885 | 727.2331 | 0.37888 | 0.63146 | 0.42738 | 0 | 0 | 0 | 619.4331 | 1032.3885 | 727.2331 | 0.37888 | 0.63146 | 0.42738 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | GRO | GROCERY | Existing | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 1.0397 | 0 | 1.1059 | Cap-Tons/1000 sf | 685.3367 | 1089.7833 | 807.7367 | 0.37635 | 0.59675 | 0.41555 | 0 | 0 | 0 | 685.3367 | 1089.7833 | 807.7367 | 0.37635 | 0.59675 | 0.41555 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | Existing | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 0.77621 | 0 | 0.88169 | Cap-Tons/1000 sf | 938.35 | 1563.9167 | 1114.35 | 0.28065 | 0.46774 | 0.32381 | 0 | 0 | 0 | 938.35 | 1563.9167 | 1114.35 | 0.28065 | 0.46774 | 0.32381 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HTL | LODGING - HOTEL | Existing | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 0.46549 | 0 | 0.49511 | Cap-Tons/1000 sf | 1084.74 | 1807.9 | 1261.0733 | 0.39952 | 0.66586 | 0.44975 | 0 | 0 | 0 | 1084.74 | 1807.9 | 1261.0733 | 0.39952 | 0.66586 | 0.44975 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | MTL | LODGING - MOTEL | Existing | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 0.46549 | 0 | 0.49511 | Cap-Tons/1000 sf | 1084.74 | 1807.9 | 1261.0733 | 0.39952 | 0.66586 | 0.44975 | 0 | 0 | 0 | 1084.74 | 1807.9 | 1261.0733 | 0.39952 | 0.66586 | 0.44975 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | Existing | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 0.82895 | 0 | 0.88169 | Cap-Tons/1000 sf | 861.7 | 1436.1667 | 1020.1 | 0.30703 | 0.51172 | 0.34707 | 0 | 0 | 0 | 861.7 | 1436.1667 | 1020.1 | 0.30703 | 0.51172 | 0.34707 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFL | OFFICE - LARGE | Existing | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 0.61708 | 0 | 0.65634 | Cap-Tons/1000 sf | 935.8933 | 1435.5599 | 1019.4933 | 0.62485 | 0.95851 | 0.67181 | 0 | 0 | 0 | 935.8933 | 1435.5599 | 1019.4933 | 0.62485 | 0.95851 | 0.67181 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFS | OFFICE - SMALL | Existing | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 0.65556 | 0 | 0.74464 | Cap-Tons/1000 sf | 651.6708 | 1086.1179 | 730.0708 | 0.47691 | 0.79485 | 0.52504 | 0 | 0 | 0 | 651.6708 | 1086.1179 | 730.0708 | 0.47691 | 0.79485 | 0.52504 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | Existing | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 1.143 | 0 | 1.2984 | Cap-Tons/1000 sf | 1001.6667 | 1593.6667 | 1145.3333 | 0.47474 | 0.75381 | 0.52011 | 0 | 0 | 0 | 1001.6667 | 1593.6667 | 1145.3333 | 0.47474 | 0.75381 | 0.52011 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | Existing | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 0.77022 | 0 | 0.87488 | Cap-Tons/1000 sf | 951.2694 | 1545.3109 | 1066.7361 | 0.63896 | 1.0382 | 0.68586 | 0 | 0 | 0 | 951.2694 | 1545.3109 | 1066.7361 | 0.63896 | 1.0382 | 0.68586 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | Existing | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 0.37551 | 0 | 0.3994 | Cap-Tons/1000 sf | 829.3289 | 1382.2148 | 947.6955 | 0.48988 | 0.81646 | 0.54011 | 0 | 0 | 0 | 829.3289 | 1382.2148 | 947.6955 | 0.48988 | 0.81646 | 0.54011 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | Existing | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 0.40936 | 0 | 0.46499 | Cap-Tons/1000 sf | 870.6053 | 1433.8978 | 995.8053 | 0.4932 | 0.81219 | 0.54153 | 0 | 0 | 0 | 870.6053 | 1433.8978 | 995.8053 | 0.4932 | 0.81219 | 0.54153 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTS | RETAIL - SMALL | Existing | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 0.45321 | 0 | 0.51479 | Cap-Tons/1000 sf | 818.607 | 1353.6783 | 929.2737 | 0.49413 | 0.81685 | 0.54656 | 0 | 0 | 0 | 818.607 | 1353.6783 | 929.2737 | 0.49413 | 0.81685 | 0.54656 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | SCN | STORAGE - CONDITIONED | Existing | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 0.24791 | 0 | 0.2816 | Cap-Tons/1000 sf | 595.2433 | 912.5167 | 679.31 | 0.4925 | 0.74857 | 0.5354 | 0 | 0 | 0 | 595.2433 | 912.5167 | 679.31 | 0.4925 | 0.74857 | 0.5354 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ASM | ASSEMBLY | New | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 0.93897 | 0 | 1.0666 | Cap-Tons/1000 sf | 1165 | 1394.6667 | 1258.3333 | 0.81053 | 0.9392 | 0.84586 | 0 | 0 | 0 | 1165 | 1394.6667 | 1258.3333 | 0.81053 | 0.9392 | 0.84586 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | New | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 0.54701 | 0 | 0.62134 | Cap-Tons/1000 sf | 820.2798 | 1007.3131 | 911.2798 | 0.6339 | 0.75217 | 0.68247 | 0 | 0 | 0 | 820.2798 | 1007.3131 | 911.2798 | 0.6339 | 0.75217 | 0.68247 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | New | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 0.621 | 0 | 0.70538 | Cap-Tons/1000 sf | 681.2667 | 799.2333 | 735.6 | 0.80567 | 0.92467 | 0.84817 | 0 | 0 | 0 | 681.2667 | 799.2333 | 735.6 | 0.80567 | 0.92467 | 0.84817 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | New | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 0.79463 | 0 | 0.84519 | Cap-Tons/1000 sf | 1058.3667 | 1180.1667 | 1116.2667 | 0.84603 | 0.9346 | 0.8896 | 0 | 0 | 0 | 1058.3667 | 1180.1667 | 1116.2667 | 0.84603 | 0.9346 | 0.8896 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | New | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 0.61214 | 0 | 0.69532 | Cap-Tons/1000 sf | 817.6167 | 941.3167 | 875.2167 | 0.91722 | 1.0366 | 0.96079 | 0 | 0 | 0 | 817.6167 | 941.3167 | 875.2167 | 0.91722 | 1.0366 | 0.96079 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EUN | EDUCATION - UNIVERSITY | New | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 0.58484 | 0 | 0.62204 | Cap-Tons/1000 sf | 821.9885 | 1032.3885 | 920.5885 | 0.50145 | 0.60745 | 0.54752 | 0 | 0 | 0 | 821.9885 | 1032.3885 | 920.5885 | 0.50145 | 0.60745 | 0.54752 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | GRO | GROCERY | New | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 1.0397 | 0 | 1.1059 | Cap-Tons/1000 sf | 836.1167 | 1089.7833 | 955.9833 | 0.19816 | 0.26607 | 0.23606 | 0 | 0 | 0 | 836.1167 | 1089.7833 | 955.9833 | 0.19816 | 0.26607 | 0.23606 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | New | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 0.77621 | 0 | 0.88169 | Cap-Tons/1000 sf | 1203.25 | 1563.9167 | 1370.2167 | 0.17329 | 0.23955 | 0.19975 | 0 | 0 | 0 | 1203.25 | 1563.9167 | 1370.2167 | 0.17329 | 0.23955 | 0.19975 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HTL | LODGING - HOTEL | New | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 0.46549 | 0 | 0.49511 | Cap-Tons/1000 sf | 1455.9 | 1807.9 | 1617.5667 | 0.33314 | 0.42001 | 0.37981 | 0 | 0 | 0 | 1455.9 | 1807.9 | 1617.5667 | 0.33314 | 0.42001 | 0.37981 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | MTL | LODGING - MOTEL | New | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 0.46549 | 0 | 0.49511 | Cap-Tons/1000 sf | 1455.9 | 1807.9 | 1617.5667 | 0.33314 | 0.42001 | 0.37981 | 0 | 0 | 0 | 1455.9 | 1807.9 | 1617.5667 | 0.33314 | 0.42001 | 0.37981 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | New | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 0.82895 | 0 | 0.88169 | Cap-Tons/1000 sf | 1121.5 | 1436.1667 | 1266.8333 | 0.17124 | 0.23331 | 0.19477 | 0 | 0 | 0 | 1121.5 | 1436.1667 | 1266.8333 | 0.17124 | 0.23331 | 0.19477 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFL | OFFICE - LARGE | New | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 0.61708 | 0 | 0.65634 | Cap-Tons/1000 sf | 1268.4599 | 1435.5599 | 1347.0933 | 0.71308 | 0.80255 | 0.76058 | 0 | 0 | 0 | 1268.4599 | 1435.5599 | 1347.0933 | 0.71308 | 0.80255 | 0.76058 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFS | OFFICE - SMALL | New | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 0.65556 | 0 | 0.74464 | Cap-Tons/1000 sf | 922.7846 | 1086.1179 | 997.9846 | 0.50774 | 0.5988 | 0.55667 | 0 | 0 | 0 | 922.7846 | 1086.1179 | 997.9846 | 0.50774 | 0.5988 | 0.55667 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | New | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 1.143 | 0 | 1.2984 | Cap-Tons/1000 sf | 1290 | 1593.6667 | 1428.3333 | 0.53332 | 0.65099 | 0.57632 | 0 | 0 | 0 | 1290 | 1593.6667 | 1428.3333 | 0.53332 | 0.65099 | 0.57632 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | New | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 0.77022 | 0 | 0.87488 | Cap-Tons/1000 sf | 1302.6442 | 1545.3109 | 1411.1442 | 0.90556 | 1.0442 | 0.94833 | 0 | 0 | 0 | 1302.6442 | 1545.3109 | 1411.1442 | 0.90556 | 1.0442 | 0.94833 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | New | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 0.37551 | 0 | 0.3994 | Cap-Tons/1000 sf | 1151.9815 | 1382.2148 | 1266.6815 | 0.76972 | 0.88599 | 0.81812 | 0 | 0 | 0 | 1151.9815 | 1382.2148 | 1266.6815 | 0.76972 | 0.88599 | 0.81812 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | New | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 0.40936 | 0 | 0.46499 | Cap-Tons/1000 sf | 1185.5644 | 1433.8978 | 1302.2311 | 0.59187 | 0.70107 | 0.63591 | 0 | 0 | 0 | 1185.5644 | 1433.8978 | 1302.2311 | 0.59187 | 0.70107 | 0.63591 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTS | RETAIL - SMALL | New | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 0.45321 | 0 | 0.51479 | Cap-Tons/1000 sf | 1139.345 | 1353.6783 | 1247.045 | 0.66171 | 0.76958 | 0.71351 | 0 | 0 | 0 | 1139.345 | 1353.6783 | 1247.045 | 0.66171 | 0.76958 | 0.71351 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | SCN | STORAGE - CONDITIONED | New | CZ09 | Pasadena Area (CZ09) |  |  |  | 1000 sf | 0.24791 | 0 | 0.2816 | Cap-Tons/1000 sf | 747.8167 | 912.5167 | 824.9833 | 0.25432 | 0.32046 | 0.27906 | 0 | 0 | 0 | 747.8167 | 912.5167 | 824.9833 | 0.25432 | 0.32046 | 0.27906 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ASM | ASSEMBLY | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.93897 | 0 | 1.0666 | Cap-Tons/1000 sf | 858.1333 | 1394.6667 | 976.1 | 0.53547 | 0.86961 | 0.5883 | 0 | 0 | 0 | 858.1333 | 1394.6667 | 976.1 | 0.53547 | 0.86961 | 0.5883 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.54701 | 0 | 0.62134 | Cap-Tons/1000 sf | 604.3879 | 1007.3131 | 704.3879 | 0.40997 | 0.68328 | 0.46397 | 0 | 0 | 0 | 604.3879 | 1007.3131 | 704.3879 | 0.40997 | 0.68328 | 0.46397 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.621 | 0 | 0.70538 | Cap-Tons/1000 sf | 494.8733 | 799.2333 | 561.1067 | 0.54233 | 0.87446 | 0.59486 | 0 | 0 | 0 | 494.8733 | 799.2333 | 561.1067 | 0.54233 | 0.87446 | 0.59486 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.79463 | 0 | 0.84519 | Cap-Tons/1000 sf | 729.1667 | 1180.1667 | 817.7667 | 0.55336 | 0.89149 | 0.60803 | 0 | 0 | 0 | 729.1667 | 1180.1667 | 817.7667 | 0.55336 | 0.89149 | 0.60803 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.61214 | 0 | 0.69532 | Cap-Tons/1000 sf | 613.59 | 941.3167 | 683.3567 | 0.66123 | 1.0093 | 0.71523 | 0 | 0 | 0 | 613.59 | 941.3167 | 683.3567 | 0.66123 | 1.0093 | 0.71523 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EUN | EDUCATION - UNIVERSITY | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.58484 | 0 | 0.62204 | Cap-Tons/1000 sf | 619.4331 | 1032.3885 | 731.5331 | 0.37053 | 0.61756 | 0.42593 | 0 | 0 | 0 | 619.4331 | 1032.3885 | 731.5331 | 0.37053 | 0.61756 | 0.42593 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | GRO | GROCERY | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 1.0397 | 0 | 1.1059 | Cap-Tons/1000 sf | 675.3367 | 1089.7833 | 801.0033 | 0.36757 | 0.59194 | 0.40777 | 0 | 0 | 0 | 675.3367 | 1089.7833 | 801.0033 | 0.36757 | 0.59194 | 0.40777 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.77621 | 0 | 0.88169 | Cap-Tons/1000 sf | 938.35 | 1563.9167 | 1115.35 | 0.27684 | 0.4614 | 0.32568 | 0 | 0 | 0 | 938.35 | 1563.9167 | 1115.35 | 0.27684 | 0.4614 | 0.32568 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HTL | LODGING - HOTEL | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.46549 | 0 | 0.49511 | Cap-Tons/1000 sf | 1084.74 | 1807.9 | 1264.74 | 0.40084 | 0.66807 | 0.45878 | 0 | 0 | 0 | 1084.74 | 1807.9 | 1264.74 | 0.40084 | 0.66807 | 0.45878 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | MTL | LODGING - MOTEL | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.46549 | 0 | 0.49511 | Cap-Tons/1000 sf | 1084.74 | 1807.9 | 1264.74 | 0.40084 | 0.66807 | 0.45878 | 0 | 0 | 0 | 1084.74 | 1807.9 | 1264.74 | 0.40084 | 0.66807 | 0.45878 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.82895 | 0 | 0.88169 | Cap-Tons/1000 sf | 861.7 | 1436.1667 | 1023.8667 | 0.3008 | 0.50134 | 0.34457 | 0 | 0 | 0 | 861.7 | 1436.1667 | 1023.8667 | 0.3008 | 0.50134 | 0.34457 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFL | OFFICE - LARGE | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.61708 | 0 | 0.65634 | Cap-Tons/1000 sf | 929.2266 | 1435.5599 | 1017.5599 | 0.61138 | 0.94538 | 0.66561 | 0 | 0 | 0 | 929.2266 | 1435.5599 | 1017.5599 | 0.61138 | 0.94538 | 0.66561 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFS | OFFICE - SMALL | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.65556 | 0 | 0.74464 | Cap-Tons/1000 sf | 651.6708 | 1086.1179 | 734.0708 | 0.47677 | 0.79461 | 0.53317 | 0 | 0 | 0 | 651.6708 | 1086.1179 | 734.0708 | 0.47677 | 0.79461 | 0.53317 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 1.143 | 0 | 1.2984 | Cap-Tons/1000 sf | 973 | 1593.6667 | 1125.3333 | 0.47119 | 0.77097 | 0.52312 | 0 | 0 | 0 | 973 | 1593.6667 | 1125.3333 | 0.47119 | 0.77097 | 0.52312 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.77022 | 0 | 0.87488 | Cap-Tons/1000 sf | 927.1865 | 1545.3109 | 1051.1865 | 0.58011 | 0.96685 | 0.63921 | 0 | 0 | 0 | 927.1865 | 1545.3109 | 1051.1865 | 0.58011 | 0.96685 | 0.63921 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.37551 | 0 | 0.3994 | Cap-Tons/1000 sf | 829.3289 | 1382.2148 | 953.0955 | 0.45556 | 0.75926 | 0.51129 | 0 | 0 | 0 | 829.3289 | 1382.2148 | 953.0955 | 0.45556 | 0.75926 | 0.51129 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.40936 | 0 | 0.46499 | Cap-Tons/1000 sf | 860.3387 | 1433.8978 | 993.3387 | 0.46163 | 0.76938 | 0.51616 | 0 | 0 | 0 | 860.3387 | 1433.8978 | 993.3387 | 0.46163 | 0.76938 | 0.51616 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTS | RETAIL - SMALL | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.45321 | 0 | 0.51479 | Cap-Tons/1000 sf | 812.207 | 1353.6783 | 929.7403 | 0.46497 | 0.77495 | 0.52557 | 0 | 0 | 0 | 812.207 | 1353.6783 | 929.7403 | 0.46497 | 0.77495 | 0.52557 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | SCN | STORAGE - CONDITIONED | Existing | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.24791 | 0 | 0.2816 | Cap-Tons/1000 sf | 606.5767 | 912.5167 | 693.2433 | 0.44311 | 0.65727 | 0.48818 | 0 | 0 | 0 | 606.5767 | 912.5167 | 693.2433 | 0.44311 | 0.65727 | 0.48818 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ASM | ASSEMBLY | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.93897 | 0 | 1.0666 | Cap-Tons/1000 sf | 1153.2333 | 1394.6667 | 1267.6333 | 0.48793 | 0.5932 | 0.5412 | 0 | 0 | 0 | 1153.2333 | 1394.6667 | 1267.6333 | 0.48793 | 0.5932 | 0.5412 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.54701 | 0 | 0.62134 | Cap-Tons/1000 sf | 823.6131 | 1007.3131 | 914.6798 | 0.34627 | 0.43668 | 0.39657 | 0 | 0 | 0 | 823.6131 | 1007.3131 | 914.6798 | 0.34627 | 0.43668 | 0.39657 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.621 | 0 | 0.70538 | Cap-Tons/1000 sf | 680.2667 | 799.2333 | 737.3 | 0.56073 | 0.65947 | 0.60937 | 0 | 0 | 0 | 680.2667 | 799.2333 | 737.3 | 0.56073 | 0.65947 | 0.60937 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.79463 | 0 | 0.84519 | Cap-Tons/1000 sf | 1050.2333 | 1180.1667 | 1114.0667 | 0.42966 | 0.50966 | 0.4604 | 0 | 0 | 0 | 1050.2333 | 1180.1667 | 1114.0667 | 0.42966 | 0.50966 | 0.4604 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.61214 | 0 | 0.69532 | Cap-Tons/1000 sf | 815.8833 | 941.3167 | 876.45 | 0.61257 | 0.7112 | 0.66323 | 0 | 0 | 0 | 815.8833 | 941.3167 | 876.45 | 0.61257 | 0.7112 | 0.66323 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EUN | EDUCATION - UNIVERSITY | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.58484 | 0 | 0.62204 | Cap-Tons/1000 sf | 818.0552 | 1032.3885 | 923.7885 | 0.26985 | 0.35985 | 0.30308 | 0 | 0 | 0 | 818.0552 | 1032.3885 | 923.7885 | 0.26985 | 0.35985 | 0.30308 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | GRO | GROCERY | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 1.0397 | 0 | 1.1059 | Cap-Tons/1000 sf | 832.1167 | 1089.7833 | 953.45 | 0.19938 | 0.27205 | 0.22542 | 0 | 0 | 0 | 832.1167 | 1089.7833 | 953.45 | 0.19938 | 0.27205 | 0.22542 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.77621 | 0 | 0.88169 | Cap-Tons/1000 sf | 1207.65 | 1563.9167 | 1371.9833 | 0.17731 | 0.24531 | 0.20711 | 0 | 0 | 0 | 1207.65 | 1563.9167 | 1371.9833 | 0.17731 | 0.24531 | 0.20711 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HTL | LODGING - HOTEL | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.46549 | 0 | 0.49511 | Cap-Tons/1000 sf | 1458.7 | 1807.9 | 1622.3667 | 0.28922 | 0.37455 | 0.32268 | 0 | 0 | 0 | 1458.7 | 1807.9 | 1622.3667 | 0.28922 | 0.37455 | 0.32268 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | MTL | LODGING - MOTEL | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.46549 | 0 | 0.49511 | Cap-Tons/1000 sf | 1458.7 | 1807.9 | 1622.3667 | 0.28922 | 0.37455 | 0.32268 | 0 | 0 | 0 | 1458.7 | 1807.9 | 1622.3667 | 0.28922 | 0.37455 | 0.32268 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.82895 | 0 | 0.88169 | Cap-Tons/1000 sf | 1124.0667 | 1436.1667 | 1269.9 | 0.17699 | 0.24219 | 0.20222 | 0 | 0 | 0 | 1124.0667 | 1436.1667 | 1269.9 | 0.17699 | 0.24219 | 0.20222 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFL | OFFICE - LARGE | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.61708 | 0 | 0.65634 | Cap-Tons/1000 sf | 1266.6599 | 1435.5599 | 1348.1266 | 0.43273 | 0.51873 | 0.46777 | 0 | 0 | 0 | 1266.6599 | 1435.5599 | 1348.1266 | 0.43273 | 0.51873 | 0.46777 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFS | OFFICE - SMALL | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.65556 | 0 | 0.74464 | Cap-Tons/1000 sf | 918.3846 | 1086.1179 | 998.5179 | 0.35994 | 0.45061 | 0.39884 | 0 | 0 | 0 | 918.3846 | 1086.1179 | 998.5179 | 0.35994 | 0.45061 | 0.39884 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 1.143 | 0 | 1.2984 | Cap-Tons/1000 sf | 1282.6667 | 1593.6667 | 1431.3333 | 0.4184 | 0.52187 | 0.47027 | 0 | 0 | 0 | 1282.6667 | 1593.6667 | 1431.3333 | 0.4184 | 0.52187 | 0.47027 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.77022 | 0 | 0.87488 | Cap-Tons/1000 sf | 1292.6442 | 1545.3109 | 1412.9776 | 0.54026 | 0.65033 | 0.59643 | 0 | 0 | 0 | 1292.6442 | 1545.3109 | 1412.9776 | 0.54026 | 0.65033 | 0.59643 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.37551 | 0 | 0.3994 | Cap-Tons/1000 sf | 1147.2481 | 1382.2148 | 1268.3148 | 0.39352 | 0.48782 | 0.44859 | 0 | 0 | 0 | 1147.2481 | 1382.2148 | 1268.3148 | 0.39352 | 0.48782 | 0.44859 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.40936 | 0 | 0.46499 | Cap-Tons/1000 sf | 1181.7978 | 1433.8978 | 1307.7978 | 0.39992 | 0.49375 | 0.45168 | 0 | 0 | 0 | 1181.7978 | 1433.8978 | 1307.7978 | 0.39992 | 0.49375 | 0.45168 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTS | RETAIL - SMALL | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.45321 | 0 | 0.51479 | Cap-Tons/1000 sf | 1140.8117 | 1353.6783 | 1250.445 | 0.36727 | 0.45727 | 0.40114 | 0 | 0 | 0 | 1140.8117 | 1353.6783 | 1250.445 | 0.36727 | 0.45727 | 0.40114 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | SCN | STORAGE - CONDITIONED | New | CZ10 | San Bernardino Area (CZ10) |  |  |  | 1000 sf | 0.24791 | 0 | 0.2816 | Cap-Tons/1000 sf | 747.85 | 912.5167 | 828.7833 | 0.26299 | 0.33499 | 0.28999 | 0 | 0 | 0 | 747.85 | 912.5167 | 828.7833 | 0.26299 | 0.33499 | 0.28999 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ASM | ASSEMBLY | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.93897 | 0 | 1.0666 | Cap-Tons/1000 sf | 836.8 | 1394.6667 | 959.5333 | 0.43583 | 0.72638 | 0.48146 | 0 | 0 | 0 | 836.8 | 1394.6667 | 959.5333 | 0.43583 | 0.72638 | 0.48146 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.54701 | 0 | 0.62134 | Cap-Tons/1000 sf | 604.3879 | 1007.3131 | 715.6212 | 0.31033 | 0.51722 | 0.35783 | 0 | 0 | 0 | 604.3879 | 1007.3131 | 715.6212 | 0.31033 | 0.51722 | 0.35783 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.621 | 0 | 0.70538 | Cap-Tons/1000 sf | 479.54 | 799.2333 | 556.24 | 0.1583 | 0.26383 | 0.18293 | 0 | 0 | 0 | 479.54 | 799.2333 | 556.24 | 0.1583 | 0.26383 | 0.18293 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.79463 | 0 | 0.84519 | Cap-Tons/1000 sf | 708.1 | 1180.1667 | 815.7667 | 0.24776 | 0.41293 | 0.28116 | 0 | 0 | 0 | 708.1 | 1180.1667 | 815.7667 | 0.24776 | 0.41293 | 0.28116 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.61214 | 0 | 0.69532 | Cap-Tons/1000 sf | 569.59 | 941.3167 | 655.09 | 0.16009 | 0.26453 | 0.18322 | 0 | 0 | 0 | 569.59 | 941.3167 | 655.09 | 0.16009 | 0.26453 | 0.18322 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EUN | EDUCATION - UNIVERSITY | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.58484 | 0 | 0.62204 | Cap-Tons/1000 sf | 619.4331 | 1032.3885 | 738.1331 | 0.29295 | 0.48825 | 0.34011 | 0 | 0 | 0 | 619.4331 | 1032.3885 | 738.1331 | 0.29295 | 0.48825 | 0.34011 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | GRO | GROCERY | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 1.0397 | 0 | 1.1059 | Cap-Tons/1000 sf | 653.87 | 1089.7833 | 783.2033 | 0.29558 | 0.49263 | 0.33265 | 0 | 0 | 0 | 653.87 | 1089.7833 | 783.2033 | 0.29558 | 0.49263 | 0.33265 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.77621 | 0 | 0.88169 | Cap-Tons/1000 sf | 938.35 | 1563.9167 | 1121.6833 | 0.2552 | 0.42533 | 0.2976 | 0 | 0 | 0 | 938.35 | 1563.9167 | 1121.6833 | 0.2552 | 0.42533 | 0.2976 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HTL | LODGING - HOTEL | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.46549 | 0 | 0.49511 | Cap-Tons/1000 sf | 1084.74 | 1807.9 | 1270.0733 | 0.36426 | 0.60711 | 0.4153 | 0 | 0 | 0 | 1084.74 | 1807.9 | 1270.0733 | 0.36426 | 0.60711 | 0.4153 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | MTL | LODGING - MOTEL | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.46549 | 0 | 0.49511 | Cap-Tons/1000 sf | 1084.74 | 1807.9 | 1270.0733 | 0.36426 | 0.60711 | 0.4153 | 0 | 0 | 0 | 1084.74 | 1807.9 | 1270.0733 | 0.36426 | 0.60711 | 0.4153 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.82895 | 0 | 0.88169 | Cap-Tons/1000 sf | 861.7 | 1436.1667 | 1030.7 | 0.25966 | 0.43277 | 0.2998 | 0 | 0 | 0 | 861.7 | 1436.1667 | 1030.7 | 0.25966 | 0.43277 | 0.2998 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFL | OFFICE - LARGE | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.61708 | 0 | 0.65634 | Cap-Tons/1000 sf | 902.5599 | 1435.5599 | 994.1933 | 0.5327 | 0.8477 | 0.58076 | 0 | 0 | 0 | 902.5599 | 1435.5599 | 994.1933 | 0.5327 | 0.8477 | 0.58076 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFS | OFFICE - SMALL | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.65556 | 0 | 0.74464 | Cap-Tons/1000 sf | 651.6708 | 1086.1179 | 737.9374 | 0.42359 | 0.70598 | 0.47199 | 0 | 0 | 0 | 651.6708 | 1086.1179 | 737.9374 | 0.42359 | 0.70598 | 0.47199 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 1.143 | 0 | 1.2984 | Cap-Tons/1000 sf | 956.2 | 1593.6667 | 1115.8667 | 0.37779 | 0.62965 | 0.42482 | 0 | 0 | 0 | 956.2 | 1593.6667 | 1115.8667 | 0.37779 | 0.62965 | 0.42482 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.77022 | 0 | 0.87488 | Cap-Tons/1000 sf | 927.1865 | 1545.3109 | 1051.8532 | 0.47079 | 0.78466 | 0.51623 | 0 | 0 | 0 | 927.1865 | 1545.3109 | 1051.8532 | 0.47079 | 0.78466 | 0.51623 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.37551 | 0 | 0.3994 | Cap-Tons/1000 sf | 829.3289 | 1382.2148 | 954.5622 | 0.40709 | 0.67848 | 0.45779 | 0 | 0 | 0 | 829.3289 | 1382.2148 | 954.5622 | 0.40709 | 0.67848 | 0.45779 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.40936 | 0 | 0.46499 | Cap-Tons/1000 sf | 860.3387 | 1433.8978 | 998.0053 | 0.40736 | 0.67893 | 0.45806 | 0 | 0 | 0 | 860.3387 | 1433.8978 | 998.0053 | 0.40736 | 0.67893 | 0.45806 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTS | RETAIL - SMALL | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.45321 | 0 | 0.51479 | Cap-Tons/1000 sf | 812.207 | 1353.6783 | 936.5403 | 0.43195 | 0.71992 | 0.48895 | 0 | 0 | 0 | 812.207 | 1353.6783 | 936.5403 | 0.43195 | 0.71992 | 0.48895 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | SCN | STORAGE - CONDITIONED | Existing | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.24791 | 0 | 0.2816 | Cap-Tons/1000 sf | 558.5767 | 912.5167 | 652.6767 | 0.33792 | 0.55082 | 0.38148 | 0 | 0 | 0 | 558.5767 | 912.5167 | 652.6767 | 0.33792 | 0.55082 | 0.38148 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ASM | ASSEMBLY | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.93897 | 0 | 1.0666 | Cap-Tons/1000 sf | 1155.7667 | 1394.6667 | 1271.1667 | 0.62603 | 0.73183 | 0.66873 | 0 | 0 | 0 | 1155.7667 | 1394.6667 | 1271.1667 | 0.62603 | 0.73183 | 0.66873 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.54701 | 0 | 0.62134 | Cap-Tons/1000 sf | 797.3798 | 1007.3131 | 906.6131 | 0.40494 | 0.5 | 0.45334 | 0 | 0 | 0 | 797.3798 | 1007.3131 | 906.6131 | 0.40494 | 0.5 | 0.45334 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.621 | 0 | 0.70538 | Cap-Tons/1000 sf | 666.2 | 799.2333 | 732.8333 | 0.15127 | 0.18704 | 0.1706 | 0 | 0 | 0 | 666.2 | 799.2333 | 732.8333 | 0.15127 | 0.18704 | 0.1706 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.79463 | 0 | 0.84519 | Cap-Tons/1000 sf | 1010.2 | 1180.1667 | 1096.9 | 0.1847 | 0.2335 | 0.20407 | 0 | 0 | 0 | 1010.2 | 1180.1667 | 1096.9 | 0.1847 | 0.2335 | 0.20407 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.61214 | 0 | 0.69532 | Cap-Tons/1000 sf | 795.9167 | 941.3167 | 869.25 | 0.12286 | 0.15053 | 0.13456 | 0 | 0 | 0 | 795.9167 | 941.3167 | 869.25 | 0.12286 | 0.15053 | 0.13456 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EUN | EDUCATION - UNIVERSITY | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.58484 | 0 | 0.62204 | Cap-Tons/1000 sf | 817.8219 | 1032.3885 | 928.4885 | 0.22522 | 0.30085 | 0.27036 | 0 | 0 | 0 | 817.8219 | 1032.3885 | 928.4885 | 0.22522 | 0.30085 | 0.27036 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | GRO | GROCERY | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 1.0397 | 0 | 1.1059 | Cap-Tons/1000 sf | 822.7833 | 1089.7833 | 950.1167 | 0.17343 | 0.2399 | 0.19843 | 0 | 0 | 0 | 822.7833 | 1089.7833 | 950.1167 | 0.17343 | 0.2399 | 0.19843 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.77621 | 0 | 0.88169 | Cap-Tons/1000 sf | 1212.1167 | 1563.9167 | 1378.7833 | 0.16397 | 0.22757 | 0.1892 | 0 | 0 | 0 | 1212.1167 | 1563.9167 | 1378.7833 | 0.16397 | 0.22757 | 0.1892 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HTL | LODGING - HOTEL | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.46549 | 0 | 0.49511 | Cap-Tons/1000 sf | 1462.4667 | 1807.9 | 1633.8 | 0.26669 | 0.34602 | 0.29699 | 0 | 0 | 0 | 1462.4667 | 1807.9 | 1633.8 | 0.26669 | 0.34602 | 0.29699 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | MTL | LODGING - MOTEL | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.46549 | 0 | 0.49511 | Cap-Tons/1000 sf | 1462.4667 | 1807.9 | 1633.8 | 0.26669 | 0.34602 | 0.29699 | 0 | 0 | 0 | 1462.4667 | 1807.9 | 1633.8 | 0.26669 | 0.34602 | 0.29699 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.82895 | 0 | 0.88169 | Cap-Tons/1000 sf | 1124.1667 | 1436.1667 | 1277.8333 | 0.15805 | 0.21799 | 0.18182 | 0 | 0 | 0 | 1124.1667 | 1436.1667 | 1277.8333 | 0.15805 | 0.21799 | 0.18182 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFL | OFFICE - LARGE | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.61708 | 0 | 0.65634 | Cap-Tons/1000 sf | 1265.7266 | 1435.5599 | 1350.9933 | 0.4057 | 0.48837 | 0.43813 | 0 | 0 | 0 | 1265.7266 | 1435.5599 | 1350.9933 | 0.4057 | 0.48837 | 0.43813 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFS | OFFICE - SMALL | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.65556 | 0 | 0.74464 | Cap-Tons/1000 sf | 919.9179 | 1086.1179 | 1001.4513 | 0.36496 | 0.45066 | 0.41629 | 0 | 0 | 0 | 919.9179 | 1086.1179 | 1001.4513 | 0.36496 | 0.45066 | 0.41629 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 1.143 | 0 | 1.2984 | Cap-Tons/1000 sf | 1288.3333 | 1593.6667 | 1438.3333 | 0.37099 | 0.45879 | 0.41436 | 0 | 0 | 0 | 1288.3333 | 1593.6667 | 1438.3333 | 0.37099 | 0.45879 | 0.41436 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.77022 | 0 | 0.87488 | Cap-Tons/1000 sf | 1308.7109 | 1545.3109 | 1422.0442 | 0.63766 | 0.73523 | 0.67716 | 0 | 0 | 0 | 1308.7109 | 1545.3109 | 1422.0442 | 0.63766 | 0.73523 | 0.67716 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.37551 | 0 | 0.3994 | Cap-Tons/1000 sf | 1162.3481 | 1382.2148 | 1280.4481 | 0.50631 | 0.59197 | 0.55404 | 0 | 0 | 0 | 1162.3481 | 1382.2148 | 1280.4481 | 0.50631 | 0.59197 | 0.55404 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.40936 | 0 | 0.46499 | Cap-Tons/1000 sf | 1185.6311 | 1433.8978 | 1316.9644 | 0.44 | 0.52863 | 0.48777 | 0 | 0 | 0 | 1185.6311 | 1433.8978 | 1316.9644 | 0.44 | 0.52863 | 0.48777 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTS | RETAIL - SMALL | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.45321 | 0 | 0.51479 | Cap-Tons/1000 sf | 1139.2783 | 1353.6783 | 1255.6117 | 0.33794 | 0.42461 | 0.37158 | 0 | 0 | 0 | 1139.2783 | 1353.6783 | 1255.6117 | 0.33794 | 0.42461 | 0.37158 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | SCN | STORAGE - CONDITIONED | New | CZ13 | Fresno Area (CZ13) |  |  |  | 1000 sf | 0.24791 | 0 | 0.2816 | Cap-Tons/1000 sf | 746.65 | 912.5167 | 833.2833 | 0.22149 | 0.28629 | 0.24662 | 0 | 0 | 0 | 746.65 | 912.5167 | 833.2833 | 0.22149 | 0.28629 | 0.24662 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ASM | ASSEMBLY | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.93897 | 0 | 1.0666 | Cap-Tons/1000 sf | 836.8 | 1394.6667 | 965.1333 | 0.46537 | 0.77562 | 0.53024 | 0 | 0 | 0 | 836.8 | 1394.6667 | 965.1333 | 0.46537 | 0.77562 | 0.53024 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.54701 | 0 | 0.62134 | Cap-Tons/1000 sf | 604.3879 | 1007.3131 | 716.4879 | 0.37136 | 0.61894 | 0.42803 | 0 | 0 | 0 | 604.3879 | 1007.3131 | 716.4879 | 0.37136 | 0.61894 | 0.42803 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.621 | 0 | 0.70538 | Cap-Tons/1000 sf | 479.54 | 799.2333 | 554.1067 | 0.4678 | 0.77966 | 0.52146 | 0 | 0 | 0 | 479.54 | 799.2333 | 554.1067 | 0.4678 | 0.77966 | 0.52146 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.79463 | 0 | 0.84519 | Cap-Tons/1000 sf | 708.1 | 1180.1667 | 812.9333 | 0.46571 | 0.77619 | 0.51861 | 0 | 0 | 0 | 708.1 | 1180.1667 | 812.9333 | 0.46571 | 0.77619 | 0.51861 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.61214 | 0 | 0.69532 | Cap-Tons/1000 sf | 570.2567 | 941.3167 | 652.29 | 0.52716 | 0.86947 | 0.5842 | 0 | 0 | 0 | 570.2567 | 941.3167 | 652.29 | 0.52716 | 0.86947 | 0.5842 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EUN | EDUCATION - UNIVERSITY | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.58484 | 0 | 0.62204 | Cap-Tons/1000 sf | 619.4331 | 1032.3885 | 739.0331 | 0.34095 | 0.56825 | 0.39892 | 0 | 0 | 0 | 619.4331 | 1032.3885 | 739.0331 | 0.34095 | 0.56825 | 0.39892 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | GRO | GROCERY | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 1.0397 | 0 | 1.1059 | Cap-Tons/1000 sf | 656.67 | 1089.7833 | 783.67 | 0.30385 | 0.50411 | 0.34355 | 0 | 0 | 0 | 656.67 | 1089.7833 | 783.67 | 0.30385 | 0.50411 | 0.34355 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.77621 | 0 | 0.88169 | Cap-Tons/1000 sf | 938.35 | 1563.9167 | 1120.0167 | 0.2709 | 0.4515 | 0.3187 | 0 | 0 | 0 | 938.35 | 1563.9167 | 1120.0167 | 0.2709 | 0.4515 | 0.3187 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HTL | LODGING - HOTEL | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.46549 | 0 | 0.49511 | Cap-Tons/1000 sf | 1084.74 | 1807.9 | 1265.74 | 0.37402 | 0.62337 | 0.43199 | 0 | 0 | 0 | 1084.74 | 1807.9 | 1265.74 | 0.37402 | 0.62337 | 0.43199 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | MTL | LODGING - MOTEL | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.46549 | 0 | 0.49511 | Cap-Tons/1000 sf | 1084.74 | 1807.9 | 1265.74 | 0.37402 | 0.62337 | 0.43199 | 0 | 0 | 0 | 1084.74 | 1807.9 | 1265.74 | 0.37402 | 0.62337 | 0.43199 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.82895 | 0 | 0.88169 | Cap-Tons/1000 sf | 861.7 | 1436.1667 | 1032.7 | 0.28415 | 0.47359 | 0.32492 | 0 | 0 | 0 | 861.7 | 1436.1667 | 1032.7 | 0.28415 | 0.47359 | 0.32492 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFL | OFFICE - LARGE | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.61708 | 0 | 0.65634 | Cap-Tons/1000 sf | 896.2266 | 1435.5599 | 987.0599 | 0.52264 | 0.83798 | 0.57144 | 0 | 0 | 0 | 896.2266 | 1435.5599 | 987.0599 | 0.52264 | 0.83798 | 0.57144 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFS | OFFICE - SMALL | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.65556 | 0 | 0.74464 | Cap-Tons/1000 sf | 651.6708 | 1086.1179 | 736.4708 | 0.43107 | 0.71845 | 0.48154 | 0 | 0 | 0 | 651.6708 | 1086.1179 | 736.4708 | 0.43107 | 0.71845 | 0.48154 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 1.143 | 0 | 1.2984 | Cap-Tons/1000 sf | 956.2 | 1593.6667 | 1113.8667 | 0.40326 | 0.67211 | 0.45063 | 0 | 0 | 0 | 956.2 | 1593.6667 | 1113.8667 | 0.40326 | 0.67211 | 0.45063 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.77022 | 0 | 0.87488 | Cap-Tons/1000 sf | 927.1865 | 1545.3109 | 1057.1865 | 0.52467 | 0.87446 | 0.58504 | 0 | 0 | 0 | 927.1865 | 1545.3109 | 1057.1865 | 0.52467 | 0.87446 | 0.58504 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.37551 | 0 | 0.3994 | Cap-Tons/1000 sf | 829.3289 | 1382.2148 | 957.3289 | 0.41931 | 0.69885 | 0.47467 | 0 | 0 | 0 | 829.3289 | 1382.2148 | 957.3289 | 0.41931 | 0.69885 | 0.47467 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.40936 | 0 | 0.46499 | Cap-Tons/1000 sf | 868.6053 | 1433.8978 | 1001.9387 | 0.40422 | 0.66665 | 0.45318 | 0 | 0 | 0 | 868.6053 | 1433.8978 | 1001.9387 | 0.40422 | 0.66665 | 0.45318 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTS | RETAIL - SMALL | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.45321 | 0 | 0.51479 | Cap-Tons/1000 sf | 812.207 | 1353.6783 | 938.207 | 0.43327 | 0.72212 | 0.49174 | 0 | 0 | 0 | 812.207 | 1353.6783 | 938.207 | 0.43327 | 0.72212 | 0.49174 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | SCN | STORAGE - CONDITIONED | Existing | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.24791 | 0 | 0.2816 | Cap-Tons/1000 sf | 559.2433 | 912.5167 | 653.51 | 0.36517 | 0.59425 | 0.4099 | 0 | 0 | 0 | 559.2433 | 912.5167 | 653.51 | 0.36517 | 0.59425 | 0.4099 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ASM | ASSEMBLY | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.93897 | 0 | 1.0666 | Cap-Tons/1000 sf | 1154.5667 | 1394.6667 | 1276.5667 | 0.33767 | 0.43301 | 0.37467 | 0 | 0 | 0 | 1154.5667 | 1394.6667 | 1276.5667 | 0.33767 | 0.43301 | 0.37467 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.54701 | 0 | 0.62134 | Cap-Tons/1000 sf | 801.6465 | 1007.3131 | 900.7131 | 0.28681 | 0.38348 | 0.31954 | 0 | 0 | 0 | 801.6465 | 1007.3131 | 900.7131 | 0.28681 | 0.38348 | 0.31954 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.621 | 0 | 0.70538 | Cap-Tons/1000 sf | 672.0333 | 799.2333 | 736.7333 | 0.37286 | 0.46286 | 0.40612 | 0 | 0 | 0 | 672.0333 | 799.2333 | 736.7333 | 0.37286 | 0.46286 | 0.40612 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.79463 | 0 | 0.84519 | Cap-Tons/1000 sf | 1016.7333 | 1180.1667 | 1099.6 | 0.32492 | 0.40758 | 0.35535 | 0 | 0 | 0 | 1016.7333 | 1180.1667 | 1099.6 | 0.32492 | 0.40758 | 0.35535 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.61214 | 0 | 0.69532 | Cap-Tons/1000 sf | 805.5167 | 941.3167 | 874.8833 | 0.42728 | 0.51928 | 0.46208 | 0 | 0 | 0 | 805.5167 | 941.3167 | 874.8833 | 0.42728 | 0.51928 | 0.46208 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EUN | EDUCATION - UNIVERSITY | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.58484 | 0 | 0.62204 | Cap-Tons/1000 sf | 821.9219 | 1032.3885 | 931.1219 | 0.2589 | 0.34957 | 0.29247 | 0 | 0 | 0 | 821.9219 | 1032.3885 | 931.1219 | 0.2589 | 0.34957 | 0.29247 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | GRO | GROCERY | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 1.0397 | 0 | 1.1059 | Cap-Tons/1000 sf | 825.45 | 1089.7833 | 950.45 | 0.1837 | 0.25237 | 0.21017 | 0 | 0 | 0 | 825.45 | 1089.7833 | 950.45 | 0.1837 | 0.25237 | 0.21017 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.77621 | 0 | 0.88169 | Cap-Tons/1000 sf | 1213.7167 | 1563.9167 | 1378.3833 | 0.17334 | 0.24001 | 0.20374 | 0 | 0 | 0 | 1213.7167 | 1563.9167 | 1378.3833 | 0.17334 | 0.24001 | 0.20374 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HTL | LODGING - HOTEL | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.46549 | 0 | 0.49511 | Cap-Tons/1000 sf | 1470.6333 | 1807.9 | 1637.3 | 0.28025 | 0.36092 | 0.31788 | 0 | 0 | 0 | 1470.6333 | 1807.9 | 1637.3 | 0.28025 | 0.36092 | 0.31788 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | MTL | LODGING - MOTEL | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.46549 | 0 | 0.49511 | Cap-Tons/1000 sf | 1470.6333 | 1807.9 | 1637.3 | 0.28025 | 0.36092 | 0.31788 | 0 | 0 | 0 | 1470.6333 | 1807.9 | 1637.3 | 0.28025 | 0.36092 | 0.31788 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.82895 | 0 | 0.88169 | Cap-Tons/1000 sf | 1125.9 | 1436.1667 | 1279.9 | 0.17202 | 0.23809 | 0.19472 | 0 | 0 | 0 | 1125.9 | 1436.1667 | 1279.9 | 0.17202 | 0.23809 | 0.19472 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFL | OFFICE - LARGE | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.61708 | 0 | 0.65634 | Cap-Tons/1000 sf | 1266.5266 | 1435.5599 | 1350.6599 | 0.41704 | 0.50371 | 0.45431 | 0 | 0 | 0 | 1266.5266 | 1435.5599 | 1350.6599 | 0.41704 | 0.50371 | 0.45431 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFS | OFFICE - SMALL | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.65556 | 0 | 0.74464 | Cap-Tons/1000 sf | 919.9179 | 1086.1179 | 999.7846 | 0.3464 | 0.43507 | 0.38503 | 0 | 0 | 0 | 919.9179 | 1086.1179 | 999.7846 | 0.3464 | 0.43507 | 0.38503 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 1.143 | 0 | 1.2984 | Cap-Tons/1000 sf | 1275 | 1593.6667 | 1434.3333 | 0.34267 | 0.43957 | 0.399 | 0 | 0 | 0 | 1275 | 1593.6667 | 1434.3333 | 0.34267 | 0.43957 | 0.399 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.77022 | 0 | 0.87488 | Cap-Tons/1000 sf | 1297.8776 | 1545.3109 | 1425.8776 | 0.3701 | 0.46602 | 0.4311 | 0 | 0 | 0 | 1297.8776 | 1545.3109 | 1425.8776 | 0.3701 | 0.46602 | 0.4311 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.37551 | 0 | 0.3994 | Cap-Tons/1000 sf | 1163.5 | 1487.5 | 1290 | 0.4812 | 0.6152 | 0.528 | 0 | 0 | 0 | 1163.5 | 1487.5 | 1290 | 0.4812 | 0.6152 | 0.528 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.40936 | 0 | 0.46499 | Cap-Tons/1000 sf | 1205.4644 | 1433.8978 | 1330.1311 | 0.3119 | 0.39057 | 0.3401 | 0 | 0 | 0 | 1205.4644 | 1433.8978 | 1330.1311 | 0.3119 | 0.39057 | 0.3401 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTS | RETAIL - SMALL | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.45321 | 0 | 0.51479 | Cap-Tons/1000 sf | 1205 | 1509 | 1330.5 | 0.53512 | 0.67012 | 0.58387 | 0 | 0 | 0 | 1205 | 1509 | 1330.5 | 0.53512 | 0.67012 | 0.58387 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | SCN | STORAGE - CONDITIONED | New | CZ14 | China Lake Area (CZ14) |  |  |  | 1000 sf | 0.24791 | 0 | 0.2816 | Cap-Tons/1000 sf | 751.08 | 912.5167 | 837.8467 | 0.23797 | 0.30797 | 0.26237 | 0 | 0 | 0 | 751.08 | 912.5167 | 837.8467 | 0.23797 | 0.30797 | 0.26237 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ASM | ASSEMBLY | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.93897 | 0 | 1.0666 | Cap-Tons/1000 sf | 836.8 | 1394.6667 | 991.4667 | 0.356 | 0.59334 | 0.41217 | 0 | 0 | 0 | 836.8 | 1394.6667 | 991.4667 | 0.356 | 0.59334 | 0.41217 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.54701 | 0 | 0.62134 | Cap-Tons/1000 sf | 604.3879 | 1007.3131 | 745.3879 | 0.28639 | 0.47732 | 0.34163 | 0 | 0 | 0 | 604.3879 | 1007.3131 | 745.3879 | 0.28639 | 0.47732 | 0.34163 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.621 | 0 | 0.70538 | Cap-Tons/1000 sf | 479.54 | 799.2333 | 577.9067 | 0.3398 | 0.56634 | 0.39187 | 0 | 0 | 0 | 479.54 | 799.2333 | 577.9067 | 0.3398 | 0.56634 | 0.39187 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.79463 | 0 | 0.84519 | Cap-Tons/1000 sf | 708.1 | 1180.1667 | 834.4333 | 0.34119 | 0.56865 | 0.39262 | 0 | 0 | 0 | 708.1 | 1180.1667 | 834.4333 | 0.34119 | 0.56865 | 0.39262 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.61214 | 0 | 0.69532 | Cap-Tons/1000 sf | 564.79 | 941.3167 | 682.59 | 0.34572 | 0.5762 | 0.39975 | 0 | 0 | 0 | 564.79 | 941.3167 | 682.59 | 0.34572 | 0.5762 | 0.39975 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EUN | EDUCATION - UNIVERSITY | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.58484 | 0 | 0.62204 | Cap-Tons/1000 sf | 619.4331 | 1032.3885 | 765.7665 | 0.27496 | 0.45826 | 0.32996 | 0 | 0 | 0 | 619.4331 | 1032.3885 | 765.7665 | 0.27496 | 0.45826 | 0.32996 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | GRO | GROCERY | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 1.0397 | 0 | 1.1059 | Cap-Tons/1000 sf | 653.87 | 1089.7833 | 798.2033 | 0.23311 | 0.38852 | 0.27141 | 0 | 0 | 0 | 653.87 | 1089.7833 | 798.2033 | 0.23311 | 0.38852 | 0.27141 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.77621 | 0 | 0.88169 | Cap-Tons/1000 sf | 938.35 | 1563.9167 | 1155.0167 | 0.2236 | 0.37266 | 0.27177 | 0 | 0 | 0 | 938.35 | 1563.9167 | 1155.0167 | 0.2236 | 0.37266 | 0.27177 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HTL | LODGING - HOTEL | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.46549 | 0 | 0.49511 | Cap-Tons/1000 sf | 1084.74 | 1807.9 | 1312.74 | 0.30356 | 0.50594 | 0.36103 | 0 | 0 | 0 | 1084.74 | 1807.9 | 1312.74 | 0.30356 | 0.50594 | 0.36103 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | MTL | LODGING - MOTEL | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.46549 | 0 | 0.49511 | Cap-Tons/1000 sf | 1084.74 | 1807.9 | 1312.74 | 0.30356 | 0.50594 | 0.36103 | 0 | 0 | 0 | 1084.74 | 1807.9 | 1312.74 | 0.30356 | 0.50594 | 0.36103 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.82895 | 0 | 0.88169 | Cap-Tons/1000 sf | 861.7 | 1436.1667 | 1065.7 | 0.22441 | 0.37401 | 0.26754 | 0 | 0 | 0 | 861.7 | 1436.1667 | 1065.7 | 0.22441 | 0.37401 | 0.26754 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFL | OFFICE - LARGE | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.61708 | 0 | 0.65634 | Cap-Tons/1000 sf | 861.336 | 1435.5599 | 978.5693 | 0.41811 | 0.69685 | 0.47278 | 0 | 0 | 0 | 861.336 | 1435.5599 | 978.5693 | 0.41811 | 0.69685 | 0.47278 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFS | OFFICE - SMALL | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.65556 | 0 | 0.74464 | Cap-Tons/1000 sf | 651.6708 | 1086.1179 | 764.6708 | 0.34164 | 0.56941 | 0.40074 | 0 | 0 | 0 | 651.6708 | 1086.1179 | 764.6708 | 0.34164 | 0.56941 | 0.40074 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 1.143 | 0 | 1.2984 | Cap-Tons/1000 sf | 956.2 | 1593.6667 | 1153.8667 | 0.3226 | 0.53766 | 0.37347 | 0 | 0 | 0 | 956.2 | 1593.6667 | 1153.8667 | 0.3226 | 0.53766 | 0.37347 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.77022 | 0 | 0.87488 | Cap-Tons/1000 sf | 927.1865 | 1545.3109 | 1075.5199 | 0.38122 | 0.63537 | 0.42959 | 0 | 0 | 0 | 927.1865 | 1545.3109 | 1075.5199 | 0.38122 | 0.63537 | 0.42959 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.37551 | 0 | 0.3994 | Cap-Tons/1000 sf | 829.3289 | 1382.2148 | 985.6622 | 0.33206 | 0.55344 | 0.38716 | 0 | 0 | 0 | 829.3289 | 1382.2148 | 985.6622 | 0.33206 | 0.55344 | 0.38716 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.40936 | 0 | 0.46499 | Cap-Tons/1000 sf | 860.3387 | 1433.8978 | 1031.0053 | 0.33413 | 0.55688 | 0.38879 | 0 | 0 | 0 | 860.3387 | 1433.8978 | 1031.0053 | 0.33413 | 0.55688 | 0.38879 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTS | RETAIL - SMALL | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.45321 | 0 | 0.51479 | Cap-Tons/1000 sf | 812.207 | 1353.6783 | 970.8737 | 0.33859 | 0.56432 | 0.39996 | 0 | 0 | 0 | 812.207 | 1353.6783 | 970.8737 | 0.33859 | 0.56432 | 0.39996 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | SCN | STORAGE - CONDITIONED | Existing | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.24791 | 0 | 0.2816 | Cap-Tons/1000 sf | 547.51 | 912.5167 | 662.7767 | 0.26989 | 0.44981 | 0.31759 | 0 | 0 | 0 | 547.51 | 912.5167 | 662.7767 | 0.26989 | 0.44981 | 0.31759 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ASM | ASSEMBLY | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.93897 | 0 | 1.0666 | Cap-Tons/1000 sf | 1086.3333 | 1394.6667 | 1217.3333 | 0.35664 | 0.46171 | 0.40547 | 0 | 0 | 0 | 1086.3333 | 1394.6667 | 1217.3333 | 0.35664 | 0.46171 | 0.40547 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.54701 | 0 | 0.62134 | Cap-Tons/1000 sf | 763.2465 | 1007.3131 | 895.9131 | 0.22643 | 0.32643 | 0.26596 | 0 | 0 | 0 | 763.2465 | 1007.3131 | 895.9131 | 0.22643 | 0.32643 | 0.26596 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.621 | 0 | 0.70538 | Cap-Tons/1000 sf | 636.9667 | 799.2333 | 720.8 | 0.47202 | 0.57106 | 0.52106 | 0 | 0 | 0 | 636.9667 | 799.2333 | 720.8 | 0.47202 | 0.57106 | 0.52106 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.79463 | 0 | 0.84519 | Cap-Tons/1000 sf | 839 | 1134 | 955 | 0.34698 | 0.46898 | 0.39108 | 0 | 0 | 0 | 839 | 1134 | 955 | 0.34698 | 0.46898 | 0.39108 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.61214 | 0 | 0.69532 | Cap-Tons/1000 sf | 752.55 | 941.3167 | 851.9833 | 0.41879 | 0.51656 | 0.47086 | 0 | 0 | 0 | 752.55 | 941.3167 | 851.9833 | 0.41879 | 0.51656 | 0.47086 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EUN | EDUCATION - UNIVERSITY | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.58484 | 0 | 0.62204 | Cap-Tons/1000 sf | 788.1852 | 1032.3885 | 921.5185 | 0.20732 | 0.29932 | 0.24008 | 0 | 0 | 0 | 788.1852 | 1032.3885 | 921.5185 | 0.20732 | 0.29932 | 0.24008 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | GRO | GROCERY | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 1.0397 | 0 | 1.1059 | Cap-Tons/1000 sf | 814.15 | 1089.7833 | 951.15 | 0.15118 | 0.22185 | 0.17505 | 0 | 0 | 0 | 814.15 | 1089.7833 | 951.15 | 0.15118 | 0.22185 | 0.17505 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.77621 | 0 | 0.88169 | Cap-Tons/1000 sf | 1190.4167 | 1563.9167 | 1390.4167 | 0.14936 | 0.21869 | 0.17859 | 0 | 0 | 0 | 1190.4167 | 1563.9167 | 1390.4167 | 0.14936 | 0.21869 | 0.17859 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HTL | LODGING - HOTEL | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.46549 | 0 | 0.49511 | Cap-Tons/1000 sf | 1415.9667 | 1807.9 | 1618.6333 | 0.22066 | 0.30333 | 0.2525 | 0 | 0 | 0 | 1415.9667 | 1807.9 | 1618.6333 | 0.22066 | 0.30333 | 0.2525 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | MTL | LODGING - MOTEL | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.46549 | 0 | 0.49511 | Cap-Tons/1000 sf | 1415.9667 | 1807.9 | 1618.6333 | 0.22066 | 0.30333 | 0.2525 | 0 | 0 | 0 | 1415.9667 | 1807.9 | 1618.6333 | 0.22066 | 0.30333 | 0.2525 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.82895 | 0 | 0.88169 | Cap-Tons/1000 sf | 1100.0667 | 1436.1667 | 1276.7333 | 0.13735 | 0.20109 | 0.16035 | 0 | 0 | 0 | 1100.0667 | 1436.1667 | 1276.7333 | 0.13735 | 0.20109 | 0.16035 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFL | OFFICE - LARGE | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.61708 | 0 | 0.65634 | Cap-Tons/1000 sf | 1236.8033 | 1435.5599 | 1344.5366 | 0.34757 | 0.43824 | 0.38577 | 0 | 0 | 0 | 1236.8033 | 1435.5599 | 1344.5366 | 0.34757 | 0.43824 | 0.38577 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFS | OFFICE - SMALL | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.65556 | 0 | 0.74464 | Cap-Tons/1000 sf | 885.5513 | 1086.1179 | 990.3513 | 0.28135 | 0.37535 | 0.32319 | 0 | 0 | 0 | 885.5513 | 1086.1179 | 990.3513 | 0.28135 | 0.37535 | 0.32319 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 1.143 | 0 | 1.2984 | Cap-Tons/1000 sf | 1230 | 1593.6667 | 1409.6667 | 0.30688 | 0.40201 | 0.35498 | 0 | 0 | 0 | 1230 | 1593.6667 | 1409.6667 | 0.30688 | 0.40201 | 0.35498 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.77022 | 0 | 0.87488 | Cap-Tons/1000 sf | 1228.9776 | 1545.3109 | 1366.6442 | 0.42567 | 0.5356 | 0.4754 | 0 | 0 | 0 | 1228.9776 | 1545.3109 | 1366.6442 | 0.42567 | 0.5356 | 0.4754 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.37551 | 0 | 0.3994 | Cap-Tons/1000 sf | 1132.6081 | 1382.2148 | 1262.9415 | 0.24565 | 0.32698 | 0.27385 | 0 | 0 | 0 | 1132.6081 | 1382.2148 | 1262.9415 | 0.24565 | 0.32698 | 0.27385 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.40936 | 0 | 0.46499 | Cap-Tons/1000 sf | 1132.0311 | 1433.8978 | 1289.0311 | 0.28643 | 0.37879 | 0.33626 | 0 | 0 | 0 | 1132.0311 | 1433.8978 | 1289.0311 | 0.28643 | 0.37879 | 0.33626 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTS | RETAIL - SMALL | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.45321 | 0 | 0.51479 | Cap-Tons/1000 sf | 1134 | 1509 | 1282 | 0.41731 | 0.55531 | 0.46686 | 0 | 0 | 0 | 1134 | 1509 | 1282 | 0.41731 | 0.55531 | 0.46686 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | SCN | STORAGE - CONDITIONED | New | CZ15 | Blythe Area (CZ15) |  |  |  | 1000 sf | 0.24791 | 0 | 0.2816 | Cap-Tons/1000 sf | 757.5 | 1051.5 | 871.5 | 0.2963 | 0.4113 | 0.337 | 0 | 0 | 0 | 757.5 | 1051.5 | 871.5 | 0.2963 | 0.4113 | 0.337 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ASM | ASSEMBLY | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.93897 | 0 | 1.0666 | Cap-Tons/1000 sf | 966.8 | 1394.6667 | 1064.1 | 0.58862 | 0.83889 | 0.63259 | 0 | 0 | 0 | 966.8 | 1394.6667 | 1064.1 | 0.58862 | 0.83889 | 0.63259 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.54701 | 0 | 0.62134 | Cap-Tons/1000 sf | 630.3879 | 1007.3131 | 724.1545 | 0.3424 | 0.54485 | 0.38836 | 0 | 0 | 0 | 630.3879 | 1007.3131 | 724.1545 | 0.3424 | 0.54485 | 0.38836 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.621 | 0 | 0.70538 | Cap-Tons/1000 sf | 557.54 | 799.2333 | 617.2733 | 0.13032 | 0.18622 | 0.14075 | 0 | 0 | 0 | 557.54 | 799.2333 | 617.2733 | 0.13032 | 0.18622 | 0.14075 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.79463 | 0 | 0.84519 | Cap-Tons/1000 sf | 765.1667 | 1180.1667 | 857.6 | 0.32186 | 0.4925 | 0.34896 | 0 | 0 | 0 | 765.1667 | 1180.1667 | 857.6 | 0.32186 | 0.4925 | 0.34896 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.61214 | 0 | 0.69532 | Cap-Tons/1000 sf | 676.2567 | 941.3167 | 739.2233 | 0.12868 | 0.1784 | 0.13763 | 0 | 0 | 0 | 676.2567 | 941.3167 | 739.2233 | 0.12868 | 0.1784 | 0.13763 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EUN | EDUCATION - UNIVERSITY | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.58484 | 0 | 0.62204 | Cap-Tons/1000 sf | 624.7665 | 1032.3885 | 726.0998 | 0.31086 | 0.51334 | 0.35839 | 0 | 0 | 0 | 624.7665 | 1032.3885 | 726.0998 | 0.31086 | 0.51334 | 0.35839 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | GRO | GROCERY | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 1.0397 | 0 | 1.1059 | Cap-Tons/1000 sf | 740.67 | 1089.7833 | 856.67 | 0.36215 | 0.53207 | 0.39078 | 0 | 0 | 0 | 740.67 | 1089.7833 | 856.67 | 0.36215 | 0.53207 | 0.39078 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.77621 | 0 | 0.88169 | Cap-Tons/1000 sf | 938.35 | 1563.9167 | 1094.75 | 0.26019 | 0.43365 | 0.29579 | 0 | 0 | 0 | 938.35 | 1563.9167 | 1094.75 | 0.26019 | 0.43365 | 0.29579 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HTL | LODGING - HOTEL | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.46549 | 0 | 0.49511 | Cap-Tons/1000 sf | 1163.54 | 1807.9 | 1316.84 | 0.42664 | 0.66048 | 0.47024 | 0 | 0 | 0 | 1163.54 | 1807.9 | 1316.84 | 0.42664 | 0.66048 | 0.47024 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | MTL | LODGING - MOTEL | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.46549 | 0 | 0.49511 | Cap-Tons/1000 sf | 1163.54 | 1807.9 | 1316.84 | 0.42664 | 0.66048 | 0.47024 | 0 | 0 | 0 | 1163.54 | 1807.9 | 1316.84 | 0.42664 | 0.66048 | 0.47024 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.82895 | 0 | 0.88169 | Cap-Tons/1000 sf | 914.7 | 1436.1667 | 1059.1667 | 0.27978 | 0.43588 | 0.31761 | 0 | 0 | 0 | 914.7 | 1436.1667 | 1059.1667 | 0.27978 | 0.43588 | 0.31761 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFL | OFFICE - LARGE | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.61708 | 0 | 0.65634 | Cap-Tons/1000 sf | 1001.8933 | 1435.5599 | 1080.2933 | 0.593 | 0.84967 | 0.63257 | 0 | 0 | 0 | 1001.8933 | 1435.5599 | 1080.2933 | 0.593 | 0.84967 | 0.63257 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFS | OFFICE - SMALL | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.65556 | 0 | 0.74464 | Cap-Tons/1000 sf | 697.1374 | 1086.1179 | 768.1374 | 0.48104 | 0.74936 | 0.52004 | 0 | 0 | 0 | 697.1374 | 1086.1179 | 768.1374 | 0.48104 | 0.74936 | 0.52004 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 1.143 | 0 | 1.2984 | Cap-Tons/1000 sf | 1086.3333 | 1593.6667 | 1219.3333 | 0.46458 | 0.67427 | 0.50985 | 0 | 0 | 0 | 1086.3333 | 1593.6667 | 1219.3333 | 0.46458 | 0.67427 | 0.50985 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.77022 | 0 | 0.87488 | Cap-Tons/1000 sf | 1103.9776 | 1545.3109 | 1205.8442 | 0.69122 | 0.96489 | 0.73672 | 0 | 0 | 0 | 1103.9776 | 1545.3109 | 1205.8442 | 0.69122 | 0.96489 | 0.73672 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.37551 | 0 | 0.3994 | Cap-Tons/1000 sf | 929.9955 | 1382.2148 | 1028.3622 | 0.51235 | 0.75302 | 0.56445 | 0 | 0 | 0 | 929.9955 | 1382.2148 | 1028.3622 | 0.51235 | 0.75302 | 0.56445 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.40936 | 0 | 0.46499 | Cap-Tons/1000 sf | 987.9387 | 1433.8978 | 1095.172 | 0.55655 | 0.7985 | 0.60795 | 0 | 0 | 0 | 987.9387 | 1433.8978 | 1095.172 | 0.55655 | 0.7985 | 0.60795 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTS | RETAIL - SMALL | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.45321 | 0 | 0.51479 | Cap-Tons/1000 sf | 917.9403 | 1353.6783 | 1015.007 | 0.56535 | 0.82661 | 0.61965 | 0 | 0 | 0 | 917.9403 | 1353.6783 | 1015.007 | 0.56535 | 0.82661 | 0.61965 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | SCN | STORAGE - CONDITIONED | Existing | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.24791 | 0 | 0.2816 | Cap-Tons/1000 sf | 653.91 | 912.5167 | 732.91 | 0.41064 | 0.56007 | 0.44994 | 0 | 0 | 0 | 653.91 | 912.5167 | 732.91 | 0.41064 | 0.56007 | 0.44994 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ASM | ASSEMBLY | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.93897 | 0 | 1.0666 | Cap-Tons/1000 sf | 1208.2667 | 1394.6667 | 1298.8667 | 0.34511 | 0.41378 | 0.37301 | 0 | 0 | 0 | 1208.2667 | 1394.6667 | 1298.8667 | 0.34511 | 0.41378 | 0.37301 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.54701 | 0 | 0.62134 | Cap-Tons/1000 sf | 825.0798 | 1007.3131 | 905.6131 | 0.2505 | 0.31536 | 0.2779 | 0 | 0 | 0 | 825.0798 | 1007.3131 | 905.6131 | 0.2505 | 0.31536 | 0.2779 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.621 | 0 | 0.70538 | Cap-Tons/1000 sf | 684 | 799.2333 | 733.9 | 0 | 0 | 0 | 0 | 0 | 0 | 684 | 799.2333 | 733.9 | 0 | 0 | 0 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.79463 | 0 | 0.84519 | Cap-Tons/1000 sf | 1021.9667 | 1180.1667 | 1089.0333 | 0.14446 | 0.17446 | 0.15539 | 0 | 0 | 0 | 1021.9667 | 1180.1667 | 1089.0333 | 0.14446 | 0.17446 | 0.15539 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.61214 | 0 | 0.69532 | Cap-Tons/1000 sf | 817.95 | 941.3167 | 870.95 | 0 | 0 | 0 | 0 | 0 | 0 | 817.95 | 941.3167 | 870.95 | 0 | 0 | 0 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EUN | EDUCATION - UNIVERSITY | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.58484 | 0 | 0.62204 | Cap-Tons/1000 sf | 832.3885 | 1032.3885 | 920.3219 | 0.23405 | 0.29998 | 0.26525 | 0 | 0 | 0 | 832.3885 | 1032.3885 | 920.3219 | 0.23405 | 0.29998 | 0.26525 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | GRO | GROCERY | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 1.0397 | 0 | 1.1059 | Cap-Tons/1000 sf | 831.7833 | 1089.7833 | 940.1167 | 0.20269 | 0.26529 | 0.23259 | 0 | 0 | 0 | 831.7833 | 1089.7833 | 940.1167 | 0.20269 | 0.26529 | 0.23259 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.77621 | 0 | 0.88169 | Cap-Tons/1000 sf | 1225.5833 | 1563.9167 | 1366.7833 | 0.16358 | 0.21725 | 0.18595 | 0 | 0 | 0 | 1225.5833 | 1563.9167 | 1366.7833 | 0.16358 | 0.21725 | 0.18595 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HTL | LODGING - HOTEL | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.46549 | 0 | 0.49511 | Cap-Tons/1000 sf | 1497.5667 | 1807.9 | 1634.7333 | 0.28938 | 0.35805 | 0.31828 | 0 | 0 | 0 | 1497.5667 | 1807.9 | 1634.7333 | 0.28938 | 0.35805 | 0.31828 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | MTL | LODGING - MOTEL | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.46549 | 0 | 0.49511 | Cap-Tons/1000 sf | 1497.5667 | 1807.9 | 1634.7333 | 0.28938 | 0.35805 | 0.31828 | 0 | 0 | 0 | 1497.5667 | 1807.9 | 1634.7333 | 0.28938 | 0.35805 | 0.31828 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.82895 | 0 | 0.88169 | Cap-Tons/1000 sf | 1133.5 | 1436.1667 | 1264 | 0.15561 | 0.20508 | 0.18014 | 0 | 0 | 0 | 1133.5 | 1436.1667 | 1264 | 0.15561 | 0.20508 | 0.18014 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFL | OFFICE - LARGE | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.61708 | 0 | 0.65634 | Cap-Tons/1000 sf | 1279.5599 | 1435.5599 | 1347.5933 | 0.6962 | 0.77944 | 0.73847 | 0 | 0 | 0 | 1279.5599 | 1435.5599 | 1347.5933 | 0.6962 | 0.77944 | 0.73847 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFS | OFFICE - SMALL | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.65556 | 0 | 0.74464 | Cap-Tons/1000 sf | 941.9179 | 1086.1179 | 1004.9846 | 0.41396 | 0.48829 | 0.45473 | 0 | 0 | 0 | 941.9179 | 1086.1179 | 1004.9846 | 0.41396 | 0.48829 | 0.45473 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 1.143 | 0 | 1.2984 | Cap-Tons/1000 sf | 1319 | 1593.6667 | 1443.6667 | 0.28746 | 0.35106 | 0.31489 | 0 | 0 | 0 | 1319 | 1593.6667 | 1443.6667 | 0.28746 | 0.35106 | 0.31489 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.77022 | 0 | 0.87488 | Cap-Tons/1000 sf | 1346.1109 | 1545.3109 | 1437.5109 | 0.36269 | 0.43269 | 0.38705 | 0 | 0 | 0 | 1346.1109 | 1545.3109 | 1437.5109 | 0.36269 | 0.43269 | 0.38705 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.37551 | 0 | 0.3994 | Cap-Tons/1000 sf | 1191.7815 | 1382.2148 | 1286.4481 | 0.31835 | 0.38329 | 0.35602 | 0 | 0 | 0 | 1191.7815 | 1382.2148 | 1286.4481 | 0.31835 | 0.38329 | 0.35602 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.40936 | 0 | 0.46499 | Cap-Tons/1000 sf | 1219.6978 | 1433.8978 | 1320.5978 | 0.33163 | 0.39896 | 0.36456 | 0 | 0 | 0 | 1219.6978 | 1433.8978 | 1320.5978 | 0.33163 | 0.39896 | 0.36456 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTS | RETAIL - SMALL | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.45321 | 0 | 0.51479 | Cap-Tons/1000 sf | 1165.545 | 1353.6783 | 1251.9117 | 0.37511 | 0.44711 | 0.40734 | 0 | 0 | 0 | 1165.545 | 1353.6783 | 1251.9117 | 0.37511 | 0.44711 | 0.40734 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SCE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | SCN | STORAGE - CONDITIONED | New | CZ16 | Mount Shasta Area (CZ16) |  |  |  | 1000 sf | 0.24791 | 0 | 0.2816 | Cap-Tons/1000 sf | 750.0167 | 912.5167 | 820.8833 | 0.22309 | 0.27549 | 0.24839 | 0 | 0 | 0 | 750.0167 | 912.5167 | 820.8833 | 0.22309 | 0.27549 | 0.24839 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ASM | ASSEMBLY | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.94349 | 0 | 1.0483 | Cap-Tons/1000 sf | 911.4667 | 1394.6667 | 1019.5667 | 0.46527 | 0.71083 | 0.5033 | 0 | 0 | 0 | 911.4667 | 1394.6667 | 1019.5667 | 0.46527 | 0.71083 | 0.5033 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.54668 | 0 | 0.60743 | Cap-Tons/1000 sf | 604.3879 | 1007.3131 | 696.4545 | 0.3484 | 0.58066 | 0.38916 | 0 | 0 | 0 | 604.3879 | 1007.3131 | 696.4545 | 0.3484 | 0.58066 | 0.38916 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.66214 | 0 | 0.73573 | Cap-Tons/1000 sf | 510.8733 | 799.2333 | 571.5067 | 0.46872 | 0.73381 | 0.50865 | 0 | 0 | 0 | 510.8733 | 799.2333 | 571.5067 | 0.46872 | 0.73381 | 0.50865 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.82639 | 0 | 0.86989 | Cap-Tons/1000 sf | 793.1667 | 1180.1667 | 868.7 | 0.55586 | 0.82653 | 0.59599 | 0 | 0 | 0 | 793.1667 | 1180.1667 | 868.7 | 0.55586 | 0.82653 | 0.59599 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.64424 | 0 | 0.71584 | Cap-Tons/1000 sf | 647.59 | 941.3167 | 708.3233 | 0.59477 | 0.86255 | 0.63387 | 0 | 0 | 0 | 647.59 | 941.3167 | 708.3233 | 0.59477 | 0.86255 | 0.63387 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EUN | EDUCATION - UNIVERSITY | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.58045 | 0 | 0.61101 | Cap-Tons/1000 sf | 619.4331 | 1032.3885 | 728.5998 | 0.31129 | 0.51882 | 0.35443 | 0 | 0 | 0 | 619.4331 | 1032.3885 | 728.5998 | 0.31129 | 0.51882 | 0.35443 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | GRO | GROCERY | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 1.0681 | 0 | 1.1243 | Cap-Tons/1000 sf | 731.3367 | 1089.7833 | 847.6033 | 0.32973 | 0.48922 | 0.36019 | 0 | 0 | 0 | 731.3367 | 1089.7833 | 847.6033 | 0.32973 | 0.48922 | 0.36019 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.78906 | 0 | 0.87675 | Cap-Tons/1000 sf | 938.35 | 1563.9167 | 1110.3167 | 0.21936 | 0.3656 | 0.2533 | 0 | 0 | 0 | 938.35 | 1563.9167 | 1110.3167 | 0.21936 | 0.3656 | 0.2533 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HTL | LODGING - HOTEL | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.46601 | 0 | 0.49055 | Cap-Tons/1000 sf | 1084.74 | 1807.9 | 1261.74 | 0.32084 | 0.53473 | 0.36331 | 0 | 0 | 0 | 1084.74 | 1807.9 | 1261.74 | 0.32084 | 0.53473 | 0.36331 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | MTL | LODGING - MOTEL | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.46601 | 0 | 0.49055 | Cap-Tons/1000 sf | 1084.74 | 1807.9 | 1261.74 | 0.32084 | 0.53473 | 0.36331 | 0 | 0 | 0 | 1084.74 | 1807.9 | 1261.74 | 0.32084 | 0.53473 | 0.36331 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.83291 | 0 | 0.87675 | Cap-Tons/1000 sf | 861.7 | 1436.1667 | 1013.6333 | 0.23953 | 0.39922 | 0.2714 | 0 | 0 | 0 | 861.7 | 1436.1667 | 1013.6333 | 0.23953 | 0.39922 | 0.2714 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFL | OFFICE - LARGE | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.60844 | 0 | 0.64047 | Cap-Tons/1000 sf | 943.5599 | 1435.5599 | 1028.6266 | 0.52807 | 0.80007 | 0.5672 | 0 | 0 | 0 | 943.5599 | 1435.5599 | 1028.6266 | 0.52807 | 0.80007 | 0.5672 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFS | OFFICE - SMALL | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.69988 | 0 | 0.77766 | Cap-Tons/1000 sf | 651.6708 | 1086.1179 | 728.7374 | 0.39841 | 0.66402 | 0.43601 | 0 | 0 | 0 | 651.6708 | 1086.1179 | 728.7374 | 0.39841 | 0.66402 | 0.43601 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 1.2308 | 0 | 1.3676 | Cap-Tons/1000 sf | 1023.6667 | 1593.6667 | 1162.3 | 0.38936 | 0.60453 | 0.42686 | 0 | 0 | 0 | 1023.6667 | 1593.6667 | 1162.3 | 0.38936 | 0.60453 | 0.42686 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.81237 | 0 | 0.90265 | Cap-Tons/1000 sf | 1007.3109 | 1545.3109 | 1119.9109 | 0.56659 | 0.86925 | 0.60812 | 0 | 0 | 0 | 1007.3109 | 1545.3109 | 1119.9109 | 0.56659 | 0.86925 | 0.60812 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.37152 | 0 | 0.39108 | Cap-Tons/1000 sf | 829.3289 | 1382.2148 | 947.6622 | 0.39861 | 0.66434 | 0.44091 | 0 | 0 | 0 | 829.3289 | 1382.2148 | 947.6622 | 0.39861 | 0.66434 | 0.44091 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.42671 | 0 | 0.47413 | Cap-Tons/1000 sf | 882.6053 | 1433.8978 | 1007.3053 | 0.40612 | 0.66001 | 0.44732 | 0 | 0 | 0 | 882.6053 | 1433.8978 | 1007.3053 | 0.40612 | 0.66001 | 0.44732 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTS | RETAIL - SMALL | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.46376 | 0 | 0.5153 | Cap-Tons/1000 sf | 824.607 | 1353.6783 | 935.4403 | 0.41885 | 0.68756 | 0.46342 | 0 | 0 | 0 | 824.607 | 1353.6783 | 935.4403 | 0.41885 | 0.68756 | 0.46342 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | SCN | STORAGE - CONDITIONED | Existing | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.25401 | 0 | 0.28224 | Cap-Tons/1000 sf | 643.91 | 912.5167 | 719.5433 | 0.43832 | 0.60945 | 0.47189 | 0 | 0 | 0 | 643.91 | 912.5167 | 719.5433 | 0.43832 | 0.60945 | 0.47189 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ASM | ASSEMBLY | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.94349 | 0 | 1.0483 | Cap-Tons/1000 sf | 1182 | 1394.6667 | 1286.5667 | 0.43248 | 0.50888 | 0.46944 | 0 | 0 | 0 | 1182 | 1394.6667 | 1286.5667 | 0.43248 | 0.50888 | 0.46944 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.54668 | 0 | 0.60743 | Cap-Tons/1000 sf | 828.7465 | 1007.3131 | 916.0131 | 0.34989 | 0.42519 | 0.38902 | 0 | 0 | 0 | 828.7465 | 1007.3131 | 916.0131 | 0.34989 | 0.42519 | 0.38902 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.66214 | 0 | 0.73573 | Cap-Tons/1000 sf | 684.8 | 799.2333 | 740.5333 | 0.45036 | 0.52499 | 0.48713 | 0 | 0 | 0 | 684.8 | 799.2333 | 740.5333 | 0.45036 | 0.52499 | 0.48713 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.82639 | 0 | 0.86989 | Cap-Tons/1000 sf | 1059.8333 | 1180.1667 | 1113.3667 | 0.61283 | 0.68536 | 0.64903 | 0 | 0 | 0 | 1059.8333 | 1180.1667 | 1113.3667 | 0.61283 | 0.68536 | 0.64903 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.64424 | 0 | 0.71584 | Cap-Tons/1000 sf | 822.7833 | 941.3167 | 881.25 | 0.58053 | 0.66193 | 0.61983 | 0 | 0 | 0 | 822.7833 | 941.3167 | 881.25 | 0.58053 | 0.66193 | 0.61983 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EUN | EDUCATION - UNIVERSITY | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.58045 | 0 | 0.61101 | Cap-Tons/1000 sf | 814.0552 | 1032.3885 | 914.7219 | 0.32139 | 0.40502 | 0.36372 | 0 | 0 | 0 | 814.0552 | 1032.3885 | 914.7219 | 0.32139 | 0.40502 | 0.36372 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | GRO | GROCERY | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 1.0681 | 0 | 1.1243 | Cap-Tons/1000 sf | 841.7833 | 1089.7833 | 950.75 | 0.1761 | 0.2329 | 0.1991 | 0 | 0 | 0 | 841.7833 | 1089.7833 | 950.75 | 0.1761 | 0.2329 | 0.1991 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.78906 | 0 | 0.87675 | Cap-Tons/1000 sf | 1193.5833 | 1563.9167 | 1358.1833 | 0.14487 | 0.20027 | 0.1673 | 0 | 0 | 0 | 1193.5833 | 1563.9167 | 1358.1833 | 0.14487 | 0.20027 | 0.1673 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HTL | LODGING - HOTEL | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.46601 | 0 | 0.49055 | Cap-Tons/1000 sf | 1453.5667 | 1807.9 | 1608.5667 | 0.26535 | 0.33592 | 0.30349 | 0 | 0 | 0 | 1453.5667 | 1807.9 | 1608.5667 | 0.26535 | 0.33592 | 0.30349 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | MTL | LODGING - MOTEL | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.46601 | 0 | 0.49055 | Cap-Tons/1000 sf | 1453.5667 | 1807.9 | 1608.5667 | 0.26535 | 0.33592 | 0.30349 | 0 | 0 | 0 | 1453.5667 | 1807.9 | 1608.5667 | 0.26535 | 0.33592 | 0.30349 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | NRS | HEALTH/MEDICAL - NURSING HOME | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.83291 | 0 | 0.87675 | Cap-Tons/1000 sf | 1124.5 | 1436.1667 | 1254.7667 | 0.14417 | 0.19424 | 0.16274 | 0 | 0 | 0 | 1124.5 | 1436.1667 | 1254.7667 | 0.14417 | 0.19424 | 0.16274 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFL | OFFICE - LARGE | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.60844 | 0 | 0.64047 | Cap-Tons/1000 sf | 1259.1599 | 1435.5599 | 1339.9933 | 0.54996 | 0.62806 | 0.59166 | 0 | 0 | 0 | 1259.1599 | 1435.5599 | 1339.9933 | 0.54996 | 0.62806 | 0.59166 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | OFS | OFFICE - SMALL | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.69988 | 0 | 0.77766 | Cap-Tons/1000 sf | 920.1846 | 1086.1179 | 994.7513 | 0.46345 | 0.54448 | 0.50542 | 0 | 0 | 0 | 920.1846 | 1086.1179 | 994.7513 | 0.46345 | 0.54448 | 0.50542 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RFF | RESTAURANT - FAST-FOOD | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 1.2308 | 0 | 1.3676 | Cap-Tons/1000 sf | 1306.3333 | 1593.6667 | 1438.6667 | 0.3382 | 0.41337 | 0.3749 | 0 | 0 | 0 | 1306.3333 | 1593.6667 | 1438.6667 | 0.3382 | 0.41337 | 0.3749 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RSD | RESTAURANT - SIT-DOWN | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.81237 | 0 | 0.90265 | Cap-Tons/1000 sf | 1330.5442 | 1545.3109 | 1442.2109 | 0.67633 | 0.76803 | 0.71783 | 0 | 0 | 0 | 1330.5442 | 1545.3109 | 1442.2109 | 0.67633 | 0.76803 | 0.71783 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RT3 | RETAIL - MULTISTORY LARGE | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.37152 | 0 | 0.39108 | Cap-Tons/1000 sf | 1158.6148 | 1382.2148 | 1273.4148 | 0.49057 | 0.57463 | 0.5325 | 0 | 0 | 0 | 1158.6148 | 1382.2148 | 1273.4148 | 0.49057 | 0.57463 | 0.5325 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTL | RETAIL - SINGLE-STORY LARGE | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.42671 | 0 | 0.47413 | Cap-Tons/1000 sf | 1191.8978 | 1433.8978 | 1313.1311 | 0.40913 | 0.49033 | 0.4499 | 0 | 0 | 0 | 1191.8978 | 1433.8978 | 1313.1311 | 0.40913 | 0.49033 | 0.4499 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | RTS | RETAIL - SMALL | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.46376 | 0 | 0.5153 | Cap-Tons/1000 sf | 1145.845 | 1353.6783 | 1245.4783 | 0.44632 | 0.52869 | 0.49012 | 0 | 0 | 0 | 1145.845 | 1353.6783 | 1245.4783 | 0.44632 | 0.52869 | 0.49012 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | SCN | STORAGE - CONDITIONED | New | CZ06 | Los Angeles Area (CZ06) |  |  |  | 1000 sf | 0.25401 | 0 | 0.28224 | Cap-Tons/1000 sf | 753.7167 | 912.5167 | 827.8833 | 0.2335 | 0.28822 | 0.26533 | 0 | 0 | 0 | 753.7167 | 912.5167 | 827.8833 | 0.2335 | 0.28822 | 0.26533 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ASM | ASSEMBLY | Existing | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.94349 | 0 | 1.0483 | Cap-Tons/1000 sf | 933 | 1394.6667 | 1043.0333 | 0.53739 | 0.80372 | 0.57655 | 0 | 0 | 0 | 933 | 1394.6667 | 1043.0333 | 0.53739 | 0.80372 | 0.57655 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ECC | EDUCATION - COMMUNITY COLLEGE | Existing | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.54668 | 0 | 0.60743 | Cap-Tons/1000 sf | 604.3879 | 1007.3131 | 700.4879 | 0.34875 | 0.58125 | 0.39188 | 0 | 0 | 0 | 604.3879 | 1007.3131 | 700.4879 | 0.34875 | 0.58125 | 0.39188 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EPR | EDUCATION - PRIMARY SCHOOL | Existing | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.66214 | 0 | 0.73573 | Cap-Tons/1000 sf | 518.2067 | 799.2333 | 576.4733 | 0.45827 | 0.7083 | 0.49684 | 0 | 0 | 0 | 518.2067 | 799.2333 | 576.4733 | 0.45827 | 0.7083 | 0.49684 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ERC | EDUCATION - RELOCATABLE CLASSROOM | Existing | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.82639 | 0 | 0.86989 | Cap-Tons/1000 sf | 854.5 | 1180.1667 | 917.9 | 0.66198 | 0.91465 | 0.70085 | 0 | 0 | 0 | 854.5 | 1180.1667 | 917.9 | 0.66198 | 0.91465 | 0.70085 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | ESE | EDUCATION - SECONDARY SCHOOL | Existing | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.64424 | 0 | 0.71584 | Cap-Tons/1000 sf | 640.2567 | 941.3167 | 701.5233 | 0.58414 | 0.8596 | 0.62478 | 0 | 0 | 0 | 640.2567 | 941.3167 | 701.5233 | 0.58414 | 0.8596 | 0.62478 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | EUN | EDUCATION - UNIVERSITY | Existing | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.58045 | 0 | 0.61101 | Cap-Tons/1000 sf | 619.4331 | 1032.3885 | 732.6665 | 0.30907 | 0.51512 | 0.35487 | 0 | 0 | 0 | 619.4331 | 1032.3885 | 732.6665 | 0.30907 | 0.51512 | 0.35487 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | GRO | GROCERY | Existing | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 1.0681 | 0 | 1.1243 | Cap-Tons/1000 sf | 740.67 | 1089.7833 | 855.7033 | 0.3136 | 0.4602 | 0.34227 | 0 | 0 | 0 | 740.67 | 1089.7833 | 855.7033 | 0.3136 | 0.4602 | 0.34227 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HSP | HEALTH/MEDICAL - HOSPITAL | Existing | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.78906 | 0 | 0.87675 | Cap-Tons/1000 sf | 938.35 | 1563.9167 | 1113.35 | 0.21166 | 0.35277 | 0.24603 | 0 | 0 | 0 | 938.35 | 1563.9167 | 1113.35 | 0.21166 | 0.35277 | 0.24603 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None
M-050 | HVAC - SEER Rated Split System AC (SEER 15) | SDGE | COM | Electric | COMHVAC - SEER Rated Split System AC (SEER 15) | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo; Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo; Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | HVAC | SpaceCool | dxAC_equip | spltSEER | spltSEER15 | 1 | 0 | 1 | 0.8 |  | NA | 1 | Split AC | Cap-Tons | HTL | LODGING - HOTEL | Existing | CZ07 | San Diego Area (CZ07) |  |  |  | 1000 sf | 0.46601 | 0 | 0.49055 | Cap-Tons/1000 sf | 1084.74 | 1807.9 | 1267.74 | 0.3039 | 0.5065 | 0.34723 | 0 | 0 | 0 | 1084.74 | 1807.9 | 1267.74 | 0.3039 | 0.5065 | 0.34723 | 0 | 0 | 0 | 74 | 15 | 15 | 15 | 5 | 0.5 | 951.5212 | 676.9804 | 870.3932 | 770.0936 | 572.7969 | 770.0936 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | [7 empty] | Medium (2013) | Medium (2013) | Medium (2013) | None