2009 Resource Adequacy Report

Produced by

The Staff of the

California Public Utilities Commission

January 10, 2011

Donald Brooks

Kevin Dudney

Jaime Gannon

Lana Tran

Michael DeMesa

2009 Resource Adequacy Report

# Table of Contents

Table of Contents	1

Index of Tables	2

Index of Figures	2

1	Executive Summary	4

2	2009 Load Forecast and Resource Adequacy Program Requirements	5

2.1	Yearly and Monthly Load Forecast Process	5

2.1.1	Yearly Load Forecast Process in 2009	6

2.1.2	Monthly Load Migration Adjustments in 2009	8

2.2	2009 System RA Requirements - CPUC Jurisdictional LSEs	10

2.3	Local RA Program	11

2.3.1	Local RA Procurement in 2009	11

2.4	Maximum Cumulative Capacity (MCC) and RA	12

2.5	MCC Buckets and Demand Response	13

2.6	Total RA Resources Available to the CAISO in 2009	16

3	Counting RA Resources	17

3.1	Establishment of CAISO’S NQC Values for 2009	18

3.2	Aggregate NQC Values 2006 through 2011	18

3.3	Import Allocations for 2009	19

4	Reliability Must Run Designations in 2009	20

5	Compliance with RAR in 2009	21

5.1	Overview of the RA Filing Process	22

5.2	Compliance Review Process	22

5.3	Enforcement and Compliance	23

5.3.1	Enactment and Implementation of E-4195	23

5.3.2	Enforcement actions taken 2006-2009 compliance years	23

5.3.3	Load Forecast Compliance	24

6	Generator Performance and Availability	25

6.1	Reliability Performance Metrics	26

6.2	Annual Average NERC GADS Performance by Technology	27

6.2.1	Combined Cycle Plants	27

6.2.2	Combustion Turbine (Peakers)	28

6.2.3	Conventional Steam Plants	29

7	Changes to the RA Program for 2010	30

7.1	Exceedance Methodology for NQC of Wind and Solar	31

7.1.1	Impacts of rule change:	31

7.1.2	Changes in wind and solar QC process from 2009 to 2010:	31

8	Appendix 1 - Total CAISO LSE Procurement as Percentage of Total Obligation	32

# Index of Tables

Table 1. 2009 Aggregated Load Forecast Data (MW)	7

Table 2 CEC Plausibility adjustments 2008-2010 (MW)	8

Table 3. Summary of Load Forecast Adjustments in 2009 (in MW)	9

Table 4. 2009 RA Filing Summary - CPUC Jurisdictional Entities (MWs)	11

Table 5. Local RA procurement in 2009	12

Table 6. Use Limited RA Capacity reported as percentage of MCC cap - summer 2009	13

Table 7. List of DR programs and their program specifications	15

Table 8.  NQC for 2006-2010	19

Table 9.  2009 Import Allocations process (MW)	19

Table 10.  2009 Import Allocations and Usage (MW)	20

Table 11. RMR designations and RMR allocations for 2008-2010	21

Table 12. Enforcement Summary Pursuant to the RA program since 2006	24

Table 13. Total CAISO LSE Procurement as Percentage of Total CAISO Obligation	32

# Index of Figures

Figure 1. Monthly Net Migration Adjustments from 2006-2009	10

Figure 2 Ability of Bucket 1 to include DR Resources	14

Figure 3. Total CAISO Summer 2009 Forward Procurement Obligation and Forward Procurement vs. LSE Demand Forecast and Actual Monthly Peak Demand (MW)	17

Figure 4. Five-Year Weighted Average NERC GADS Performance	27

Figure 5. Combined Cycle Gas Turbine EFORD	28

Figure 6. Combined Cycle Gas Turbine NCF	28

Figure 7. Combustion Turbine Units’ EFORd	29

Figure 8. Combustion Turbine NCF	29

Figure 9. Steam Turbine EFORd	30

Figure 10. Steam Turbine NCF	30

Table of Acronyms

| AS | Ancillary Services |
| --- | --- |
| CAISO | California Independent System Operator |
| CAM | Cost-Allocation Methodology |
| CCGT | Combined Cycle Gas Turbine |
| CEC | California Energy Commission |
| DA | Direct Access |
| DASR | Direct Access Service Request |
| DG | Distributed Generation |
| DR | Demand Response |
| DSM | Demand Side Management |
| EAF | Equivalent Availability Factor |
| ED | Energy Division |
| EFORd | Equivalent Forced Outage Rate of demand |
| ELCC | Effective Load Carrying Capacity |
| ERRA | Energy Resource Recovery Account |
| ESP | Electricity Service Provider |
| ETC | Existing Transmission Contract |
| FERC | Federal Energy Regulatory Commission |
| FOH | Forced Outage Hours |
| HE | Hour Ending |
| ICPM | Interim Capacity Procurement Mechanism |
| IOU | Investor Owned Utility |
| LD | Liquidated Damages |
| LI | Load Impact |
| LOLP | Loss of Load Probability |
| LSE | Load Serving Entity |
| MCC | Maximum Cumulative Capacity |
| MOO | Must Offer Obligation |
| MW | Megawatt |
| NCF | Net Capacity Factor |
| NDC | Net Dependable Capacity |
| NERC | North American Reliability Corporation |
| NQC | Net Qualifying Capacity |
| PRM | Planning Reserve Margin |
| QC | Qualifying Capacity |
| QF | Qualifying Facility |
| RA | Resource Adequacy |
| RAR | Resource Adequacy Requirement |
| RMR | Reliability Must Run |
| RPS | Renewable Portfolio Standard |
| SCP | Standard Capacity Product |
| SFTP | Secure File Transfer Protocol |
| TAC | Transmission Access Charge |
| TCPM | Transitional Capacity Procurement Mechanism |
| TIC | Total Installed Capacity |
| ULR | Use Limited Resources |

# Executive Summary

The intent of the Resource Adequacy (RA) program is to ensure that sufficient capacity is available to meet the peak load and reserve requirements of California Public Utilities Commission (CPUC) jurisdictional Load Serving Entities (LSEs).  This Report provides a review of the CPUC’s RA program, summarizing RA program experience during the 2009 RA compliance year.  While this report does not make explicit policy recommendations, it is intended to provide factual information relevant to the currently open RA rulemaking (R.09-10-032) and ongoing implementation of the RA program in California.

Each year, the RA program requires LSEs to submit two rounds of Year-Ahead filings due in September and October and twelve Month-Ahead filings due monthly during the compliance year.  In 2009, the RA program worked as intended; actual peak load for 2009 occurred in September, when capacity resources procured by all LSEs (CPUC jurisdictional and non-CPUC jurisdictional) totaled 54,313 MW of resources to meet 45,994 MW of actual California Independent System Operator (CAISO) peak load.  System RA resources, including Demand Response resources, across the CAISO ranged between 47,996 MW (May) to 59,224 MW of resources (August), or between 102 percent and 106 percent of CAISO total procurement obligations.

In 2009 and again in 2010 the reliability of LSE load forecasts improved.  This was demonstrated by a significant reduction in the number of California Energy Commission (CEC) plausibility adjustments required.  The overall pattern of aggregate monthly LSE migration adjustments also continued from compliance year 2008 through the 2009 compliance year.  In 2009, there was a net increase in total monthly RA requirements as a result of LSE forecast adjustments, but the aggregate adjustments were significantly lower and concentrated in different months than before 2008.

CPUC jurisdictional LSEs provided 54,587 megawatts (MW) of RA capacity to the CAISO during the forecasted peak month of August 2009.  During 2009, no load reduction, staged emergencies, flex alerts, or other significant reliability problems occurred within the CAISO due to unavailability of adequate generating resources.  Local RA obligations were also fulfilled during 2009 compliance year.  During each month of 2009 CPUC jurisdictional LSEs provided at least 25,272 MW of RA capacity from physical resources in specific local areas.  In addition, Local RA obligations are decreasing as a result of transmission improvements.  Overall Local RA obligations decreased by 191 MW from 2008 to 2009.

Demand Response (DR) resources are accounted for in the RA program differently than traditional thermal generating resources.  If DR programs were to fit within the MCC buckets, there would need to be some standardization of DR programs and changes to DR programs in order to make them fit within the MCC buckets.

Although several mechanics of unit commitment changed with the CAISO’s implementation of Market Redesign and Technology Update (MRTU), the trend noted in the 2007 and 2008 Resource Adequacy Reports of reduced use of backstop procurement by CAISO via Reliability Must-Run (RMR) continued during 2009.

The essence of the RA program is mandatory LSE acquisition of capacity to meet load and reserve requirements.  Non-compliance occurs if either an LSE files with a procurement deficiency (i.e., it did not meet its RA obligations) or does not file at all, files late, or not in the manner required.  In total the Commission has issued 15 citations for violations related to compliance years 2006 through 2009 and has collected $47,500 in payments from LSEs arising from these citations.  There have also been a total of three enforcement cases brought by the Commission during that time.

Since the RA Program requires LSEs to demonstrate procurement of valid RA capacity, the RA Program is reliant on generation procured to be available and online when the CAISO needs to commit it.  In California, 45 conventional steam units, 55 combined cycle, and 71 combustion turbine peaker units submit performance data to the GADS.

# 2009 Load Forecast and Resource Adequacy Program Requirements

Each year, the RA program requires LSEs to submit a series of filings including load forecasts and compliance showings.  Generally, there are two rounds of Year-Ahead filings due in September and October and twelve Month-Ahead filings due monthly during the compliance year.  Each compliance filing is preceded by a load forecast for the same period.

In 2009, the RA program worked as intended, providing LSEs with timely information on RA Requirements and an opportunity to make adjustments.  In 2009 and again in 2010 the reliability of LSE load forecasts improved, as demonstrated by a significant reduction in the number of CEC plausibility adjustments required.

## Yearly and Monthly Load Forecast Process

The RA program relies on load forecasts supplied and checked by the CEC to establish each LSE’s RA Requirement.  The load forecast used in the RA program for system RA obligations is the most recent CEC “1 in 2” monthly load forecast that is available as of the time the Resource Adequacy Requirement (RAR) is established for the compliance year.

In order to establish the System RA Requirement, CEC staff reviewed load forecasts submitted by each LSE, reconciled those load forecasts against its own forecast for the entire IOU service territories, and generated an individual load forecast for each LSE for each month of 2009.  For the 2009 Year-Ahead System RA filings due in 2008, CPUC staff sent a spreadsheet containing Local RA obligations, final load forecasts, and allocations for DR, RMR, and Capacity Allocation Mechanism (CAM) resources to each LSE via password protected email on July 30, 2009.

The 2009 compliance year filing process was complicated by a number of factors.  There were delays in data gathering, delaying issuance of the 2009 System and Local RA allocations until July 30, 2008.  Final 2009 Templates and Guides were sent to LSEs on August 14, 2008.  Two LSEs successfully disputed CEC adjustments made to their year-Ahead forecasts, requiring the Energy Division to reallocate and resend Local RA information to LSEs on August 28, 2008.  Finally, there was a delay in the online date of a resource that required Energy Division to reallocate revised Local RA obligations in San Diego Local Area on October 5, along with the 2009 RMR allocations.  Subsequent to the change in Local RA information in San Diego Local Area, parties requested a delay in the 2009 RA Filing due date, from October 31 to mid-November to give LSEs sufficient time to complete their RA purchases.  Administrative Law Judge Wetzell issued a ruling on October 15 that reset the 2009 compliance date to November 21.

CPUC jurisdictional LSEs submitted their Year-Ahead compliance filings on November 21; Energy Division evaluated the Year-Ahead RA filings for compliance, and notified LSEs when their filings were approved.  One LSE applied for and was granted a waiver of penalties related to the 2009 year-Ahead System and Local RA obligations.

During the course of 2009 compliance year, LSEs submitted monthly load forecasts to the CEC to show any changes in load expected due to load migration.  The CEC checked the revised load forecasts to make sure they remained plausible and were within a tolerance level of the statewide forecast. Where the CEC did not dispute the Month-Ahead adjusted forecast, each LSE submitted its RA compliance filing using their adjusted forecast supplied to the CEC.

### Yearly Load Forecast Process in 2009

Each LSE’s Year-Ahead System RA obligation for 2009 was based on two levels of load forecasting produced by the LSEs and the CEC.  Decision (D.) 05-10-042 required LSEs to submit historical sales figures and a projected forecast for the following compliance year based on a reasonable assumption of load growth and customer retention.   This is referred to as the “Best Estimate” approach.  These forecasts were submitted to the CEC for evaluation; the CEC adjusted for transmission losses and load migration of customers returning to IOU service from direct access ESPs.  The CEC applied a trigger for a plausibility adjustment if the aggregate of LSE load forecasts in an IOU service area failed to match the CEC’s load forecast for that IOU service area.  As specified by D.05-10-042, adjustments were made to account for the impact of energy efficiency (EE), distributed generation (DG), and coincidence of peak load. The CPUC sent individual LSE forecasts to the LSEs on July 30, 2008.

Table 1 shows the aggregate LSE submissions for 2009 and the adjustments that were made across all three IOU service areas.  Because the historic and forecast data submitted by participating LSEs contain market sensitive information, results are discussed and presented in aggregate.  These adjustments include plausibility adjustments to account for customer retention, demand side management adjustments, and an adjustment to add load in aggregate to bring the total forecasts to within one percent of the CEC’s service area forecasts.  Finally, aggregate service area forecasts were adjusted for peak coincidence.  The process was the same as for 2008 compliance year, and an outline of the process was included in the 2008 RA report.

The forecast for CPUC jurisdictional LSEs showed an expected peak in August 2009 at 46,342 MW, which represents a 3.4% increase from the peak forecast of 44,734 MW in 2008.

Table 1. 2009 Aggregated Load Forecast Data (MW)

| SUMMARY TOTAL |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Peak Demand for Month of Calendar 2009 (MW) |  |  |  |  |  |  |  |  |  |  |  |
| Element | Service Area | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |
|  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 |
| Submitted LSE Forecast (Metered Load + T&D Losses + UFE) | Total | 29,981 | 29,037 | 28,804 | 30,170 | 35,937 | 40,344 | 43,980 | 46,897 | 41,896 | 35,165 | 30,245 | 32,007 |
| CEC Adjustment for Plausibility/ Migrating load | Total | 437 | 436 | 441 | 459 | 519 | 553 | 605 | (188) | 595 | 514 | 484 | 481 |
| EE/DG Adjustment | Total | 0 | 0 | 0 | - | (0) | 0 | 0 | 0 | (0) | (0) | (0) | (0) |
| Pro rata adjustment to match CEC forecast within 1% | Total | - | 1 | 16 | 106 | - | 36 | 216 | 99 | 341 | 7 | 191 | 134 |
| Noncoincident Peak Demand | Total | 30,418 | 29,474 | 29,261 | 30,735 | 36,455 | 40,933 | 44,801 | 46,808 | 42,832 | 35,687 | 30,920 | 32,622 |
| Coincidence Adjustment | Total | (427) | (533) | (928) | (395) | (391) | (594) | (691) | (466) | (593) | (1,112) | (780) | (574) |
| Final Load Forecast to Used for Compliance | Total | 29,991 | 28,941 | 28,334 | 30,339 | 36,065 | 40,339 | 44,110 | 46,342 | 42,239 | 34,575 | 30,140 | 32,048 |

Source: CEC Staff aggregate Load Forecast adjustment

As in previous compliance years, the CEC was required to adjust LSE Year-Ahead forecasts due to implausible LSE customer retention assumptions.  In contrast to previous years, however, the magnitude of total plausibility adjustments has decreased significantly.   illustrates the magnitude of plausibility adjustments in each month and compares 2008, 2009, and 2010 compliance years.  Nine of twelve ESPs and two of three IOUs serving load in 2009 did not require plausibility adjustments applied to the year-Ahead forecast in any month of either 2008 or 2009 compliance year.  Thus, plausibility adjustments were concentrated in a relatively small number of LSEs.  In 2010, plausibility adjustments were even more concentrated, and of a much smaller magnitude.  Only one of three IOUs and one of nine ESPs required plausibility adjustments in 2010.   The same IOU and ESP required adjustments to their 2010 forecasts as in 2008 and 2009.  The IOU required large downward adjustments in August of 2008, 2009, and 2010 compliance years.  The same IOU as well as the one ESP required upward plausibility adjustments in the remaining months over the same periods.

Plausibility adjustments, in terms of MW volume, declined in 2009 over previous years, meaning more certainty is being provided in the year-Ahead forecast process as the program matures.

Table 2 CEC Plausibility adjustments 2008-2010 (MW)

| Year | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 2008 Compliance Year | 470 | 627 | 562 | 655 | 705 | 702 | 716 | (173) | 713 | 649 | 568 | 472 |
| 2009 Compliance Year | 437 | 436 | 441 | 459 | 519 | 553 | 605 | (188) | 595 | 514 | 484 | 481 |
| 2010 Compliance Year | 50 | 48 | 19 | 65 | 21 | 22 | 225 | (44) | 352 | 155 | 17 | 15 |
| Percentage Decrease 2009-2010 | (89%) | (89%) | (96%) | (86%) | (96%) | (96%) | (63%) | (77%) | (41%) | (70%) | (96%) | (97%) |

Source: Aggregated year-Ahead CEC load forecasts 2008-2010

### Monthly Load Migration Adjustments in 2009

After the Year-Ahead forecast process, LSEs also adjust their load forecasts during the compliance year to account for load migration.  D.05-10-042 outlined a process whereby LSEs adjust their load forecasts on a monthly basis.  The CPUC directed the LSEs to submit revised forecasts two months prior to the filing month, as discussed in the RA Guide for 2009 compliance year.  These load forecast adjustments are solely for the purpose of accounting for load migration between LSEs, not changing demographic or electrical conditions.

The overall pattern of aggregate monthly LSE migration adjustments changed from 2007 compliance year to 2008, and that pattern continued through the 2009 compliance year.   In 2009, there was a net increase in total monthly RA requirements as a result of LSE forecast adjustments, but the aggregate adjustments were significantly lower and concentrated in different months than before 2008.  Load forecast adjustments increased RA requirements in all months of the 2009 compliance year by one percent, which was less than the approximately three percent aggregate increase each month in the 2007 compliance year.   shows monthly load forecast adjustments ranging between 283 and 425 MW in 2009.  This is a slight increase from the monthly load adjustment range of 203 to 336 MW during the peak months of 2008, but a significant decrease from the load adjustments in 2006 and 2007 compliance years.  Contrasting with previous years, 2009 data illustrated relatively stable load forecast adjustments each month, with the maximum and minimum monthly adjustments in 2009 only differing by 33% (from 283 to 425 MW) while adjustments in previous years varied by much greater amounts.

Table 3. Summary of Load Forecast Adjustments in 2009 (in MW)

|  | Description | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | Total Forecasts sent out in July, 2008 | 29,991 | 28,941 | 28,334 | 30,339 | 36,065 | 40,339 | 44,110 | 46,342 | 42,239 | 34,575 | 30,140 | 32,048 |
| 2 | Monthly Load Forecast adjustments through 2009 | 367 | 324 | 388 | 283 | 305 | 333 | 388 | 357 | 355 | 425 | 389 | 346 |
| 3 | Total forecasts used in 2009 monthly RA filings | 30,359 | 29,265 | 28,722 | 30,623 | 36,369 | 40,672 | 44,498 | 46,699 | 42,594 | 35,000 | 30,529 | 32,394 |
| 4 | Line 3 as percent of Line 1 | 101% | 101% | 101% | 101% | 101% | 101% | 101% | 101% | 101% | 101% | 101% | 101% |

Source – Aggregated Load Forecast Adjustments submitted to the CEC and CPUC through 2009

Figure 1 illustrates the trend in monthly net migration adjustments to LSE forecasts during compliance years 2006-2009.  Overall there has been a significant decrease in net load adjustments since 2006.  For example, net load migration adjustments in September 2009 were 61% lower than net load migration adjustments in September 2006.

Figure 1. Monthly Net Migration Adjustments from 2006-2009

Source: Monthly Forecast adjustments submitted by LSEs, 2006-2009

## 2009 System RA Requirements - CPUC Jurisdictional LSEs

The CPUC-jurisdictional LSEs satisfied their individual and collective system RAR for every month of 2009.  The total MWs of RA resources procured exceeded the total System RAR by between 7 percent and 29 percent, depending on the month.  RA resources include physical resources within CAISO, Demand Response, DWR contracts, and imports.  With the beginning of 2009 compliance year, Liquidated Damages (LD) contracts have been completely phased out and no longer count towards meeting CPUC jurisdictional RA obligations, although certain Publicly Owned Utilities (POUs) continue to apply LD contracts towards their RA obligations when filing with CAISO.

During the forecasted peak month of August 2009, CPUC jurisdictional LSEs were collectively required to procure 51,071 MW of resources to meet expected system needs plus a 15 percent reserve margin.  These LSEs procured 107 percent of the total System RAR, or 54,587 MW; which represents 3,517 MW in reserves beyond that required by the RA program.  Table 4 shows total CPUC jurisdictional RA procurement for each month of 2009. The LSEs’ individual forecasts are summed each month after being adjusted for load migration in column B, Demand Response resources are subtracted to create a Net Demand in Column D, a Planning Reserve Margin (PRM) is applied to create the RA obligation in Column E, and non-DR resources are compared to the resulting RA obligation and Net Demand in Columns G and H.  Compliance is represented by procurement over 100 percent of the RA obligation in column G, which is 115 percent of the peak demand forecasts.

Table 4. 2009 RA Filing Summary - CPUC Jurisdictional Entities (MWs)

| A | B | C | D | E | F | G | H |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 2009 | Demand Forecast1 | Demand Response2 | Net Demand | RAR3 | Total Resources Reported4 | Resources Reported as % of RAR | Resources Reported as % of Net Demand |
|  |  |  | D=B-C | E=D*1.15 |  | G=F/E | H=F/D |
| Jan | 30,359 | 1,004 | 29,204 | 33,758 | 37,554 | 111% | 129% |
| Feb | 29,265 | 1,003 | 28,262 | 32,501 | 36,224 | 111% | 128% |
| Mar | 28,722 | 1,030 | 27,692 | 31,846 | 35,702 | 112% | 129% |
| Apr | 30,623 | 1,045 | 29,578 | 34,014 | 34,476 | 101% | 117% |
| May | 36,369 | 1,446 | 34,923 | 40,162 | 44,224 | 110% | 127% |
| Jun | 40,672 | 2,261 | 38,411 | 44,173 | 48,979 | 111% | 128% |
| Jul | 44,498 | 2,276 | 42,223 | 48,556 | 52,365 | 108% | 124% |
| Aug | 46,699 | 2,290 | 44,410 | 51,071 | 54,587 | 107% | 123% |
| Sep | 42,594 | 2,287 | 40,306 | 46,352 | 50,262 | 108% | 125% |
| Oct | 35,000 | 1,455 | 33,546 | 38,578 | 39,380 | 102% | 117% |
| Nov | 30,529 | 1,018 | 29,511 | 33,938 | 36,406 | 107% | 123% |
| Dec | 32,394 | 1,005 | 31,390 | 36,098 | 38,927 | 108% | 124% |

Source: Aggregated LSE Monthly RA Filings

## Local RA Program

Beginning with the 2007 compliance year, the CPUC has required LSEs to demonstrate annually that they have acquired adequate generation capacity within defined, transmission-constrained areas.  There were no monthly Local RA filings in 2009 compliance year; although D.10-03-022 adopted a biannual Local RA true up process for 2010, and the possible addition of Local RA true-up filings are in the scope of the current RA proceeding R.09-10-032.  Other aspects of the Local RA program remained unchanged.

### Local RA Procurement in 2009

In D.08-06-031 the CPUC established Local RA obligations for 2009 compliance year and ordered LSEs to procure Local RA capacity in each of five Local Areas (Big Creek/Ventura, LA Basin, San Diego, Greater Bay Area, and Other PG&E Local).  These Local Areas are defined by the CPUC, significantly informed by the CAISO 2009 Local Capacity Technical Analysis.

CPUC jurisdictional LSEs’ overall Local RA procurement for 2009 is summarized in Table 5.  CPUC jurisdictional LSEs procured Local RA Resources sufficient to meet CPUC Local RA obligations in all five Local Areas of California in 2009, with aggregate procurement exceeding Local RAR by 12 percent for all Local Areas, and from zero to 27 percent in individual Local Areas.

Table 5. Local RA procurement in 2009

| Local Areas in 2009 – units in MW unless specified | Total LCR | CPUC jurisdictional Local RAR | Average Physical Resources Reported Each Month by Area | Local RMR/ DR/ CAM credit claimed | Average procurement as percent of Local RAR |
| --- | --- | --- | --- | --- | --- |
| LA Basin | 9,728 | 8,864 | 9,524 | 1,335 | 123% |
| Big Creek/Ventura | 3,178 | 2,895 | 3,506 | 176 | 127% |
| San Diego | 3,051 | 3,051 | 2,832 | 222 | 100% |
| Greater Bay Area | 4,791 | 4,457 | 4,025 | 743 | 107% |
| Other PG&E Areas | 6,198 | 5,768 | 5,734 | 370 | 106% |
| Totals | 26,946 | 25,035 | 25,621 | 2,847 | 114% |

Source: Aggregated 2009 Local RA filings

## Maximum Cumulative Capacity (MCC) and RA

During the development of the RA program in 2004 and 2005, parties were concerned that LSEs would meet their RA obligations with a large percentage of use limited resources (i.e., units that are either contractually or operationally limited) which was believed may cause the CAISO difficulties operating the system reliably.  To prevent this problem, the CPUC ordered LSEs in D. 04-10-035 to acquire a mix of resources that can be used to operate the grid at various load levels.  This approach recognized that many otherwise qualifying resources will not be available all hours of the month.  To ensure that LSEs did not over-rely on Use Limited Resources to meet load outside of peak, the CPUC created four resource categories, known as the Maximum Cumulative Capacity (MCC) buckets. Bucket 1 resources are available for just 30 to 60 hours each month during the five summer months, while Bucket 4 resources are available all hours of the month.  More information regarding the MCC buckets is available in the 2005 RA workshop report.

Table 6 illustrates that in 2009, LSEs provided capacity in each bucket well below the aggregate MCC restrictions, and are making available to the CAISO Bucket 4 resources predominantly.  This pattern is indicative of individual LSE filings in general as well.  CPUC jurisdictional LSEs contracted for RA resources that fall within Bucket 4 in excess of 87% of required capacity in all summer months of 2009.  LSE’s contracts with use limited capacity did not exceed RA program limitations, and thus use limited resources for RA did not create a reliability risk in the summer of 2009.

Table 6. Use Limited RA Capacity reported as percentage of MCC cap - summer 2009

| 2009 | Bucket1 | Bucket2 | Bucket3 | Bucket4 |
| --- | --- | --- | --- | --- |
| Max allowable Cumulative Capacity% | 13.30% | 18.20% | 30.10% | 100% |
| Minimum Hours in Month for Bucket | 30-60 May thru Sep | 160 | 384 | All |
| May | 0.88% | 4.98% | 4.68% | 92.09% |
| June | 0.78% | 4.60% | 7.16% | 91.18% |
| July | 0.67% | 4.98% | 7.04% | 88.86% |
| August | 0.63% | 4.82% | 7.69% | 87.74% |
| September | 0.60% | 4.81% | 6.70% | 89.78% |

Source: Aggregate LSE RA Filings for 2009 – percentage represents percent of total RA capacity reported by LSEs that fit into each bucket

## MCC Buckets and Demand Response

In efforts to more fully and accurately calculate the value of DR resources in the RA program, parties have discussed ways to categorize DR similarly to other RA resources.  This discussion implies that DR could fit into one or more MCC buckets.  DR resources are not currently categorized or required to fit into the current MCC buckets, although many DR resources are use-limited.  This means that if DR were included in the MCC Buckets, the amount of use limited resources that the CAISO must manage in order to operate the system may be higher than simply the sum of current Bucket 1 resources.  In order to get a better understanding of the extent to which DR can be compared to other generation, the following chart compares DR to Bucket 1 total capacity listed and the MCC restriction.  Energy Division anticipates that due to the hours of operation to which DR programs currently are restricted, DR would most likely only be able to fit into Bucket 1 (available for 40 to 60 hours each month, May thru September).  Some programs would need to extend their hours of availability to fit into Bucket 1

Figure 2 compares total capacity listed in Bucket 1 for August 2009 with the total Bucket 1 plus all DR resources in CAISO to demonstrate that there is room in Bucket 1 for DR resources if they were added.  Thus even with DR included in Bucket 1, there would be no over-reliance upon use limited resources.

Figure 2 Ability of Bucket 1 to include DR Resources

Source: Aggregate information from LSE RA filings filed with the CPUC

DR resources are accounted for in the RA program differently than traditional thermal generating resources.  If DR programs were to fit within the MCC buckets, there would need to be some standardization of DR programs and changes to DR programs in order to make them fit within the MCC buckets.  Table 7 summarizes the diversity of DR programs by IOU, and illustrates the difficulty in generalizing, especially with regards hours of availability.  It would be possible to create a MCC bucket for DR,  but that would likely require a bucket with less hours of availability than the current Bucket 1, and DR programs would likely need to be designed around rules that have not historically impacted DR programs, such as increased hours for each event, and more events per month or year.

Table 7. List of DR programs and their program specifications

| IOU | Program | Category | Program Months | Hours the Program is Available | Maximum Event Length | Day of week availability | Max Hrs per Month | Max Hrs/ year |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| PG&E | Agricultural and Pumping - Interruptible | Interruptible | Jan - Dec | All | 6 | All | 40 | 150 |
| PG&E | Base Interruptible Program | Interruptible | Jan - Dec | All | 6 | All | 60 | 120 |
| PG&E | Capacity Bidding Program | Price Response | May-Oct | 11am-7pm | 8 | Weekdays non-holiday | 24 | N/A |
| PG&E | Critical Peak Pricing | Price Response | June-Sept | 2pm-6pm | 4 | Weekdays non-holiday | N/A | 60 |
| PG&E | Demand Bidding Program | Price Response | Jan - Dec | 12pm-8pm | 8 | Weekdays non-holiday | N/A | N/A |
| PG&E | Summer Discount Plan - Base | Interruptible | June-Sept | All | 6 | All | N/A | 90 |
| PG&E | Summer Discount Plan - Enhanced | Interruptible | June-Sept | All | 6 | All | Unlimited | Unlimited |
| PG&E | Scheduled Load Reduction Program | Price Response | June-Sept | 8am-8pm | 4 | Weekdays non-holiday | N/A | N/A |
| PG&E | Peak Time Rebate | Price Response | Jan - Dec | 2pm-6pm | 4 | Weekdays non-holiday | N/A | 48 |
| PG&E | Critical Peak Pricing | Price Response | June-Sept | 2pm-6pm | 4 | Weekdays non-holiday | N/A | 60 |
| SCE | Base Interruptible Program | Interruptible | Jan - Dec | 24 hours/day | 4 | All | 10 events/month | 120 |
| SCE | Schedule Load Reduction Program | Interruptible | Jun - Sep | Customer enrolls : 8 am - Noon, Noon - 4 pm; 4 pm - 8 pm | 4 | Weekdays non-holiday | 3 times per day, 15 times per week | Unlimited |
| SCE | SmartAC | Interruptible | May - Oct | 24 hours/day | 6 | All | Unlimited | 100 |
| SCE | Aggregator Managed Portfolio | Price Response | May - Oct | 11 am - 7 pm | 6 | Weekdays non-holiday | Unlimited | 50 |
| SCE | Capacity Bidding Program | Price Response | May - Oct | 11 am - 7 pm | 3 products: 4, 6, or 8 hrs | Weekdays non-holiday | 24 | Unlimited |
| SCE | Demand Bidding Program | Price Response | Jan - Dec | Noon - 8 pm | 8 hrs; customers can bid less hours | Weekdays non-holiday | Unlimited | Unlimited |
| SCE | Dept Water Resources | Price Response | NA |  |  |  |  |  |
| SCE | Peak Choice | Price Response | May - Oct | Customers enroll: 1 pm - 7 pm or 24 hours/day | Customer enrollment 2-3 hours, 3-5 hours, 4-6 hours | 1 pm - 7 pm: Mon - Fri non- holiday 24 hours: all non-holiday | Unlimited | 75 |
| SCE | SmartRate (Residential) | Price Response | May - Oct | 2 pm - 7 pm | 5 hours | Weekdays non-holiday | Unlimited | 15 events/year |
| SDGE | Critical Peak Pricing - Default | Day Ahead Demand Response | Jan-Dec | 11am-6pm | 7 | All | Unlimited | 126 |
| SDGE | Capacity Bidding | Day Ahead & Day-Of Demand Response | May – Oct | 11am-7pm | customer choice of 4,6 or 8 hrs | Weekdays non-holiday | 24 | 144 |
| SDGE | Summer Saver | Day-Of Demand Response | May – Oct | 12:00pm - 8:00pm | 4 | weekdays only or weekdays and weekends | 40 | 120 |
| SDGE | Base Interruptible | Day Of Interruptible | Jan – Dec | all hours | 4 | All | 40 | 120 |
| SDGE | Aggregator Managed Program (DR contracts) | Day Of Demand Response | May - Oct | 12pm-6pm | 5 | Weekdays non-holiday | Unlimited | 50 |
| SDGE | Critical Peak Pricing - Emergency | Day Of Firm Load | Jan – Dec | all hours | 6 | All | 40 | 80 |

Source: IOU data request

## Total RA Resources Available to the CAISO in 2009

The CPUC has coordinated its RA program with the CAISO’s reliability requirements.  The CAISO also receives resource adequacy filings from non-CPUC jurisdictional LSEs.  Figure 3 compares the total LSE forecasts used for compliance across the CAISO against the CAISO Procurement obligation, total RA procured by LSEs within CAISO, and the actual CAISO peak load in the summer months of 2009.  In all months, the capacity available to CAISO exceeded the actual monthly peak load, and in only one month (September) did the actual peak load approach or exceed the Year-Ahead load forecast for that month.  Actual peak load for 2009 occurred in September, when capacity resources procured by all LSEs (CPUC jurisdictional and non-CPUC jurisdictional) totaled 54,313 MW of resources to meet 45,994 MW of actual CAISO peak load.  System RA resources, including Demand Response resources, across the CAISO ranged between 47,996 MW (May) to 59,224 MW of resources (August), or between 102 percent and 106 percent of CAISO total procurement obligations.

Figure 3. Total CAISO Summer 2009 Forward Procurement Obligation and Forward Procurement vs. LSE Demand Forecast and Actual Monthly Peak Demand (MW)

Source: Aggregated data compiled from CAISO MRTU Analysis and checked against Monthly CPUC and non-CPUC RA Filings

Table 13 (Appendix 1) illustrates total procurement for the summer of 2009 for all LSEs by contract type, and compares such procurement to the CAISO procurement obligation.  The data represented in Figure 3 derives from Table 13.  Significantly, 74 percent to 79 percent of all procured resources for summer 2009 were unit specific physical resources within the CAISO control area; 8 to 12 percent were imports, and about 1 percent were non-DWR Liquidated Damages contracts listed by the POUs.

# Counting RA Resources

Net Qualifying Capacity is the amount of a resource’s capacity that can be counted for RA compliance filings.  The CPUC established NQC counting conventions, which are computed based on the applicable resource type.  Qualifying Capacity (QC) represents the maximum capacity eligible to be counted for meeting the CPUC’s RAR prior to assessing the deliverability of the resource.  The CAISO adjusts a resource’s QC for deliverability; the resulting value is the NQC.  Each year, the CPUC posts on its website the NQC for each resource that is eligible to sell RA capacity to CPUC jurisdictional LSEs.  The CPUC adopted the current QC counting conventions in D.10-06-036.

California will have a greater energy resource supply in 2010 than in 2009.  Total NQC on the 2010 NQC list is 3,441 MW higher than total NQC on the 2009 NQC list.  The 2010 compliance year NQC list is posted to the CPUC website.  Several large plants came online and were added to the 2010 NQC list, including Starwood Midway, Gateway, Panoche Energy Center, Otay Mesa Energy Center, Inland Empire Units 1 and 2, Orange Grove, the El Cajon Peaker and the Blythe Energy Project.  Several smaller renewable resources also came online in 2010.  Further, several curtailable large pumping loads were added to the NQC list in 2010 as demand response resources.  Additional plants are under construction, such as the repowering of the Humboldt Generating Station, the new Colusa Energy Center, and the expansion of the Riverside Energy Resource Center.  A summary of the current status of plants subject to CEC siting review, which may eventually be added to California’s resource pool, is posted to the CEC website.

## Establishment of CAISO’S NQC Values for 2009

Significant changes have occurred to the NQC list since the 2006 compliance year.  Several new resources have been added, the format of the list has changed, and now there is more information posted on the list such as Zonal and Local Area designation.  The update of the 2009 NQC list was completed with the following adjustments:

- Updated values for resources whose counting conventions include historical data (e.g., wind and solar without backup resources).

- Updated values for resources with erroneous or missing NQC that may have been listed in error in the previous NQC posting.  This update included modifications to the NQC by the CAISO pursuant to its testing and verification authority under section 40.5.2 of its Tariff.

Further developments lay ahead for the 2010 NQC list:

- Calculations for wind and solar resources will use CAISO settlement quality meter data, instead of IOU purchase data as was used in previous years.

## Aggregate NQC Values 2006 through 2011

Table 8 shows aggregate NQC values from the CAISO NQC list for 2006-2010.  In compiling the totals, most facilities were given a single, year-round NQC value.  Some facilities such as wind and solar units without backup were given twelve monthly NQC values due to performance variations between months.  For those facilities that were given monthly NQC values, this table shows August NQC values for the total amount.

Table 8.  NQC for 2006-2010

| Year | Total NQC (MW) | Total Number of Scheduling Resource IDs | Net NQC change (MW) | Net Gain in CAISO IDs on list |
| --- | --- | --- | --- | --- |
| 2006 | 46,687 | 563 |  |  |
| 2007 | 46,504 | 572 | (183) | 9 |
| 2008 | 48,056 | 600 | 1,552 | 30 |
| 2009 | 48,899 | 613 | 843 | 13 |
| 2010 | 52,340 | 646 | 3,441 | 33 |

Source: NQC lists from 2006 through 2010

## Import Allocations for 2009

The CAISO allocates available import capacity to CPUC jurisdictional and non-CPUC jurisdictional LSEs to ensure that California is not relying on more imports than could be accommodated by the current transmission system.  The CPUC worked closely with the CAISO on the development of this process for use in the CPUC RA program.  The CAISO has a 13 step process in the CAISO tariff to perform this allocation.  The steps of the process are summarized in the CPUC RA Guide for 2009 and the results of selected steps are summarized in the table below:

Table 9.  2009 Import Allocations process (MW)

| Maximum Imports for 2009 compliance year | 16,604 |
| --- | --- |
| Total ETC for outside the control area loads | 3,997 |
| Available Import Capability (for loads in the control area) | 12,608 |
| Existing Contract Import Capability (ETC inside loads) | 2,143 |
| Total Pre-RA Import Commitments | 6,984 |
| Total Pre-RA Import Commitments & ETC | 8,343 |
| Remaining Import Capability after Step 4 | 4,264 |
| Assigned Remaining Import Capability | 2,254 |
| Remaining Import Capability after Step 10 | 2,010 |
| Assigned Remaining Import Capability | 1,672 |
| Remaining Import Capability after Step 12 | 338 |
| Remaining Import Capability after Step 13 (Aug 2008) | 197 |

Source:  Aggregate CAISO import allocations posted here: http://www.caiso.com/2061/20619792cbc0.pdf

Throughout the summer of 2009, the CAISO allocated 12,608 MW out of 16,604 MW of import capacity to LSEs, while 3,997 MW was allocated to Existing Transmission Contracts (ETCs) outside the CAISO control area.  Table 10 below summarizes 2009 Import Allocations and the use of Import Allocations in RA filings.  All LSEs in CAISO reported between 4,150 and 7,213 MW of import capacity.  Table 10 also shows the amount of import allocations used as a percentage of total allocations for in control area load LSEs used between 34 and 75 percent of their total import allocations during the summer of 2009.  This represents a slight increase at the high end of the range relative to 2007’s range of 45 to 65 percent of import allocations used.  Imports represented between 8 and 12 percent of all RA capacity.

Table 10.  2009 Import Allocations and Usage (MW)

| Line | Element | May | June | July | August | September |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | Import Allocations provided to LSEs for use in RA filings | 12,608 | 9, 618 | 9,618 | 9, 618 | 9, 618 |
| 2 | Imports shown by CPUC jurisdictional LSEs | 2,731 | 2,552 | 4,632 | 5,540 | 4,033 |
| 3 | Imports shown by non-CPUC jurisdictional LSEs | 1,546 | 1,598 | 1,688 | 1,673 | 1,595 |
| 4 | Total Imports shown | 4,277 | 4,150 | 6,320 | 7,213 | 5,628 |
| 5 | Allocations not used in RA Filings: | 8,331 | 5,468 | 3,298 | 2,405 | 3,990 |
| 6 | Percentage used of allocated (line 4/Line 1) | 34% | 43% | 66% | 75% | 59% |

Source: Import Allocation information posted on the CAISO website as well as aggregate RA filing information

# Reliability Must Run Designations in 2009

Generating resources with existing RMR contracts must be redesignated by the CAISO for the next compliance year and presented to the CAISO Board of Governors for approval by October 1st of each year. Designations for new RMR contracts are more flexible, and may arise during the relevant compliance year.  RMR resources are placed into two classes: Condition 1 contracts are allowed to operate in the energy market even if not dispatched by the CAISO for reliability purposes, and Condition 2 units are generally not allowed to operate in the energy market but are under the full dispatch of the CAISO for reliability purposes.  Both types of RMR contracts are paid for by all customers in the transmission area. Condition 1 units are able to competitively earn revenue in the energy market in addition to the capacity payments under the RMR Agreement.

In D.06-06-064 the CPUC ordered that capacity from Condition 1 RMR contracts will be allocated to LSEs to count only towards the LSE’s Local RA obligation, while Condition 2 RMR units may be counted towards both the System and Local RAR obligations.  Because they are able to participate in the market, Condition 1 units are allowed to sell their System RA credit to a third party, typically through a “wrap around” contract.  RMR units with RA contracts that set the fixed cost recovery via the RMR contract to $0 are not allocated to LSEs and are able to count towards the RAR of the LSE that has entered into RA contracts with them.

Pursuant to the stated policy preference of the Commission, Local RA began to supplant RMR contracting for the 2007 compliance year and a significant decline was seen in 2007 RMR designations.  That trend continued for 2009 and 2010 compliance year.  Table 11 provides a summary of the CAISO’s 2008, 2009, and 2010 RMR designations.  In response to CPUC Local RA compliance filings, the CAISO began to reduce its volume of RMR designations; 731 MW of RMR capacity mostly in the PG&E service territory was released from RMR for 2008 compliance year, 1022 MW of capacity was released in 2009 compliance year (Encina Power Plant, the Cabrillo II units, and Geysers unit 6) and another 1262 MW of capacity was released for 2010 compliance year.  Units released from RMR contracts for 2010 include:

- South Bay units 3 and 4

- Los Medanos Energy Center

- Escondido, Border, and El Cajon units

In addition to releasing units from RMR contracts, the CAISO transitioned some RMR contracts to other types of dual fuel or blackstart interim agreements.  These changes reduced RMR designations even further.

Each September, the CAISO and the CPUC receive preliminary Local RA filings and evaluate which of the current RMR contracts can be terminated because either they are no longer needed for reliability or the relevant units have RA contracts for the following compliance year.  Accordingly, some RMR units file with the FERC to terminate their Year-Ahead designation due to verification of RA contracts with those units and inclusion as RA resources in the LSEs’ final Year-Ahead Local RA Filings.  This represents another opportunity to reduce CAISO reliance on RMR agreements.  Table 11 shows the downward trend of RMR contracting since the 2008 compliance year.

Table 11. RMR designations and RMR allocations for 2008-2010

| Year |  | PG&E | SCE | SDG&E | Total |
| --- | --- | --- | --- | --- | --- |
| 2008 | Compliance Year CAISO Board Memo | 1,303 | 0 | 1,961 | 3,264 |
|  | Compliance year Local RMR allocations | 749 | 0 | 277 | 1,026 |
|  | Difference in CAISO designations from previous year | (731) | 0 | 0 | (731) |
| 2009 | Compliance year CAISO Board of Governors | 1,263 | 0 | 979 | 2,242 |
|  | Compliance year Local RMR allocations | 709 | 0 | 132 | 841 |
|  | Difference in CAISO designations from previous year | (40) | 0 | (982) | (1,022) |
| 2010 | Compliance year CAISO Board of Governors | 709 | 0 | 311 | 1,020 |
|  | Compliance year Local RMR allocations | 709 | 0 | 311 | 1,020 |
|  | Difference in CAISO designations from previous year | (554) | 0 | (668) | (1,222) |

Source: CAISO Board of governors meetings for 10/17/2007, and 10/29/08, and 10/21/09

# Compliance with RAR in 2009

CPUC staff continued the implementation of the RA program during 2009 and built on the experience of 2006 through 2008.  Beginning with the 2009 compliance year, LSEs transitioned to submitting compliance filings to Energy Division via an electronic Secure File Transfer Protocol (SFTP) system. Energy Division hosted a July 24, 2008 workshop to discuss the electronic system.  Final 2009 templates and guides were made available to LSEs on July 13, 2008.

## Overview of the RA Filing Process

The 2009 System and Local RA filing templates and guides were a significant upgrade from previous templates and guides.  In addition to being filed electronically, several important automations were built into the template.

Staff convened workshops in July of 2008 to demonstrate the new changes and provide LSEs with the opportunity to ensure that they understood how to fill the template out.  The System and Local templates for the 2010 compliance year were issued on August 13, 2009.  The order and timing of filings was the same for 2009 compliance year as previous compliance years, with the exception of the extension discussed in section 2.1.  LSEs were responsible for submitting two Year-Ahead filings for 2009.  As with previous years, the CPUC required that all filings be submitted simultaneously to the CAISO, CPUC, and CEC.

Energy Division evaluates many RA filings each year, issues resource allocations, and continually works with LSEs to improve the RA administration process.  Three LSEs ceased operations during 2009 compliance year.  This means Energy Division currently receives 14 filings each year from 12 LSEs, totaling 168 filings per year.  In addition to the load forecasting duties the CEC performs and the supply plan validations that the CAISO performs, Energy Division staff perform including Demand Response allocations, Local RA allocations, and CAM and RMR allocations.  As knowledge in the market has increased and as filing requirements have become more simplified, time and work requirements have decreased.  However, with the possible reopening of the DA market as well as the inclusion of the small and multi-jurisdictional LSEs in the RA program, there is the possibility of a growth in the number of LSEs.

## Compliance Review Process

The CPUC checked the filings for compliance by verifying that each LSE’s submittal was accurate, timely, and satisfied all requirements. The CAISO reviewed the filings to check whether the RA filings submitted by LSEs were consistent with the supply plans submitted by generators, and used the submittals to let CAISO operations staff know which units were under contract and available.  The CEC reviewed the filings and the historical load information provided by the LSEs for the appropriate time period to determine whether those filings matched load forecasts.

In 2009, CPUC Staff continued to work closely with LSEs to resolve any questions regarding the RA filing process and templates.  CPUC Staff has been able to develop answers to numerous questions raised by LSEs that have special or unique circumstances.  It is the hope of CPUC Staff that this process of working with the LSEs to reconcile differences and make revisions will continue to lead to fewer questions in the future and make the RA filing process smoother.  CPUC Staff, in a coordinated effort with the CEC and CAISO, has reviewed all compliance filings received to date according to a comprehensive procedure that includes verifying timely arrival of the filings, matching resources listed against those of the NQC list, confirming compliance with local and Path 26 requirements, and requesting corrections.  The CAISO collects and organizes supply plans submitted by generators, and helps Energy Division compare the supply plans to the LSE filings.  Once compliance is verified, Energy Division approves filings and sends an approval letter to each LSE.

## Enforcement and Compliance

The essence of the RAR program is mandatory LSE acquisition of capacity to meet load and reserve requirements.  The short timeframes in which CPUC, CAISO and CEC Staff must verify that adequate capacity has been procured and to complete backstop procurement if necessary creates a need for filings to arrive on time and be correct.  Non-compliance occurs if either an LSE files with a procurement deficiency (i.e., it did not meet its RA obligations) or does not file at all, files late, or not in the manner required.  These types of non-compliance generally lead to enforcement actions or citations.  Although CPUC staff has not experienced a situation where backstop procurement by the CAISO has resulted from CPUC jurisdictional LSE procurement deficiencies, the situation may occur if compliance is not strictly enforced.  Additionally, errors and deficiencies require staff to spend time investigating and determining the cause of the situation, and then work with the LSE to remedy problems.  Due to the administrative obligations of the RA Program, Energy Division Staff has worked to simplify and streamline filing procedures, and now accepts RA Filings electronically via a Secure FTP application.  CPUC staff has also done significant outreach to LSEs to educate them as to filing procedures, and strives to clear up any confusion prior to filing deadlines.

### Enactment and Implementation of E-4195

In November 2009, the CPUC made changes to the citation program by adopting Resolution E-4195, which replaces Resolution E-4017.   The resolution “transfers authority to draft and issue citations from Energy Division to Commission Staff as a whole, broadens the scope of the Resolution to encompass all LSEs that are potentially subject to RA obligations, and adds a Specified Violation for failure to meet RA obligations with a small procurement deficiency.”  Resolution E-4195 does not modify the RA program itself; it merely modifies the citation and enforcement rules.

### Enforcement actions taken 2006-2009 compliance years

Since the approval of Resolution E-4195, Energy Division refers potential violations to the CPUC’s Consumer Protection and Safety Division (CPSD), which prosecutes enforcement cases related to the RA program on behalf of the Commission.  Overall compliance in 2009 has been similar to the pattern seen in previous years.  Table 12 summarizes enforcement actions and citations taken by the Commission since inception of the RA program in 2006.  In total the Commission has issued 15 citations for violations related to compliance years 2006 through 2009 and has collected $47,500 in payments from LSEs arising from these citations.

An enforcement action was taken against Constellation New Energy in 2007 for failure to comply with the 2007 Year-Ahead Local RA obligation; this action was settled in Resolution L-350.  A presiding officer’s decision was approved by the Commission accepting settlement of in I.09-01-017 against Calpine Power America-CA, LLC related to the 2008 System and Local RA Filings.  The Commission also issued I.10-04-010 against CNE for failure to properly file their January 2009 RA Filing.

Table 12. Enforcement Summary Pursuant to the RA program since 2006

| Compliance Year | 2006 | 2007 | 2008 | 2009 | Total |
| --- | --- | --- | --- | --- | --- |
| Citations issued | 1 | 3 | 7 | 4 | 15 |
| LSEs cited | Commerce Energy | 3Phases Renewables; Commerce Energy; American Utilities Network | 3Phases Renewables (2); Commerce Energy (2); Corona Department of Water & Power; Sempra Energy; Shell Energy; | Commerce Energy (3); CNE; |  |
| Penalties paid in citations | $1,500 | $5,000 | $14,500 | $26,500 | $47,500 |
| Enforcement Cases | 0 | 1 | 1 | 1 | 3 |
| Penalties paid in enforcement cases | 0 | $107,500 | $225,000 | Pending | $332,500 |

Source – CPUC enforcement records

Although 2009 saw a large improvement in the quality of the RA filings, recurrent minor errors still consume staff time and delay the processing of filings.  Due to improvements in other aspects of the filings, these errors primarily relate to the outage counting protocol, incorrect CAISO resource IDs, and a number of other small errors.  There is also the continued need to monitor administrative issues such as filing dates and filing procedures.

In order to expedite filings and prevent further errors, the Commission approved D.08-06-031 which, among other refinements, approved the use of electronic filing procedures and the use of a more automated reporting template that will prevent many of the errors seen in previous years.

### Load Forecast Compliance

After the compliance year, the CEC has continued to review load forecasts for a given compliance period against actual observed loads from that period.  While so far there has been no enforcement action taken in response to any repeated pattern of forecast discrepancy by any particular LSE, that is a distinct possibility in the future.  Only a limited number of LSEs require plausibility adjustments and among these, some LSEs require greater adjustments than others.  Plausibility adjustments that are large enough that CEC needs to adjust total load forecasts in preparation for the Year-Ahead filing create significant work for the oversight agencies and all LSEs that receive revised RA instructions.

This subject received extensive discussion at the RA workshops held by Energy Division staff in 2009.  In the future, LSEs may be subject to penalties if a pattern emerges of continued significant differences between actual historical information and load forecasts.

# Generator Performance and Availability

Since the RA Program requires LSEs to demonstrate procurement of valid RA capacity, the RA Program is reliant on generation procured to be available and online when the CAISO needs to commit it.  For that reason, measurement and evaluation of generator performance is a necessary component of the RA program, including attention to standard metrics of generator availability.  Several RA proceedings make assumptions regarding generator availability, such as the RA Proceeding R.09-10-032, and the LTPP proceeding R.10-05-006.

Generator performance is measured by the North American Electric Reliability Corporation (NERC) via the Generator Asset Data System (GADS).  California power plants self-report performance data to NERC, pursuant to the CPUC’s General Order 167.  The GADS is a comprehensive database of outage data collected from 5,300 units worldwide.  The GADS is recognized as an industry standard for power plant reliability data.  ISOs across the country use GADS data to calculate forced and unforced capacity values for their capacity markets.  The GADS system evaluates and publishes statistics that allow for comparison across generators, generator classes, and regions.  There are also a variety of statistics published, such that it is possible to measure generators according to a number of factors.  Comparison of these statistics allows for a comparison of generator performance between California generators and national averages, and comparison across classes of generators.  The charts that follow illustrate the performance and availability of California's generators in three categories against national averages and illustrate the trend in these statistics over the previous five years.

In California, 45 conventional steam units, 55 combined cycle, and 71 combustion turbine peaker units submit performance data to the GADS. While NERC is developing performance factors and definitions for renewable resources, this report discusses only performance data for thermal power plants.   NERC GADS performance factors measure generation reliability for a broad range of technologies and fuel sources. The three most relevant factors on an aggregate level, are: Demand Equivalent Forced Outage Rates (EFORd), Equivalent Availability Factor (EAF), and Net Capacity Factor (NCF).  For optimal performance, a plant strives to achieve high availability and capacity factors, and a low outage rate.

Section 6.1 discusses each factor and its desirable measure. Figure 4 compares the average weighted NERC performance factors for California generators by fossil fuel technology for the years 2004-08.

Section 6.2 describes aggregate performance for California’s primary power plant technologies: Combined Cycle Units, Combustion Turbine Units, and Conventional Steam Turbines.  Figures 5 through 13 compare the annual performance for each NERC GADS factor, by technology, against the national average performance.

## Reliability Performance Metrics

The EAF indicates the percentage of time that a unit is capable of providing generation. California conventional steam units, natural gas peakers, and new combined cycle units, on average, are available at least 85% of the time.  California’s generators have an EAF very similar to national averages, and thus are not explored further below.  Conversely, a high EFORd value indicates a high level of forced outages.  EFORd represents the percentage of time that a unit is out of service during periods it should be available. The weighted average EFORd for all technologies is below 8%, with combined cycle plants performing the most reliably.

The NCF represents the actual energy generated by a unit, relative to the amount of power the unit can produce at maximum operating capacity.  Plants that operate as baseload are capable of operating at much higher capacity factors than peaking plants. Newer combined cycle units operate at a much higher capacity factor than combustion turbine peakers or conventional steam boiler driven steam plants.  By design, simple cycle peakers ramp quickly to meet high demand, typically during summer peak periods. Peakers also act as standby generation.  For that reason, peakers run infrequently, or for short, variable periods of time.

Conventional steam plants operate at a lower NCF than combined cycle units, but at a higher level than peaker plants.  California’s conventional steam plants were designed 30-60 years ago for continuous operation to serve baseload, and were used that way for many years.  Due to the age of their technology, California’s steam plants do not operate as cost-efficiently as new combined cycle power plants, and therefore do not run as often.  As Figure 4 illustrates, the five-year average NCF for combined cycle units, at 60%, is much higher than the NCF for conventional steam turbines at 10.9% and combustion turbine peakers at 3.15%.

Figure 4. Five-Year Weighted Average NERC GADS Performance

Source: California plant specific GADS data gathered by CPUC

## Annual Average NERC GADS Performance by Technology

### Combined Cycle Plants

Combined cycle plants consist of one or more combustion turbine generators (CTs), and a steam turbine generator.  During the first cycle, the CT generates electricity. The steam turbine recovers the CT’s waste heat to fuel a second generating cycle of electricity production, thus increasing the amount of power generated by the original fuel supply.  On average, combined cycle steam units perform similarly to combined cycle gas turbine (CCGT) units.  Combined cycle plants are a common choice for baseload needs due to their high operating efficiencies, low capital costs, and relatively low emissions.

Between 2004 and 2008, the NCF for California combined cycle plants exceeded the national average.  California combined cycle plants maintained a high, constant level of average productivity, between 55-65% ().  The low national average NCF of 32% partially reflects other states’ reliance on less costly fuel sources, such as hydropower or coal-fired plants.  A low NCF can also reflect factors outside of a plant operator’s control, such as how often a plant is dispatched, economic factors that impact decisions to run the plant, and cumulative mechanical stress that affects the plant’s ability to operate continuously.  Figure 5 shows that forced outage rates were lower than the national average EFORd between 2006-2008.

Figure 5. Combined Cycle Gas Turbine EFORD

Source: GADS California plant specific data gathered by the CPUC under GO 167

Figure 6. Combined Cycle Gas Turbine NCF

Source: California plant specific GADS data gathered by the CPUC under GO 167

### Combustion Turbine (Peakers)

Simple-cycle gas turbine power plants (also called Combustion Turbines or peaking facilities) consist of one or two combustion gas turbines which power a generator. These plants are designed to ramp quickly to meet peak demand, typically during the summer, and therefore generate only for short periods. Figure 8 shows that California peakers operate at low capacity factors, as do peakers nationwide.

Figure 7. Combustion Turbine Units’ EFORd

Source: California plant specific GADS data gathered by the CPUC under GO 167

Figure 8. Combustion Turbine NCF

Source: California plant specific GADS data gathered by the CPUC under GO 167

### Conventional Steam Plants

Figure 9 illustrates that between 2006 and 2008, California’s steam plants, on average, demonstrated a lower forced outage rate than steam units nationwide.  During that same period, NCF for California steam plants declined relative to the national average.  The continued decline in NCF for California units is consistent with the use of the aging plants as cycling units to follow load, rather than operate continuously to serve baseload.

Figure 9. Steam Turbine EFORd

Source: California plant specific GADS data gathered by the CPUC under GO 167

Figure 10. Steam Turbine NCF

Source: California plant specific GADS data gathered by the CPUC under GO 167

# Changes to the RA Program for 2010

During 2009, the CAISO successfully implemented MRTU, which changed a number of provisions related to the RA Program.  These include the enactment of ICPM to replace TCPM as the backstop capacity mechanism, a change to the cost codes and charge types related to CAISO unit commitment, and the implementation of market power mitigation within MRTU.

In addition to MRTU implementation, the CPUC further refined the RA program in 2010 compliance year in D.09-06-028, which modified QC counting rules for non-dispatchable resources, including adoption of an exceedance methodology for wind and solar resources.  D.10-06-036 adopted a final QC manual as Appendix B.  Explanation of the exceedance approach is found in Section 8.

## Exceedance Methodology for NQC of Wind and Solar

The Commission adopted D.09-06-028, which among other things, adopted the exceedance methodology for computation of the NQC of wind and solar resources.  The CPUC published a fact sheet which further explained these changes but a summary of the changes to NQC due to this new methodology are presented here.   Trends in aggregate NQC amounts are explained in Table 8.  Even with the decrease in wind and solar NQC, there was a 2,891 MW increase in total NQC available to meet RA requirements.

### Impacts of rule change:

- Approximately a 25% reduction in QC of wind and solar facilities in summer months, and 65% reduction in winter months from previous methodology

  - Solar: no change in peak months; reduced to near zero in winter

  - Wind: reductions in all months

- Reduces available QC by approximately 160 to 370 MW depending on the month of the year (on average: 250 MW, or approximately 0.5% of total NQC)

- New wind resources will receive QC based on the QC of existing wind resources; new solar will receive QC based on QC of existing solar resources.  The factors used to calculate QC for new resources can be found on the 2010 NQC list.

### Changes in wind and solar QC process from 2009 to 2010:

- Switch to a 70% exceedance methodology from an averaging methodology

- A shift in the hours and days used, the new five hour ranges are 4 to 9 p.m. during November to March; 1 to 6 p.m. during April to October

- Years of data analyzed: 2006-2008 instead of 2005-2007

- Resource production data source: CAISO data instead of IOU data

# Appendix 1 - Total CAISO LSE Procurement as Percentage of Total Obligation

Table 13. Total CAISO LSE Procurement as Percentage of Total CAISO Obligation

| 2009 | Type of LSE | Peak Forecast (MW) | RAR | I. Physical Resources in ISO Control Area | II. DWR contracts | III. Total Imports | V. Dispatchable DR and Participating Load | Liquidated Damages Contracts | CAM/ RMR /Other | Total RA Capacity | RA Capacity as a Percentage of RAR |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 5/09 | CPUC LSEs | 36,369 | 41,824 | 35,457 | 2,588 | 2,731 | 2,629 | 0 | 425 | 44,224 | 106% |
|  | Non-CPUC LSEs | 3,048 | 3,442 | 1,824 |  | 1,546 | 105 | 260 | 21 | 3,772 | 110% |
|  | Total RA capacity | 39,417 | 45,266 | 37,281 | 2,588 | 4,277 | 2,734 | 260 | 446 | 47,996 | 106% |
|  | % of Capacity |  |  | 78% | 5% | 9% | 6% | 1% | 1% | 100% |  |
| 6/09 | CPUC LSEs | 40,672 | 46,773 | 39,765 | 3,050 | 2,552 | 2,629 | 0 | 589 | 48,979 | 105% |
|  | Non-CPUC LSEs | 3,313 | 3,749 | 2,066 |  | 1,598 | 52 | 277 | 20 | 4,021 | 107% |
|  | Total RA capacity | 43,985 | 50,522 | 41,831 | 3,050 | 4,150 | 2,681 | 277 | 609 | 53,000 | 105% |
|  | % of Capacity |  |  | 79% | 6% | 8% | 5% | 1% | 1% | 100% |  |
| 7/09 | CPUC LSEs | 44,498 | 51,173 | 40,456 | 3,617 | 4,632 | 2,670 | 0 | 589 | 52,365 | 102% |
|  | Non-CPUC LSEs | 3,506 | 4,032 | 2,045 |  | 1,688 | 67 | 441 | 18 | 4,269 | 106% |
|  | Total RA capacity | 48,004 | 55,205 | 42,501 | 3,617 | 6,320 | 2,737 | 441 | 607 | 56,634 | 103% |
|  | % of Capacity |  |  | 75% | 6% | 11% | 5% | 1% | 1% | 100% |  |
| 8/09 | CPUC LSEs | 46,699 | 53,704 | 41,762 | 3,617 | 5,540 | 2,677 | 0 | 589 | 54,587 | 102% |
|  | Non-CPUC LSEs | 3,879 | 4,435 | 2,300 |  | 1,673 | 182 | 457 | 18 | 4,657 | 105% |
|  | Total RA capacity | 50,578 | 58,139 | 44,062 | 3,617 | 7,213 | 2,859 | 457 | 607 | 59,244 | 102% |
|  | % of Capacity |  |  | 74% | 6% | 12% | 5% | 1% | 1% | 100% |  |
| 9/09 | CPUC LSEs | 42,594 | 48,983 | 38,972 | 3,617 | 4,033 | 2,653 | 0 | 589 | 50,262 | 103% |
|  | Non-CPUC LSEs | 3,280 | 3,748 | 1,898 |  | 1,595 | 129 | 392 | 18 | 4,051 | 108% |
|  | Total RA capacity | 45,874 | 52,731 | 40,870 | 3,617 | 5,628 | 2,782 | 392 | 607 | 54,313 | 103% |
|  | % of Capacity |  |  | 75% | 7% | 10% | 5% | 1% | 1% | 100% |  |

Source: Aggregated RA data collected by CPUC along with RCST data from CAISO for the summer of 2009

Commission Jurisdictional LSEs include all Investor Owned Utilities (IOUs) Electricity Service Providers (ESPs) and Community Choice Aggregators (CCAs)

The Local RA shown does not include DR, RMR, and CAM resources as these resources are used to reduce an LSE’s Local RA obligation.  See Table 5

CAM resources are those built for system needs, not just IOU specific needs; allocations of capacity credit for CAM resources are performed according to the mechanism adopted in D.07-09-044

http://docs.cpuc.ca.gov/efile/RULINGS/92223.pdf

This request for wavier was posted to the CPUC website on February 18, 2010 at the following link:

http://www.cpuc.ca.gov/NR/rdonlyres/CFD3706D-207E-4FB7-B213-C15C20FC84E6/0/Approval09LocalRAWaiver.pdf

Final CPUC decisions may be found at http://docs.cpuc.ca.gov/cyberdocs/Libraries/WEBPUB/Common/decSearchDsp.asp

http://docs.cpuc.ca.gov/PUBLISHED/GRAPHICS/98960.PDF

2008 RA report is linked to the CPUC website here: http://www.cpuc.ca.gov/PUC/energy/Procurement/RA/index.htm#Final%20Reports

One ESP ended their ESP registration before the 2009 compliance year (APS Energy Services) and two more ended their ESP registrations during the 2009 compliance year (AUN, and Corona Department of Water and Power).

Annual RA Filing Guides are available on the CPUC website:  http://www.cpuc.ca.gov/PUC/energy/Procurement/RA/ra_guides_2008-09.htm

LD contracts are energy-only contracts which require a limited payment of damages in the event of non-performance, and are therefore regarded as less reliable for short-term purposes.  D.05-10-042 adopted a phase out schedule that was completed after the 2008 compliance year.

The Demand Response listed includes a small amount of non-IOU DR resources (about 3.7 MW) listed independent of the amount that is part of the annual IOU DR allocation.

The Monthly CEC Load Forecast is the same forecast as applicable to the Monthly Filings, from Line 3 in Table 3

The Local RA program is discussed in Section 3.3 of the 2007 Resource Adequacy Report

LCR studies and materials for 2009 and previous years is posted at the following link: http://www.caiso.com/1c44/1c44bbc954950.html

Total LCR for each Local Area includes CPUC jurisdictional and non-jurisdictional LSEs.

http://docs.cpuc.ca.gov/published/REPORT/46914.PDF

http://docs.cpuc.ca.gov/PUBLISHED/FINAL_DECISION/119856.htm (QC manual adopted as Appendix B).

NQC information, including the NQC list for 2009 is posted here:  http://www.caiso.com/1796/179688b22c970.html

http://www.energy.ca.gov/sitingcases/all_projects.html

CAISO tariff section 40.5.2.2

California Public Utilities Commission D.06-06-064, Section 3.3.7.1.

One CCA (Marin Energy Authority) has registered and has begun to submit RA Filings with the Commission as of May, 2010.

http://docs.cpuc.ca.gov/WORD_PDF/FINAL_RESOLUTION/93662.PDF

Res. E-4195, pg 1.

http://docs.cpuc.ca.gov/PUBLISHED/FINAL_RESOLUTION/73108.htm

The docket card for this proceeding can be accessed here: http://docs.cpuc.ca.gov/published/proceedings/I0901017.htm

Documents for this proceeding are posted here: http://docs.cpuc.ca.gov/published/proceedings/I1004010.htm

A 3rd citation was rescinded

http://162.15.7.24/PUBLISHED/GENERAL_ORDER/108114.htm

Figure 4 compares capacity-weighted performance metrics (WEFORd, WEAF, and NCF), which take into account the different capacity ratings of different units in a pooled comparison.  However, no further adjustment is needed for NCF, as it is already calculated as a capacity weighted equation.

Figures 5 through 13 compare unweighted EFORd for California plants to the national average. National Average NCF and WEAF are derived from annual Historical Availability Statistics from NERC’s Generating Availability Report 2004-08, dated 8/21/09.  National Average EFORd is derived from NERC’s Generating Unit Statistical Brochure for 2004, 2005, 2006, 2007, and 2008.

The national average EFORd for combined cycle plants was not available for 2004 and 2005.

http://docs.cpuc.ca.gov/WORD_PDF/FINAL_DECISION/119856.PDF

http://www.cpuc.ca.gov/NR/rdonlyres/B0AC73A8-737D-46CF-B021-BD28CB351FC1/0/WindandSolarQualifyingCapacity_FactSheet.doc